[image: image1.wmf]GR  NVILLE

 County Schools

2010 ELECTRICAL

SAFETY PLAN
Researched,

Assembled and Edited By:

Granville County Schools 

Sidney B. Moody
Safety/Regulatory Coordinator
PO Box 927 / 106 Hicks Mill Road 
Oxford, NC 27565 

                                                                                                   October 2010                                                                          
Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
INDEX : 









PAGE # 
1. ELECTRICAL SAFETY PLAN 






   3 
2. ELECTRICAL SAFETY REQUIREMENTS




   3-4 
3. ELECTRICAL SAFETY INSPECTIONS 




    4 
4. EMPLOYEES RESPONSIBILITIES 





    4-6 
5. ELECTRICAL SAFETY PRACTICES 





     6-8 
6. ELECTRICAL SAFETY PROCEDURES 




      8-9 
7. DE-ENERGIZED ELECTRICAL PROCEDURES 



      9-10 
8. ENERGIZED ELECTRICAL PROCEDURES 




     10-11 
9. VEHICLE OR MECHANICAL EQUIPMENT 




      11-12 
10. EMERGENCY REMOVAL OR TAG AND LOCK 



       13 
11. CONTROL OF HAZARDOUS ENERGY (LOCK-OUT/TAG-OUT) 

        13 
12. TAG-OUT DEVICES







         14 
13. LOCK-OUT DEVICES







         15 
14. ENERGY-ISOLATING DEVICES 





     1516 
15. PLUG/CORD AND HOSE-CONNECTED TYPE EQUIPMENT                            16 
16. ELECTRICALLY POWERED EQUIPMENT                                                      16-17 
17. CHEMICAL AND/OR PRESSURIZED LINES                                                   17-18 
18. STORED MECHANICAL ENERGY                                                                       18 
19. ENERGY SAFETY TRAINING                                                                               19 

ELECTRICAL SELF-AUDIT SAFETY QUESTIONS                                   20-22 
2

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
1. ELECTRICAL SAFETY PLAN 
1. All electrical work will be conducted in a manner consistent with existing regulations and with good standard practices. 

2. Electrical work has the potential for personnel electrocution and the potential hazard of catastrophic property damage. 

3. Granville County Schools employees when working with electricity and electrical equipment will exercise extreme caution. 

4. Electrical equipment can also cause fire because of its potential as an ignition source for causing fire or explosion. 

5. Fire is frequently caused by short circuits, overheating equipment and failure of current limiters, thermal sensors, and other safety devices. 

6. Explosions will occur when flammable liquids, gases, and dusts are exposed to ignition sources generated by electrical equipment. 

2. ELECTRICAL SAFETY REQUIREMENTS 
1. Electrical installations and utilization equipment will be in accordance with the current edition of the National Electrical Code, National Fire Protection Association (NFPA 70); American National Standards Institute (ANSI) Standard C1. This code will apply to replacement, installation, or utilization equipment. 

2. Equipment or facilities designed, fabricated for, and intended for use by Granville County Schools’ personnel will be procured to meet the requirements of the National Electric Code. 

3. Frames of all electrical equipment, regardless of voltage will be grounded. 

3

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
4. Exposed non-current carrying metal parts of electrical equipment that will be come energized under abnormal conditions will be grounded in accordance with the National Electrical Code. 

5. Wires will be covered wherever they are joined, such as: outlets, switches, junction boxes, etc. 

6. Parts of electrical equipment which in ordinary operation produces arcs, sparks, etc., will not be operated or used in explosive atmospheres or in close proximity to combustible materials. 

7. Equipment connected by flexible extension cords will be grounded either by a 3-wire cord or by a separate ground wire (except double insulated equipment). 

8. Ground fault circuit interrupters (GFCI) will be used on all 120-volt, single-phase, 15- and 20-ampere receptacle outlets at job sites when the receptacles are not a part of the permanent wiring of the building or structure. 

9. Receptacles on a two wire, single-phase portable or vehicle-mounted generator rated not more than 5 kilowatt, where the circuit conductors of the generator are insulated from the generator frame and all or the grounded surfaces, need not be protected with GFCI’s. 

3. ELECTRICAL SAFETY INSPECTIONS 
1. Supervisors will insure that work areas are inspected for possible electrical hazards. 

2. Sufficient workspace will be provided and maintained around electric equipment to permit safe operations and maintenance of such equipment. 

4

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
4. EMPLOYEES RESPONSIBILITIES
A. Supervisors: 
1. All work hazards will be anticipated and all safeguards utilized. 

2. Ensures that all employees are properly trained and instructed in the safe operation of electrical equipment and aware of all hazards associated with the use of these electrical devices. 

3. Initiates any necessary administrative action required to enforce safety practices. 

4. Requests assistance from Granville County Schools’ Management regarding equipment operation that requires unique safety practice instructions. 

B. Employees: 
1. Granville County Schools will follow electrical safety policies and procedures and instructions of Supervisors and the Safety and Health Manager. 

2. Brings to the attention of the Supervisor and/or Health and Safety Branch potential hazardous situations such as discrepancies between instruction, procedures, policies and manual, faulty equipment, misapplication of device, etc. 

3. Electrical equipment known to be malfunctioning will be repaired or replaced before use. The repair will be initiated as soon as possible after the malfunction is noted. 

C. Safety and Health Manager: 
1. Assists supervisors in defining hazardous operations, designating safe practices and selecting proper application of devices. 

2. When necessary, obtains from the principle supervisor, standard operating procedure for electrical equipment and devices in use. 

5

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
3. In coordination with Granville County Schools’ Management and other supervisors, reviews and approves standard operating procedures. 

4. Evaluates potential electrical hazards during facility inspections to insure compliance with existing Granville County Schools’ plan and other safety guidelines. 

5. Requests support from Granville County Schools’ Management on hardware and equipment testing, tagging out of unserviceable equipment, and taking corrective action where necessary. 

5. ELECTRICAL SAFETY PRACTICES 
The following practices are to be followed by all employees: 
A. Individual: 
1. The user is responsible for obtaining necessary tools and safety equipment from the designated storage area, checking it for discrepancies, returning it to storage in good condition and identifying any faulty equipment to his/her supervisor. 

2. It will be the Supervisor’s immediate responsibility to replace any faulty safety equipment and notify Granville County Schools Safety and Health Manager. 

3. Eye protection is required during any electronic or electrical hardware repair, installation and/or open front operation. 

4. Electrical safety shoes, long sleeve non-polyester, low flammability shirts and insulating gloves will be worn when operating or testing 600 volt or higher equipment. 

5. Protective apron will be worn over polyester or other highly conductive apparel. 

6

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
6. .In the event of a medical emergency, Granville County Schools Management will contact local Emergency Rescue Units (911), and direct Emergency Rescue Units to the scene. 

7. If there is a person nearby who has received First Aid/CPR training, they will be contacted immediately to give assistance. 

B. Laboratory Requirements: 
1. All electrical and electronic laboratory equipment will be inspected for electrical hazards before using. 

2. All electrical equipment will be grounded through power cords, frame grounding and/or grounding through wiring in conduit system. 

3. Some power tools and instruments are double insulated and do not require or need three pronged plugs. 

4. Contact Granville County Schools’ Safety and Health Manager where the discrepancy or hazard exists. 

5. Laboratory equipment will be kept clear of electrical panel boards with the following clearances: 36 inches for 120/208 volts and 42 inches for 277/480 volts and up to 600 volt equipment. 

6. Operation of panel board circuit breakers by laboratory personnel is prohibited except in case of personal emergency. 

7. Switching devices that are tagged and locked will not be operated until issuer removes the tags. 

8. When work is to be performed on electrical equipment, care will be taken to make sure the electrical source is turned off, rendered inoperative, tagged and locked. (Re: Lock out/Tag out). 

9. Working on live parts of 50 volts or more will not be done except in an emergency and with proper procedure and/or qualified “Buddy” with appropriate safety equipment. 

7

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
10. Extension cords are intended only for temporary use with portable appliances, tools, and similar equipment that are not normally used at one specific location. 

11. Extension cords are not to be used as a substitute for fixed wiring. 

6. ELECTRICAL SAFETY PROCEDURES 
1. Granville County School’ employees may not enter spaces containing exposed energized parts, unless illumination is provided that enables the employees to perform the work safely. 

2. Where lack of illumination or an obstruction precludes observation of the work to be performed, employees may not perform tasks near exposed energized parts. 

3. Granville County Schools’ Employees may not reach blindly into areas which may contain energized parts. 

4. When a Granville County Schools’ employee works in a confined or enclosed space (such as a manhole or vault) that contains exposed energized parts, Granville County Schools will provide, and the employee will use, protective shields, protective barriers, or insulating materials as necessary to avoid inadvertent contact with these parts. 

5. Doors, hinged panels, and the like will be secured to prevent their swinging into Granville County Schools’ employee and causing the employee to contact exposed energized parts. 

6. Conductive materials and equipment that are in contact with any part of Granville County Schools’ employee's body will be handled in a manner that will prevent them from contacting exposed energized conductors or circuit parts. 

7. If a Granville County Schools’ employee must handle long dimensional conductive objects (such as ducts and pipes) in areas with exposed live parts, Granville County Schools will institute work practices (such as the use of insulation, guarding, and material handling techniques) which will minimize the hazard. 

8

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
8. Portable ladders will have nonconductive side rails if they are used where Granville County Schools’ employee or the ladder could contact exposed energized parts. 

9. Conductive articles of jewelry and clothing (such a watch bands, bracelets, rings, key chains, necklaces, metalized aprons, cloth with conductive thread, or metal headgear) may not be worn if they might contact exposed energized parts. However, such articles may be worn if they are rendered nonconductive by covering, wrapping, or other insulating means. 

7. DE-ENERGIZED ELECTRICAL PROCEDURES 
1. De-energized parts are live electrical parts that Granville County Schools’ employees may be exposed to and must be de-energized before the employee works on or near them, unless the employer can demonstrate that de-energizing introduces additional or increased hazards or is infeasible due to equipment design or operational limitations. 

2. Live parts that operate at less than 50 volts to ground need not be de-energized if there will be no increased exposure to electrical burns or to explosion due to electric arcs. 

3. Examples of increased or additional hazards include interruption of life support equipment, deactivation of emergency alarm systems, shutdown of hazardous location ventilation equipment, or removal of illumination for an area. 

4. Examples of work that may be performed on or near energized circuit parts because of infeasibility due to equipment design or operational limitations include testing of electric circuits that can only be performed with the circuit energized and work on circuits that form an integral part of a continuous industrial process in a chemical plant that would otherwise need to be completely shut down in order to permit work on one circuit or piece of equipment. 

9

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
5. The circuits and equipment to be worked on will be disconnected from all electric energy sources. Control circuit devices, such as push buttons, selector switches, and interlocks, may not be used as the sole means for deenergizing circuits or equipment. Interlocks for electric equipment may not be used as a substitute for lockout and tagging procedures. 

6. Stored electric energy which might endangera Granville County Schools’ employee will be released. Capacitors will be discharged and high capacitance elements will be short-circuited and grounded, if the stored electric energy might endanger personnel. 

7. Stored non-electrical energy in devices that could reenergize electric circuit parts will be blocked or relieved to the extent that the circuit parts could not be accidentally energized by the device. 

8. If work is to be performed near overhead lines, the lines will be de-energized and grounded, or other protective measures will be provided before work is started. 

9. If the lines are to be de-energized, arrangements will be made with the person or organization that operates or controls the electric circuits involved to de-energize and ground them. 

10. If protective measures, such as guarding, isolating, or insulating, are provided, these precautions will prevent Granville County Schools’ employees from contacting such lines directly with any part of their body or indirectly through conductive materials, tools, or equipment. 

8. ENERGIZED ELECTRICAL PROCEDURES 
1. If the exposed live parts are not de-energized (i.e., for reasons of increased or additional hazards or infeasibility), other safety-related work practices will be used to protect Granville County Schools’ employees who may be exposed to the electrical hazards involved. 

2. Such work practices will protect employees against contact with energized circuit parts directly with any part of their body or indirectly through some other conductive object. 

10

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
3. The work practices that are used will be suitable for the conditions under which the work is to be performed and for the voltage level of the exposed electric conductors or circuit parts 

4. A qualified Granville County Schools employee will conduct tests and visual inspections, as necessary, to verify that all tools, electrical jumpers, shorts, grounds, and other such devices have been removed, so that the circuits and equipment can be safely energized. 

5. Only qualified Granville County Schools’ employees may work on electric circuit parts or equipment. These employees will be capable of working safely on energized circuits and will be familiar with the proper use of special precautionary techniques, personal protective equipment, insulating and shielding materials, and insulated tools. " 

9. VEHICLE OR MECHANICAL EQUIPMENT 
1. Any Granville County Schools’ vehicle or mechanical equipment capable of having parts of its structure elevated near energized overhead lines will be operated so that a clearance of 10 ft. (305 cm) is maintained. 

2. If the voltage is higher than 50kV, the clearance will be increased 4 in. (10 cm) for every 10kV over that voltage. 

3. However, under any of the following conditions, the clearance may be reduced: 

NO  GRANVILLE COUNTY SCHOOLS’  EMPLOYEE WILL PERFORM THE FOLLOWING : UNLESS DOCUMENTED QUALIFICATION IS ON FILE AND EMPLOYEE HAS BEEN AUTHORIZED BY THE SAFETY MANAGER AND GCS ADMINISTRATION>
a. If the vehicle is in transit with its structure lowered, the clearance may be reduced to 4 ft. (122 cm). 

b. If the voltage is higher than 50kV, the clearance will be increased 4 in. (10 cm) for every 10 kV over that voltage. 

c. If insulating barriers are installed to prevent contact with the lines. 

d. If the barriers are rated for the voltage of the line being guarded and are not a part of or an attachment to the vehicle or its raised structure, the clearance may be reduced to a distance within the designed working dimensions of the insulating barrier. 

11

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
**SEE NOTE ON PREVIOUS PAGE -APPLIES THROUGH ITEM  6 BELOW.

CONTRACT TO  QUALIFIED COMPANIES.
e. If the equipment is an aerial lift insulated for the voltage involved, and if the work is performed by a qualified person, the clearance (between the un-insulated portion of the aerial lift and the power line) may be reduced to the distance given in Table S-5. 

TABLE S-5 - APPROACH DISTANCES FOR QUALIFIED EMPLOYEES – 
ALTERNATING CURRENT 
Voltage range (phase to phase) Minimum approach distance 
300V and less Avoid Contact 

Over 300V, not over 750V 1 ft. 0 in. (30.5 cm) 

Over 750V, not over 2kV 1 ft. 6 in. (46 cm) 

Over 2kV, not over 15kV 2 ft. 0 in. (61 cm) 

Over 15kV, not over 37kV 3 ft. 0 in. (91 cm) 

Over 37kV, not over 87.5kV 3 ft. 6 in. (107 cm) 

Over 87.5kV, not over 121kV 4 ft. 0 in. (122 cm) 

Over 121kV, not over 140kV 4 ft. 6 in. (137 cm) 

4. Granville County Schools employees standing on the ground may not contact the vehicle or mechanical equipment or any of its attachments, unless the employee is using protective equipment rated for the voltage; or the equipment is located so that no un-insulated part of its structure (that portion of the structure that provides a conductive path to employees on the ground) can come into contact with the employee. 

5. If any vehicle or mechanical equipment capable of having parts of its structure elevated near energized overhead lines is intentionally grounded, Granville County Schools employees working on the ground near the point of grounding may not stand at the grounding location whenever there is a possibility of overhead line contact. 

6. Additional precautions, such as the use of barricades or insulation, will be taken to protect Granville County Schools’ employees from hazardous ground potentials, depending on earth resistively and fault currents, which can develop within the first few feet or more outward from the grounding point closer to the line than permitted. 

12

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
10. EMERGENCY REMOVAL OR TAG AND LOCK 
In the event of an emergency in which the person responsible for removing the tag and lock cannot be located, Granville County Schools’ Maintenance Crew Leader, or Assistant Maintenance Crew Leader will remove the device in the presence of another employee. The person removing the device shall document the action in writing to the Safety & Health Manager. Details for removal are given in the Lock out/Tag out Plan. 

11. CONTROL OF HAZARDOUS ENERGY (LOCK-OUT/TAG-OUT) 
1. The extreme hazard of electrical equipment is the potential for personnel electrocution from contacting energized systems. 

2. Electrical equipment can also cause catastrophic property damage because of its potential as an ignition source for causing fire or explosion. 

3. These procedures comply with the requirements for the isolation or control of hazardous energy sources. 

4. The accidental release of energy during maintenance work can and frequently does cause severe injuries, amputations, and death. 

5. Energy can be present in the form of electricity, potential energy (due to gravity) stored in elevated masses, chemical corrosives, chemical toxicity, or pressure. 

6. The only exceptions are those situations involving “hot tap” operations. 

7. For this exception to be valid, Granville County Schools’ employees involved will demonstrate that the continuity of services is essential, that shutdown of the energy source is impractical, and that documented (written) procedures and special equipment have been implemented that will provide proven effective protection. All employees involved will have certified credentials on file with the Safety & Health manager and have express consent from GCS Administration. 
8. These procedures apply to all maintenance or installation operations conducted on Granville County Schools premises. 

13

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
12. TAG-OUT DEVICES 
1. Tags affixed to energy isolating devices are warning devices that do not provide the physical restraint on those devices that a lock would provide. 

2. Any tag so attached to an energy-isolating device will not be removed without authorization of the person attaching it, and it will never be bypassed, ignored, or otherwise defeated. 

3. Tags will be legible and understandable in order to be effective. 

4. Tags will be made of materials that will withstand environmental conditions encountered in the workplace. 

5. When utilized, tags will be securely attached to energy isolating devices so that they cannot be inadvertently or accidentally detached during use. 

6. Tag-out devices will be substantial enough to prevent inadvertent or accidental removal. 

7. Tag-out devices will warn against hazardous conditions if the machine or equipment is energized and will include appropriate warnings such as: 

DO NOT START 
DO NOT ENERGIZE 
DO NOT OPEN 
DO NOT OPERATE 
DO NOT CLOSE 
14

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
13. LOCK-OUT DEVICES 
Lockout devices and practices are listed as follows: 
1. Padlocks. Key operated padlocks are recommended and will be assigned individually. 

2. Multiple lock adapters will enable more than one employee to place their own padlock on the isolating device to guarantee that the machine or equipment will remain deactivated until each and every employee completes their own task, and only then will the last padlock be removed. 

3. Chains or other commercially available devices will be used to prevent valves from being opened or, in some cases, closed. The principle of multiple lock adapters still applies even when chains or other devices are used on operations requiring more than one employee. 

14. ENERGY-ISOLATING DEVICES 
1. If devices are not capable of being locked out, they will be modified so that they are capable of being locked out whenever major replacement, repair, renovation, or modification of the machine or equipment takes place. 

2. Whenever new machines or equipment are installed, energy-isolating devices for such machines or equipment will be designed to accept a lockout device. 

3. If an isolating device cannot be locked out for any reason, then additional steps will be taken to assure full employee protection such as removing fuses, blocking switches, blanking off lines, etc. 

4. If the machine or equipment is not capable of being locked out, a tag-out procedure will be documented and utilized. 

15

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
5. The tag-out procedure will provide full employee protection equivalent to a lockout system. 

6. For full employee protection, when a tag-out device is used on an energy-isolating device, the device will be attached at the same location that the lockout device would have been attached, and will demonstrate that the tag-out device will provide a level of safety that is equivalent to that of a lockout system. 

15. PLUG/CORD AND HOSE-CONNECTED TYPE EQUIPMENT 
1. When servicing or installing plug/cord or hose connected electrical, pneumatic, or hydraulically powered equipment, the cord or hose will be disconnected from the equipment to be worked on, prior to starting the work. 

2. A tag warning against reconnecting the plug or hose will be affixed to the plug or hose end. 

3. Any stored energy (e.g., capacitor voltage, hydraulic pressure) will be safely released prior to the start of maintenance or installation 
             16. ELECTRICALLY POWERED EQUIPMENT   

1. Electrically powered equipment will be de-energized and their source of electricity manually disconnected from them prior to the removal of protective covers or the start of other maintenance or installation work. 

2. It is important to recognize that locking and tagging on/off switches is often not sufficient to prevent accidental start up or prevent voltage from being present in the equipment. 

3. If the equipment is not wired properly (i.e., the polarity is reversed) or the switch is of the single pole type, voltage can be present even if the operating switch is in the off position. For these reasons, manual disconnects will be placed in the off position and/or the equipment’s power fuses removed from the motor control center. 

16

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
4. Every Granville County Schools’ employee working on the circuit or piece of equipment will place a pad lock and warning tag on the electrical isolation device (e.g., disconnect switch). 

5. Every Granville County Schools’ employee working on the circuit or piece of equipment will attempt to energize or start the piece of equipment prior to starting work. Each on/off switch capable of energizing the equipment will be “tried.” 

6. If the try step reveals that the equipment is capable of being energized, the proper disconnects will be located and locked out and the try step repeated. 

7. As every Granville County Schools’ employee completes their task, they will remove their padlock and tag from the isolating energy device. 

8. All protective covers or panels will be securely re-attached prior to energizing the equipment after work is completed. In the event that protective covers will be removed to make adjustments on energized equipment, appropriate guards will be constructed and attached in such a manner as to prevent employee contact with live circuitry capable of causing human injury. 

9. Such guards will be of durable construction, adequate to prevent injurious contact, and remain in place at all times that the equipment is energized. 

17. CHEMICAL AND/OR PRESSURIZED LINES 
Prior to working on any pressurized line or a line containing a toxic, flammable, reactive, or corrosive material, the following procedure will be implemented by Granville County Schools: 
1. The line to be serviced will have two block valves upstream of the work area or device to be serviced or installed, placed in the closed position and tagged. 

17

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
2. The bleed valve (between the two block valves) will be opened and tagged so that leakage of the valve upstream would be readily obvious. The line will be depressurized or drained in a safe manner. 

3. Lines will be broken in such a manner as to release pressure away from the employee. All solids or liquids drained will be safely collected. This procedure is called “double block and bleed.” 

Prior to working on any pressurized line or a line containing a toxic, flammable, reactive, or corrosive material, the following procedure will be implemented by Granville County Schools: 
1. If it is possible for pressure or line material to enter the work area from more than one direction, the line in each direction of travel will be “double blocked and bled” as described above. 

2. In the event that “double block and bleed” procedures are infeasible (i.e., the line is not provided with adequate valves), alternative measures will be implemented. 

3. One alternate measure is to place a solid “blind” in a flange located between the available upstream valve and the work area. If blinds are used they will be sufficiently corrosion and pressure-resistant to ensure that if the valve leaks, the blind will stop the material or pressure from reaching the work area. 

18. STORED MECHANICAL ENERGY 
1. In situations where equipment to be worked on has stored mechanical energy (e.g., in a flywheel or drop hammer), the stored energy will be released or blocked in a safe manner before starting maintenance or installation work. 

2. Effective blocking practices will include the installation of safety blocks or adequate supports. Under no circumstances will “bumper jacks” or “scissor jacks” be considered to be adequate blocks. 

18

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
19. ENERGY SAFETY TRAINING 
1. The purpose in providing training to employees is to ensure that they understand the purpose and function of the lock-out/tag-out program and procedures, and that they have the knowledge and skills required for the safe application, usage, and removal of energy controls. 

2. Granville County Schools’ employees who work around electrical equipment but who do not perform a primary duty of electrical system installation or maintenance will be briefed by their supervisor on the hazards of electricity and the proper precautions to observe. 

3. Each authorized Granville County Schools’ employee who will use a lock-out/tag-out procedure will receive training in the recognition of applicable hazardous energy sources, the type and magnitude of the energy available in the workplace, and the methods and means necessary for isolation and control. 

4. Granville County Schools’ employees will be retrained whenever there is a change in their job assignment; a change in machines, equipment, or processes that present a new hazard; or when there is a change in the lock-out/tag-out procedures. 

19

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
Electrical Self-Audit Safety Questions Page One
YES - NO Are your workplace electricians familiar with the OSHA Electrical Safety Orders? 

YES - NO Do you specify compliance with OSHA for all contract electrical work? 

YES - NO Are all employees required to report as soon as practicable any obvious hazard to life or property observed in connection with electrical equipment or lines? 

YES - NO Are employees instructed to make preliminary inspections and/or appropriate tests to determine what conditions exist before starting work on electrical equipment or lines? 

YES - NO When electrical equipment or lines are to be serviced, maintained or adjusted, are necessary switches opened, locked out and tagged whenever possible? 

YES - NO Are portable electrical tools and equipment grounded or of the double insulated type? 

YES - NO Are electrical appliances such as vacuum cleaners, polishers, vending machines grounded? 

YES - NO Do extension cords being used have a grounding conductor? 

YES - NO Are multiple plug adaptors prohibited? 

YES - NO Are ground-fault circuit interrupters installed on each temporary 15 or 20 ampere, 120 volt AC circuit at locations where construction, demolition, modifications, alterations or excavations are being performed? 

YES - NO Are all temporary circuits protected by suitable disconnecting switches or plug connectors at the junction with permanent wiring? 

YES - NO Is exposed wiring and cords with frayed or deteriorated insulation repaired or replaced promptly? 

YES - NO Are flexible cords and cables free of splices or taps? 

YES - NO Are clamps or other securing means provided on flexible cords or cables at plugs, receptacles, tools, equipments and is the cord jacket securely held in place? 

YES - NO Are all cord, cable and raceway connections intact and secure? 

YES - NO In wet or damp locations, are electrical tools and equipment appropriate for the use, or location, or otherwise protected? 

20

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
Electrical Self-Audit Safety Questions Page Two
YES - NO Is the location of electrical power lines and cables (over head, under ground, under floor, other side of walls) determined before digging, drilling or similar work is begun? 

YES - NO Are metal measuring tapes, ropes, hand lines or similar devices with metallic thread woven into the fabric prohibited where they could come in contact with energized parts of equipment or circuit conductors? 

YES - NO Is the use of metal ladders prohibited in areas where the ladder or the person using the ladder could come in contact with energized parts of equipment, fixtures or circuit conductors? 

YES - NO Are all disconnecting switches and circuit breakers labeled to indicate the use or equipment served? 

YES - NO Are disconnecting means always opened before fuses are replaced? 

YES - NO Do all interior wiring systems include provisions for grounding metal parts or electrical raceways, equipment and enclosures? 

YES - NO Are all electrical raceways and enclosures securely fastened in place? 

YES - NO Are all energized parts of electrical circuits and equipment guarded against accidental contact by approved cabinets or enclosures? 

YES - NO Is sufficient access and working space provided and maintained about all electrical equipment to permit ready and safe operations and maintenance? 

YES - NO Are all unused openings (including conduit knockouts) in electrical enclosures and fittings closed with appropriate covers, plugs or plates? 

YES - NO Are electrical enclosures such as switches, receptacles, junction boxes provided with tight-fitting covers or plates? 

YES - NO Are electrical enclosures such as switches, receptacles, tools, junction boxes provided with tight-fitting covers or plates? 

YES - NO Are disconnecting switches for electrical motors in excess of two horsepower capable of opening the circuit when the motor in a stalled condition without exploding? (Switches must be horsepower rated equal to or in excess of the motor hp rating.) 

YES - NO Is low voltage protection provided in the control device of motors driving machines or equipment which could cause probable injury from inadvertent starting? 

YES - NO Is each motor disconnecting switch or circuit breaker located within sight of the motor control device? 

21

Granville County Schools 
2010 ELECTRICAL SAFETY PLAN 
Electrical Self-Audit Safety Questions Page Three
YES - NO Is each motor located within sight of its controller or the controller disconnecting means capable of being locked in the open position, or is separate disconnecting means installed in the circuit within sight of the motor? 

YES - NO Is the controller for each motor in excess of two horsepower rated in horsepower equal or in excess of the rating of the motor it serves? 

YES - NO Are employees who regularly work on or around energized electrical equipment or lines instructed in cardio-pulmonary resuscitation (CPR) methods? 

YES - NO Are employees prohibited from working alone on energized lines or equipment over 600 volts? 

GRANVILLE COUNTY SCHOOLS 
Location:_________________________________

Reviewer’s Signature: ____________________________________________ 
Date Conducted: __________________________________________ 
22

                    








