## Chaparral MS
CHAPARRAL MIDDLE SCHOOL
| Existing Fixtures | [9 empty] | Proposed Fixtures |  |  |  |  | Demand Savings (kW/year) | Energy Savings (kWh/year) | Utility Cost Savings (kWh/year) | Unit Fixture Cost | Estimated Total Cost
|  |  | Fixture Data |  |  |  |  | Electric Demand (kW) | Annual Hours of Operation | Total Annual Energy Consumption (kWh) | Fixture Code | Fixture Description | Input kW | Electric Demand (kW) | Total Annual Energy Consumption (kWh)
| Building | Interior / Exterior | Description | Lamp Type | Mounting | kW | Fixture Qty
Ese | O | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 38 | 1.178 | 1717 | 2022.626 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.874 | 1500.658 | 0.304 | 521.968 | 120.2614 | 251.65 | 9562.7
Ese | O | Interior | PAR 8" | I36 | Recessed | 0.036 | 16 | 0.576 | 1717 | 988.992 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.136 | 233.512 | 0.44 | 755.48 | 174.0626 | 17.975 | 287.6
Ese | O | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 6 | 0.354 | 1717 | 607.818 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.156 | 267.852 | 0.198 | 339.966 | 78.3282 | 287.6 | 1725.6
Ese | O | Exterior | High Pressure Sodium Wall Pack | HPS70/1 | Wall Pack | 0.095 | 5 | 0.475 | 4100 | 1947.5 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.175 | 717.5 | 0 | 1230 | 283.392 | 1078.5 | 5392.5
Ese | P | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 90 | 8.01 | 1717 | 13753.17 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.51 | 6026.67 | 4.5 | 7726.5 | 1780.1856 | 287.6 | 25884
Ese | P | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 6 | 0.354 | 1717 | 607.818 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.204 | 350.268 | 0.15 | 257.55 | 59.3395 | 377.475 | 2264.85
Ese | A | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 24 | 2.136 | 1717 | 3667.512 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.936 | 1607.112 | 1.2 | 2060.4 | 474.7162 | 287.6 | 6902.4
Ese | A | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 3 | 0.177 | 1717 | 303.909 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.102 | 175.134 | 0.075 | 128.775 | 29.6698 | 377.475 | 1132.425
Ese | A | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 1 | 0.031 | 1717 | 53.227 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.023 | 39.491 | 0.008 | 13.736 | 3.1648 | 251.65 | 251.65
Ese | C | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 24 | 2.136 | 1717 | 3667.512 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.936 | 1607.112 | 1.2 | 2060.4 | 474.7162 | 287.6 | 6902.4
Ese | C | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 3 | 0.093 | 1717 | 159.681 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.069 | 118.473 | 0.024 | 41.208 | 9.4943 | 251.65 | 754.95
Ese | C | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 6 | 0.354 | 1717 | 607.818 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.204 | 350.268 | 0.15 | 257.55 | 59.3395 | 377.475 | 2264.85
Ese | D | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 36 | 3.204 | 1717 | 5501.268 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 1.404 | 2410.668 | 1.8 | 3090.6 | 712.0742 | 287.6 | 10353.6
Ese | D | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 6 | 0.186 | 1717 | 319.362 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.138 | 236.946 | 0.048 | 82.416 | 18.9886 | 251.65 | 1509.9
Ese | D | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 7 | 0.413 | 1717 | 709.121 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.238 | 408.646 | 0.175 | 300.475 | 69.2294 | 377.475 | 2642.325
Ese | E | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 48 | 4.272 | 1717 | 7335.024 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 1.872 | 3214.224 | 2.4 | 4120.8 | 949.4323 | 287.6 | 13804.8
Ese | E | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 2 | 0.062 | 1717 | 106.454 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.046 | 78.982 | 0.016 | 27.472 | 6.3295 | 251.65 | 503.3
Ese | E | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 3 | 0.177 | 1717 | 303.909 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.102 | 175.134 | 0.075 | 128.775 | 29.6698 | 377.475 | 1132.425
Ese | F | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 17 | 1.003 | 1717 | 1722.151 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.442 | 758.914 | 0.561 | 963.237 | 221.9298 | 287.6 | 4889.2
Ese | F | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 15 | 1.335 | 1717 | 2292.195 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.585 | 1004.445 | 0.75 | 1287.75 | 296.6976 | 287.6 | 4314
Ese | F | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 3 | 0.177 | 1717 | 303.909 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.102 | 175.134 | 0.075 | 128.775 | 29.6698 | 377.475 | 1132.425
Ese | G | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 48 | 4.272 | 1717 | 7335.024 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 1.872 | 3214.224 | 2.4 | 4120.8 | 949.4323 | 287.6 | 13804.8
Ese | G | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 2 | 0.062 | 1717 | 106.454 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.046 | 78.982 | 0.016 | 27.472 | 6.3295 | 251.65 | 503.3
Ese | G | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 2 | 0.118 | 1717 | 202.606 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.068 | 116.756 | 0.05 | 85.85 | 19.7798 | 377.475 | 754.95
Ese | H | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 48 | 4.272 | 1717 | 7335.024 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 1.536 | 2637.312 | 2.736 | 4697.712 | 1082.3528 | 341.525 | 16393.2
Ese | H | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 17 | 1.003 | 1717 | 1722.151 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.578 | 992.426 | 0.425 | 729.725 | 168.1286 | 377.475 | 6417.075
Ese | J | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 38 | 3.382 | 1717 | 5806.894 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 1.482 | 2544.594 | 1.9 | 3262.3 | 751.6339 | 287.6 | 10928.8
Ese | J | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 5 | 0.155 | 1717 | 266.135 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.115 | 197.455 | 0.04 | 68.68 | 15.8239 | 251.65 | 1258.25
Ese | J | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 19 | 1.121 | 1717 | 1924.757 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.646 | 1109.182 | 0.475 | 815.575 | 187.9085 | 377.475 | 7172.025
Ese | J | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 4 | 0.356 | 1717 | 611.252 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.128 | 219.776 | 0.228 | 391.476 | 90.1961 | 341.525 | 1366.1
Ese | J | Interior | Linear Fluorescent 4x4 | F32T8/4-s | Surface | 0.112 | 6 | 0.672 | 1717 | 1153.824 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.192 | 329.664 | 0.48 | 824.16 | 189.8865 | 341.525 | 2049.15
Ese | K | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 17 | 1.003 | 1717 | 1722.151 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.442 | 758.914 | 0.561 | 963.237 | 221.9298 | 287.6 | 4889.2
Ese | K | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 10 | 0.89 | 1717 | 1528.13 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.39 | 669.63 | 0.5 | 858.5 | 197.7984 | 287.6 | 2876
Ese | K | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 2 | 0.062 | 1717 | 106.454 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.046 | 78.982 | 0.016 | 27.472 | 6.3295 | 251.65 | 503.3
Ese | K | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 2 | 0.118 | 1717 | 202.606 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.068 | 116.756 | 0.05 | 85.85 | 19.7798 | 377.475 | 754.95
Ese | K | Exterior | High Pressure Sodium Wall Pack | HPS250/1 | Wall Pack | 0.295 | 2 | 0.59 | 4100 | 2419 | LED54/1-WP | LED Wall Pack Fixture (e.g. Lithonia DSXW2-30C-530-40K-T3M) | 0.054 | 0.108 | 442.8 | 0 | 1976.2 | 455.3165 | 629.125 | 1258.25
Ese | M | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 96 | 8.544 | 1717 | 14670.048 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.744 | 6428.448 | 4.8 | 8241.6 | 1898.8646 | 287.6 | 27609.6
Ese | M | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 4 | 0.124 | 1717 | 212.908 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.092 | 157.964 | 0.032 | 54.944 | 12.6591 | 251.65 | 1006.6
Ese | M | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 6 | 0.354 | 1717 | 607.818 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.204 | 350.268 | 0.15 | 257.55 | 59.3395 | 377.475 | 2264.85
Ese | M | Interior | Linear Fluorescent 2x4 | F32T8/4 | Recessed | 0.112 | 72 | 8.064 | 1717 | 13845.888 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 2.808 | 4821.336 | 5.256 | 9024.552 | 2079.2568 | 287.6 | 20707.2
Ese | SC | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 11 | 0.649 | 1717 | 1114.333 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.286 | 491.062 | 0.363 | 623.271 | 143.6016 | 287.6 | 3163.6
Ese | SC | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 82 | 7.298 | 1717 | 12530.666 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.198 | 5490.966 | 4.1 | 7039.7 | 1621.9469 | 287.6 | 23583.2
Ese | SC | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 28 | 0.868 | 1717 | 1490.356 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.644 | 1105.748 | 0.224 | 384.608 | 88.6137 | 251.65 | 7046.2
Ese | SC | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 1 | 0.089 | 1717 | 152.813 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.032 | 54.944 | 0.057 | 97.869 | 22.549 | 341.525 | 341.525
Ese | SC | Interior | Linear Fluorescent 2x4 | F32T8/4 | Recessed | 0.112 | 30 | 3.36 | 1717 | 5769.12 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 1.17 | 2008.89 | 2.19 | 3760.23 | 866.357 | 287.6 | 8628
Ese | Gym | Interior | Linear Fluorescent 2x4 | F32T8/4 | Recessed | 0.112 | 12 | 1.344 | 1717 | 2307.648 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.468 | 803.556 | 0.876 | 1504.092 | 346.5428 | 287.6 | 3451.2
Ese | Gym | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 42 | 3.738 | 1717 | 6418.146 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 1.638 | 2812.446 | 2.1 | 3605.7 | 830.7533 | 287.6 | 12079.2
Ese | Gym | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 3 | 0.093 | 1717 | 159.681 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.069 | 118.473 | 0.024 | 41.208 | 9.4943 | 251.65 | 754.95
Ese | Gym | Exterior | High Pressure Sodium Wall Pack | HPS70/1 | Wall Pack | 0.095 | 8 | 0.76 | 4100 | 3116 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.28 | 1148 | 0 | 1968 | 453.4272 | 1078.5 | 8628
Ese | Gym | Interior | Linear Fluorescent 2x4 | F32T8/6 | Recessed | 0.175 | 62 | 10.85 | 1717 | 18629.45 | LED59 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 2.418 | 4151.706 | 8.432 | 14477.744 | 3335.6722 | 287.6 | 17831.2
Ese | Gym | Interior | Linear Fluorescent 1x4 | F32T8/2-1 | Recessed | 0.059 | 12 | 0.708 | 1717 | 1215.636 | LED29 | LED Troffer 1'x4' (e.g. Lithonia VTL4-30L-LP840) | 0.029 | 0.348 | 597.516 | 0.36 | 618.12 | 142.4148 | 341.525 | 4098.3
[7 empty] | Total kW | 91.622 | Total kWh | 161663.949 |  |  | TOTALS | 37.37 | 65505.919 | 52.99 | 96158.03 | 22154.8101 |  | 315730.875

## Moorpark HS
MOORPARK HIGH SCHOOL
| Existing Fixtures | [9 empty] | Proposed Fixtures |  |  |  |  | Demand Savings (kW/year) | Energy Savings (kWh/year) | Utility Cost Savings (kWh/year) | Unit Fixture Cost | Estimated Total Cost
|  |  | Fixture Data |  |  |  |  | Electric Demand (kW) | Annual Hours of Operation | Total Annual Energy Consumption (kWh) | Fixture Code | Fixture Description | Input kW | Electric Demand (kW) | Total Annual Energy Consumption (kWh)
| Building | Interior / Exterior | Description | Lamp Type | Mounting | kW | Fixture Qty
Ese | A | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 51 | 4.539 | 1717 | 7793.463 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 1.989 | 3415.113 | 2.55 | 4378.35 | 787.6652 | 287.6 | 14667.6
Ese | A | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 21 | 1.239 | 1717 | 2127.363 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.546 | 937.482 | 0.693 | 1189.881 | 214.0596 | 287.6 | 6039.6
Ese | A | Interior | Linear Fluorescent 2x4 | F32T8/4-s | Surface | 0.112 | 13 | 1.456 | 1717 | 2499.952 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.416 | 714.272 | 1.04 | 1785.68 | 321.2438 | 341.525 | 4439.825
Ese | A | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 12 | 1.068 | 1717 | 1833.756 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.384 | 659.328 | 0.684 | 1174.428 | 211.2796 | 341.525 | 4098.3
Ese | A | Interior | Linear Fluorescent 2x4 | F32T8/2-s2 | Surface | 0.059 | 90 | 5.31 | 1717 | 9117.27 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 2.88 | 4944.96 | 2.43 | 4172.31 | 750.5986 | 341.525 | 30737.25
Ese | A | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 19 | 1.121 | 1717 | 1924.757 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.646 | 1109.182 | 0.475 | 815.575 | 146.7219 | 377.475 | 7172.025
Ese | A | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 42 | 1.302 | 1717 | 2235.534 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.966 | 1658.622 | 0.336 | 576.912 | 103.7865 | 251.65 | 10569.3
Ese | B | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 85 | 7.565 | 1717 | 12989.105 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.315 | 5691.855 | 4.25 | 7297.25 | 1312.7753 | 287.6 | 24446
Ese | B | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 21 | 1.239 | 1717 | 2127.363 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.546 | 937.482 | 0.693 | 1189.881 | 214.0596 | 287.6 | 6039.6
Ese | B | Interior | Linear Fluorescent 2x2 U-tube | FU31T8/2 | Recessed | 0.059 | 2 | 0.118 | 1717 | 202.606 | LED31 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2VTL2-33L-ADP-LP840) | 0.031 | 0.062 | 106.454 | 0.056 | 96.152 | 17.2977 | 179.75 | 359.5
Ese | B | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 4 | 0.356 | 1717 | 611.252 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.128 | 219.776 | 0.228 | 391.476 | 70.4265 | 341.525 | 1366.1
Ese | B | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 3 | 0.177 | 1717 | 303.909 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.102 | 175.134 | 0.075 | 128.775 | 23.1666 | 377.475 | 1132.425
Ese | B | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 38 | 1.178 | 1717 | 2022.626 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.874 | 1500.658 | 0.304 | 521.968 | 93.902 | 251.65 | 9562.7
Ese | B | Interior | Linear Fluorescent 2x4 | F32T8/8-p | Pendant | 0.224 | 3 | 0.672 | 1717 | 1153.824 | LED25 | LED Pendant Fixture 1'x4' (e.g. Lithonia GRD-MSL4-800LMF-30K) | 0.025 | 0.075 | 128.775 | 0.597 | 1025.049 | 184.4063 | 287.6 | 862.8
Ese | C | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 2 | 0.178 | 1717 | 305.626 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.078 | 133.926 | 0.1 | 171.7 | 30.8888 | 287.6 | 575.2
Ese | C | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 21 | 1.239 | 1717 | 2127.363 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.546 | 937.482 | 0.693 | 1189.881 | 214.0596 | 287.6 | 6039.6
Ese | C | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 18 | 1.062 | 1717 | 1823.454 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.612 | 1050.804 | 0.45 | 772.65 | 138.9997 | 377.475 | 6794.55
Ese | C | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 9 | 0.279 | 1717 | 479.043 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.207 | 355.419 | 0.072 | 123.624 | 22.24 | 251.65 | 2264.85
Ese | D | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 24 | 2.136 | 1717 | 3667.512 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.936 | 1607.112 | 1.2 | 2060.4 | 370.666 | 287.6 | 6902.4
Ese | D | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 25 | 1.475 | 1717 | 2532.575 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.65 | 1116.05 | 0.825 | 1416.525 | 254.8328 | 287.6 | 7190
Ese | D | Interior | Linear Fluorescent 2x2 | F17T8/2 | Recessed | 0.033 | 12 | 0.396 | 1717 | 679.932 | LED31 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2VTL2-33L-ADP-LP840) | 0.031 | 0.372 | 638.724 | 0.024 | 41.208 | 7.4133 | 179.75 | 2157
Ese | D | Interior | Linear Fluorescent 2x4 | F32T8/2-s2 | Surface | 0.059 | 4 | 0.236 | 1717 | 405.212 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.128 | 219.776 | 0.108 | 185.436 | 33.3599 | 341.525 | 1366.1
Ese | D | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 51 | 3.009 | 1717 | 5166.453 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 1.734 | 2977.278 | 1.275 | 2189.175 | 393.8326 | 377.475 | 19251.225
Ese | D | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 10 | 0.31 | 1717 | 532.27 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.23 | 394.91 | 0.08 | 137.36 | 24.7111 | 251.65 | 2516.5
Ese | D | Interior | Compact Fluorescent 8" | CFQ17/2 | Recessed | 0.048 | 7 | 0.336 | 1717 | 576.912 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.0595 | 102.1615 | 0.2765 | 474.7505 | 85.4076 | 17.975 | 125.825
Ese | D | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 23 | 2.185 | 4100 | 8958.5 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.805 | 3300.5 | 0 | 5658 | 1017.8742 | 600 | 13800
Ese | D | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 1 | 0.059 | 1717 | 101.303 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.034 | 58.378 | 0.025 | 42.925 | 7.7222 | 377.475 | 377.475
Ese | D | Exterior | High Pressure Sodium | HPS150/1 | Wall Pack | 0.188 | 15 | 2.82 | 4100 | 11562 | LED54/1-WP | LED Wall Pack Fixture (e.g. Lithonia DSXW2-30C-530-40K-T3M) | 0.054 | 0.81 | 3321 | 0 | 8241 | 1482.5559 | 350 | 5250
Ese | D | Exterior | High Pressure Sodium | HPS250/1 | Wall Pack | 0.295 | 12 | 3.54 | 4100 | 14514 | LED54/1-WP | LED Wall Pack Fixture (e.g. Lithonia DSXW2-30C-530-40K-T3M) | 0.054 | 0.648 | 2656.8 | 0 | 11857.2 | 2133.1103 | 350 | 4200
Ese | E | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 8 | 0.712 | 1717 | 1222.504 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 0.312 | 535.704 | 0.4 | 686.8 | 123.5553 | 287.6 | 2300.8
Ese | E | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 96 | 5.664 | 1717 | 9725.088 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 2.496 | 4285.632 | 3.168 | 5439.456 | 978.5581 | 287.6 | 27609.6
Ese | E | Interior | Linear Fluorescent 2x2 U-tube | FU31T8/2 | Recessed | 0.059 | 4 | 0.236 | 1717 | 405.212 | LED31 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2VTL2-33L-ADP-LP840) | 0.031 | 0.124 | 212.908 | 0.112 | 192.304 | 34.5955 | 179.75 | 719
Ese | E | Interior | Linear Fluorescent 2x4 | F32T8/2-s2 | Surface | 0.059 | 2 | 0.118 | 1717 | 202.606 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.064 | 109.888 | 0.054 | 92.718 | 16.68 | 341.525 | 683.05
Ese | E | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 104 | 6.136 | 1717 | 10535.512 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 3.536 | 6071.312 | 2.6 | 4464.2 | 803.1096 | 377.475 | 39257.4
Ese | E | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 2 | 0.062 | 1717 | 106.454 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.046 | 78.982 | 0.016 | 27.472 | 4.9422 | 251.65 | 503.3
Ese | E | Interior | Compact Fluorescent 8" | CFQ17/2 | Recessed | 0.048 | 1 | 0.048 | 1717 | 82.416 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.0085 | 14.5945 | 0.0395 | 67.8215 | 12.2011 | 17.975 | 17.975
Ese | E | Interior | PAR 8" | I36 | Recessed | 0.036 | 1 | 0.036 | 1717 | 61.812 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.0085 | 14.5945 | 0.0275 | 47.2175 | 8.4944 | 17.975 | 17.975
Ese | E | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 8 | 0.76 | 4100 | 3116 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.28 | 1148 | 0 | 1968 | 354.0432 | 600 | 4800
Ese | F | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 90 | 8.01 | 1717 | 13753.17 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.51 | 6026.67 | 4.5 | 7726.5 | 1389.9974 | 287.6 | 25884
Ese | G | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 90 | 8.01 | 1717 | 13753.17 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.51 | 6026.67 | 4.5 | 7726.5 | 1389.9974 | 287.6 | 25884
Ese | H | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 90 | 8.01 | 1717 | 13753.17 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.51 | 6026.67 | 4.5 | 7726.5 | 1389.9974 | 287.6 | 25884
Ese | I1 | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 12 | 1.14 | 4100 | 4674 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.42 | 1722 | 0 | 2952 | 531.0648 | 600 | 7200
Ese | I2 | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 12 | 1.14 | 4100 | 4674 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.42 | 1722 | 0 | 2952 | 531.0648 | 600 | 7200
Ese | J | Interior | Linear Fluorescent 2x4 | F32T8/3 | Recessed | 0.089 | 90 | 8.01 | 1717 | 13753.17 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 3.51 | 6026.67 | 4.5 | 7726.5 | 1389.9974 | 287.6 | 25884
Ese | J | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 33 | 1.947 | 1717 | 3342.999 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.858 | 1473.186 | 1.089 | 1869.813 | 336.3794 | 287.6 | 9490.8
Ese | J | Interior | Linear Fluorescent 2x4 | F32T8/4-s | Surface | 0.112 | 9 | 1.008 | 1717 | 1730.736 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.288 | 494.496 | 0.72 | 1236.24 | 222.3996 | 341.525 | 3073.725
Ese | J | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 6 | 0.534 | 1717 | 916.878 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.192 | 329.664 | 0.342 | 587.214 | 105.6398 | 341.525 | 2049.15
Ese | J | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 126 | 7.434 | 1717 | 12764.178 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 4.284 | 7355.628 | 3.15 | 5408.55 | 972.9981 | 377.475 | 47561.85
Ese | J | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 137 | 4.247 | 1717 | 7292.099 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 3.151 | 5410.267 | 1.096 | 1881.832 | 338.5416 | 251.65 | 34476.05
Ese | J | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 3 | 0.285 | 4100 | 1168.5 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.105 | 430.5 | 0 | 738 | 132.7662 | 600 | 1800
Ese | J | Interior | Metal Halide High Bay | MH400/1-p | Pendant | 0.458 | 40 | 18.32 | 1717 | 31455.44 | LED140/1 | LED High Bay Pendant (e.g. Lithonia JCBL-18000LM-ACCR-40K-70CRI | 0.14 | 5.6 | 9615.2 | 12.72 | 21840.24 | 3929.0592 | 1078.5 | 43140
Ese | J1 | Interior | Linear Fluorescent 2x2 U-tube | FU31T8/2 | Recessed | 0.059 | 3 | 0.177 | 1717 | 303.909 | LED31 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2VTL2-33L-ADP-LP840) | 0.031 | 0.093 | 159.681 | 0.084 | 144.228 | 25.9466 | 179.75 | 539.25
Ese | J1 | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 18 | 1.062 | 1717 | 1823.454 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.612 | 1050.804 | 0.45 | 772.65 | 138.9997 | 377.475 | 6794.55
Ese | K | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 72 | 4.248 | 1717 | 7293.816 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 1.872 | 3214.224 | 2.376 | 4079.592 | 733.9186 | 287.6 | 20707.2
Ese | L | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 72 | 4.248 | 1717 | 7293.816 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 1.872 | 3214.224 | 2.376 | 4079.592 | 733.9186 | 287.6 | 20707.2
Ese | M | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 24 | 1.416 | 1717 | 2431.272 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.624 | 1071.408 | 0.792 | 1359.864 | 244.6395 | 287.6 | 6902.4
Ese | M | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 24 | 1.416 | 1717 | 2431.272 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 0.816 | 1401.072 | 0.6 | 1030.2 | 185.333 | 377.475 | 9059.4
Ese | M | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 14 | 0.434 | 1717 | 745.178 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.322 | 552.874 | 0.112 | 192.304 | 34.5955 | 251.65 | 3523.1
Ese | M | Interior | PAR 8" | I36 | Recessed | 0.036 | 10 | 0.36 | 1717 | 618.12 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.085 | 145.945 | 0.275 | 472.175 | 84.9443 | 17.975 | 179.75
Ese | M | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 17 | 1.615 | 4100 | 6621.5 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 0.595 | 2439.5 | 0 | 4182 | 752.3418 | 600 | 10200
Ese | Rest | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 487 | 43.343 | 1717 | 74419.931 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 15.584 | 26757.728 | 27.759 | 47662.203 | 8574.4303 | 341.525 | 166322.675
Ese | Rest | Interior | Linear Fluorescent 2x4 | F32T8/2 | Recessed | 0.059 | 16 | 0.944 | 1717 | 1620.848 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.416 | 714.272 | 0.528 | 906.576 | 163.093 | 287.6 | 4601.6
Ese | Rest | Interior | Linear Fluorescent 2x4 | F32T8/4-s | Surface | 0.112 | 113 | 12.656 | 1717 | 21730.352 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 3.616 | 6208.672 | 9.04 | 15521.68 | 2792.3502 | 341.525 | 38592.325
Ese | Rest | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 156 | 9.204 | 1717 | 15803.268 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 5.304 | 9106.968 | 3.9 | 6696.3 | 1204.6644 | 377.475 | 58886.1
Ese | Rest | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 7 | 0.217 | 1717 | 372.589 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 0.161 | 276.437 | 0.056 | 96.152 | 17.2977 | 251.65 | 1761.55
Ese | Rest | Interior | Compact Fluorescent 8" | CFQ17/2 | Recessed | 0.048 | 78 | 3.744 | 1717 | 6428.448 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.663 | 1138.371 | 3.081 | 5290.077 | 951.6849 | 17.975 | 1402.05
Ese | Rest | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 88 | 8.36 | 4100 | 34276 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 3.08 | 12628 | 0 | 21648 | 3894.4752 | 600 | 52800
Ese | Rest | Interior | Metal Halide High Bay | MH400/1-p | Pendant | 0.458 | 46 | 21.068 | 1717 | 36173.756 | LED140/1 | LED High Bay Pendant (e.g. Lithonia JCBL-18000LM-ACCR-40K-70CRI | 0.14 | 6.44 | 11057.48 | 14.628 | 25116.276 | 4518.4181 | 1078.5 | 49611
[7 empty] | Total kW | 242.979 | Total kWh | 469251.578 |  |  | TOTALS | 99.1665 | 187338.3095 | 129.1305 | 281913.2685 | 50716.197 |  | 988330.575

## Mountain Meadows ES
MOUNTAIN MEADOWS ES
| Existing Fixtures | [9 empty] | Proposed Fixtures |  |  |  |  | Demand Savings (kW/year) | Energy Savings (kWh/year) | Utility Cost Savings (kWh/year) | Unit Fixture Cost | Estimated Total Cost
|  |  | Fixture Data |  |  |  |  | Electric Demand (kW) | Annual Hours of Operation | Total Annual Energy Consumption (kWh) | Fixture Code | Fixture Description | Input kW | Electric Demand (kW) | Total Annual Energy Consumption (kWh)
| Building | Interior / Exterior | Description | Lamp Type | Mounting | kW | Fixture Qty
Epr | All | Interior | Linear Fluorescent 2x4 | F32T8/4 | Recessed | 0.112 | 287 | 32.144 | 1288 | 41401.472 | LED39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 11.193 | 14416.584 | 20.951 | 26984.888 | 5361.8972 | 287.6 | 82541.2
Epr | All | Exterior | High Pressure Sodium | HPS70/1-c | Canopy | 0.095 | 25 | 2.375 | 4100 | 9737.5 | LED35/1-c | LED Canopy Fixture (e.g. Lithonia KACM-20C-530) | 0.035 | 0.875 | 3587.5 | 0 | 6150 | 1222.005 | 683.05 | 17076.25
Epr | All | Interior | Linear Fluorescent 1x4 | F32T8/2-s | Surface | 0.059 | 47 | 2.773 | 1288 | 3571.624 | LED34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 1.598 | 2058.224 | 1.175 | 1513.4 | 300.7126 | 377.475 | 17741.325
Epr | All | Interior | Compact Fluorescent 8" | CFQ17/2 | Recessed | 0.048 | 1 | 0.048 | 1288 | 61.824 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.0085 | 10.948 | 0.0395 | 50.876 | 10.1091 | 17.975 | 17.975
Epr | All | Exterior | High Pressure Sodium | HPS70/1 | Wall Pack | 0.095 | 31 | 2.945 | 4100 | 12074.5 | LED35/1 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 | 1.085 | 4448.5 | 0 | 7626 | 1515.2862 | 1078.5 | 33433.5
Epr | All | Interior | Linear Fluorescent 2x4 | F32T8/3-s | Surface | 0.089 | 123 | 10.947 | 1288 | 14099.736 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 3.936 | 5069.568 | 7.011 | 9030.168 | 1794.2944 | 341.525 | 42007.575
Epr | All | Interior | Linear Fluorescent 1x4 | F32T8/2 | Recessed | 0.059 | 2 | 0.118 | 1288 | 151.984 | LED26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 0.052 | 66.976 | 0.066 | 85.008 | 16.8911 | 287.6 | 575.2
Epr | All | Interior | Linear Fluorescent 2x2 U-tube | FU31T8/2 | Recessed | 0.059 | 16 | 0.944 | 1288 | 1215.872 | LED31 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2VTL2-33L-ADP-LP840) | 0.031 | 0.496 | 638.848 | 0.448 | 577.024 | 114.6547 | 179.75 | 2876
Epr | All | Interior | Linear Fluorescent 1x4 | F32T8/1-s | Surface | 0.031 | 104 | 3.224 | 1288 | 4152.512 | LED23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 2.392 | 3080.896 | 0.832 | 1071.616 | 212.9301 | 251.65 | 26171.6
Epr | All | Interior | Linear Fluorescent 2x4 | F32T8/4-s | Surface | 0.112 | 12 | 1.344 | 1288 | 1731.072 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.384 | 494.592 | 0.96 | 1236.48 | 245.6886 | 341.525 | 4098.3
Epr | All | Interior | Linear Fluorescent 4x4 | F32T8/6-s | Surface | 0.175 | 8 | 1.4 | 1288 | 1803.2 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.256 | 329.728 | 1.144 | 1473.472 | 292.7789 | 341.525 | 2732.2
Epr | All | Interior | Linear Fluorescent 4x4 | F32T8/4-s | Surface | 0.112 | 2 | 0.224 | 1288 | 288.512 | LED32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 0.064 | 82.432 | 0.16 | 206.08 | 40.9481 | 341.525 | 683.05
Epr | All | Exterior | Compact Fluorescent 8" | CFQ17/2 | Recessed | 0.048 | 17 | 0.816 | 4100 | 3345.6 | LED8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 | 0.1445 | 592.45 | 0 | 2753.15 | 547.0509 | 17.975 | 305.575
[7 empty] | Total kW | 59.302 | Total kWh | 93635.408 |  |  | TOTALS | 22.484 | 34877.246 | 32.7865 | 58758.162 | 11675.2468 |  | 230259.75

## Existing Lighting Schedule
Existing | [5 empty] | Proposed |  |  |  | Incentive Estimates |  |  |  |  | 0.0725 | 50% | 0.15
Fixture Code | Lamp Code | Lamp Wattage | Lamps/ Fixture | Description | kW/Fixt* (App. B) | Fixture Code | Lamp Code | Lamp Wattage | Description | kW/Fixt | klm | LPW | Incentive | Material Cost/ Fixture | Sales Tax | Labor Cost/Fixture (1) | Contractor O&P (2) | Total Cost (4)
F17T8/1 | F21ILL | 17 | 1 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO | 0.02 | F17T8/1 | F21ILL | 17 | No Change | 0.02 |  |  |  | 0 | 0 |  | 0 | 0
F17T8/2 | F22ILL | 17 | 2 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO | 0.033 | LED31 | LED31 | 0 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2VTL2-33L-ADP-LP840) | 0.031 | 3.941 | 126 | 23.646 | 100 | 7.25 | 50 | 22.5 | 179.75
F17T8/3 | F23ILL | 17 | 3 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO | 0.047 | F17T8/3 | F23ILL | 17 | No Change | 0.047 |  |  |  | 0 | 0 | 0 | 0 | 0
F17T8/4 | F24ILL | 17 | 4 | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, NLO | 0.061 | F17T8/4 | F24ILL | 17 | No Change | 0.061 |  |  |  | 0 | 0 | 0 | 0 | 0
F28T8/1 | F41WLL | 30 | 1 | 82 CRI, 18,000 HR. RSR, Fluorescent, (1) 48'' T-8 lamp, Premium PRS Ballast, NLO | 0.026 | F28T8/1 | F41WLL | 28 | No Change | 0.026 |  |  |  | 0 | 0 | 0 | 0 | 0
F28T8/2 | F42WLL | 30 | 2 | 82 CRI, 18,000 HR. RSR, Fluorescent, (2) 48'' T-8 lamp, Premium PRS Ballast, NLO | 0.052 | F28T8/2 | F42WLL | 28 | No Change | 0.052 |  |  |  | 0 | 0 | 0 | 0 | 0
F28T8/3 | F43WLL | 30 | 3 | 82 CRI, 18,000 HR. RSR, Fluorescent, (3) 48'' T-8 lamp, Premium PRS Ballast, NLO | 0.076 | F28T8/3 | F43WLL | 28 | No Change | 0.076 |  |  |  | 0 | 0 | 0 | 0 | 0
F28T8/4 | F44WLL | 30 | 4 | 82 CRI, 18,000 HR. RSR, Fluorescent, (4) 48'' T-8 lamp, Premium PRS Ballast, NLO | 0.098 | F28T8/4 | F44WLL | 28 | No Change | 0.098 |  |  |  | 0 | 0 | 0 | 0 | 0
F32T8/1 | F41ILL | 32 | 1 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO | 0.031 | LED22 | LED22 | 22 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.022 |  |  |  | 0 | 0 | 0 | 0 | 0
F32T8/1-s | F41ILL | 32 | 1 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO | 0.031 | LED23 | LED23 | 23 | LED Surface 4' (e.g. Deco DACH-LED-4-23-40 | 0.023 | 2.56 | 130 | 15.36 | 140 | 10.15 | 70 | 31.5 | 251.65
F32T8/2-1 | F42ILL | 32 | 2 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO | 0.059 | LED29 | LED29 | 29 | LED Troffer 1'x4' (e.g. Lithonia VTL4-30L-LP840) | 0.029 | 3.006 | 104 | 0 | 190 | 13.775 | 95 | 42.75 | 341.525
F32T8/2 | F42ILL | 32 | 2 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO | 0.059 | LED26 | LED26 | 26 | LED Troffer 2'x4' (e.g. Lithonia 2VTL4-30L-LP840) | 0.026 | 3.836 | 146 | 30.688 | 160 | 11.6 | 80 | 36 | 287.6
F32T8/2-s | F42ILL | 32 | 2 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO | 0.059 | LED34 | LED34 | 34 | LED Surface 1'x4' (e.g. Deco DSW-LED-4-35-40) | 0.034 | 4.42 | 145 | 35.36 | 210 | 15.225 | 105 | 47.25 | 377.475
F32T8/2-p | F42ILL | 32 | 2 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO | 0.059 | LED25 | LED25 | 25 | LED Pendant Fixture 1'x4' (e.g. Lithonia GRD-MSL4-800LMF-30K) | 0.025 | 3.303 | 133 | 0 | 160 | 11.6 | 80 | 36 | 287.6
F32T8/2-s2 | F42ILL | 32 | 2 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO | 0.059 | LED32 | LED32 | 32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 4.059 | 126 | 24.354 | 190 | 13.775 | 95 | 42.75 | 341.525
F32T8/3 | F43ILL | 32 | 3 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO | 0.089 | LED39 | LED39 | 39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 5.209 | 133 | 31.254 | 160 | 11.6 | 80 | 36 | 287.6
F32T8/3-s | F43ILL | 32 | 3 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO | 0.089 | LED32 | LED32 | 32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 4.059 | 126 | 24.354 | 190 | 13.775 | 95 | 42.75 | 341.525
F32T8/4 | F44ILL | 32 | 4 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO | 0.112 | LED39 | LED39 | 39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 5.209 | 133 | 31.254 | 160 | 11.6 | 80 | 36 | 287.6
F32T8/4-s | F44ILL | 32 | 4 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO | 0.112 | LED32 | LED32 | 32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 4.059 | 126 | 24.354 | 190 | 13.775 | 95 | 42.75 | 341.525
F32T8/6 | F46ILL | 32 | 6 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, NLO | 0.175 | LED59 | LED59 | 59 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4-48L-LP840) | 0.039 | 5.209 | 133 | 31.254 | 160 | 11.6 | 80 | 36 | 287.6
F32T8/6-s | F46ILL | 32 | 6 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (6) 48", T-8 lamp, Instant Start Ballast, NLO | 0.175 | LED32 | LED32 | 32 | LED Surface 2'x4' (e.g. Lithonia 2TLX4-40L-A12-LP850) | 0.032 | 4.059 | 126 | 24.354 | 190 | 13.775 | 95 | 42.75 | 341.525
F32T8/8-p | F48ILL | 32 | 8 | 70 CRI, 20,000 Hr. RSR, Fluorescent, (8) 48", T-8 lamp, Instant Start Ballast, NLO | 0.224 | LED25 | LED25 | 25 | LED Pendant Fixture 1'x4' (e.g. Lithonia GRD-MSL4-800LMF-30K) | 0.025 | 3.303 | 133 | 0 | 160 | 11.6 | 80 | 36 | 287.6
F96T8/1 | F81ILL | 59 | 1 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO | 0.058 | LED31 | LED31 | 31 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T8/2-p | F82ILL | 59 | 2 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO | 0.109 | LED50 | LED50 | 50 | LED Pendant Fixture 1'x4' (e.g. Lithonia GRD-MSL8-800LMF-35K) | 0.05 | 6.802 | 137 | 0 | 160 | 11.6 | 80 | 36 | 287.6
F96T8/3 | F83ILL | 59 | 3 | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO | 0.167 | LED47/2 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.094 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T8/4 | F84ILL | 59 | 4 | Fluorescent, (4) 96", T-8 lamp, Instant Start Ballast, NLO | 0.219 | LED47/2 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.094 |  |  | 0 | 0 | 0 | 0 | 0 | 0
FU31T8/2 | FU2ILL | 32 | 2 | Fluorescent, (2) U-Tube, T-8 lamp, Instand Start Ballast | 0.059 | LED31 | LED31 | 31 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2VTL2-33L-ADP-LP840) | 0.031 | 3.941 | 126 | 23.646 | 100 | 7.25 | 50 | 22.5 | 179.75
F20T12/1 | F21SS | 20 | 1 | Fluorescent, (1) 24", STD lamp | 0.028 | LED25 | LED25 | 25 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2RTLEDR) | 0.025 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F20T12/2 | F22SS | 20 | 2 | Fluorescent, (2) 24", STD lamp | 0.056 | LED25 | LED25 | 25 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2RTLEDR) | 0.025 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F20T12/3 | F23SS | 20 | 3 | Fluorescent, (3) 24", STD lamp | 0.062 | LED38 | LED38 | 38 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2RTLEDR) | 0.038 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F20T12/4 | F24SS | 20 | 4 | Fluorescent, (4) 24", STD lamp | 0.112 | LED38 | LED38 | 38 | LED Volumetric Kit 2'x2' (e.g. Lithonia 2RTLEDR) | 0.038 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F40T12/1 | F41SIL | 39 | 1 | Fluorescent, (1) 48", STD IS lamp, Electronic ballast | 0.046 | LED31 | LED31 | 31 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F40T12/2 | F42SIL | 39 | 2 | Fluorescent, (2) 48", STD IS lamp, Electronic ballast | 0.074 | LED31 | LED31 | 31 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F40T12/3 | F43SIL | 39 | 3 | Fluorescent, (3) 48", STD IS lamp, Electronic ballast | 0.12 | LED39 | LED39 | 39 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.039 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F40T12/4 | F44SIL | 39 | 4 | Fluorescent, (4) 48", STD IS lamp, Electronic ballast | 0.148 | LED47 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.047 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F40T12/6 | F46SIL | 39 | 6 | Fluorescent, (6) 48", STD IS lamp, Electronic ballast | 0.24 | LED70 | LED70 | 70 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.07 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F40T12/8 | F48SIL | 39 | 8 | Fluorescent, (8) 48", STD IS lamp, Electronic ballast | 0.296 | LED70 | LED70 | 70 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.07 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F48T12HO/2 | F42SHS | 60 | 2 | Fluorescent, (2) 48", STD HO lamp | 0.145 | LED47 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.047 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12/1 | F81ES | 60 | 1 | Fluorescent, (1) 96", ES lamp | 0.075 | LED31 | LED31 | 31 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12/2 | F82ES | 60 | 2 | Fluorescent, (2) 96", ES lamp | 0.128 | LED31/2 | LED31 | 31 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.062 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12/3 | F83ES | 60 | 3 | Fluorescent, (3) 96", ES lamp | 0.203 | LED47/2 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.094 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12/4 | F84ES | 60 | 4 | Fluorescent, (4) 96", ES lamp | 0.256 | LED47/2 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.094 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12HO/1 | F81EHS | 95 | 1 | Fluorescent, (1) 96", ES HO lamp | 0.112 | LED31 | LED31 | 31 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12HO/2 | F82EHS | 95 | 2 | Fluorescent, (2) 96", ES HO lamp | 0.227 | LED31/2 | LED31 | 31 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.062 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12HO/3 | F83EHS | 95 | 3 | Fluorescent, (3) 96", ES HO lamp | 0.38 | LED47/2 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.094 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F96T12HO/4 | F84EHS | 95 | 4 | Fluorescent, (4) 96", ES HO lamp | 0.454 | LED47/2 | LED47 | 47 | LED Volumetric Kit 2'x4' (e.g. Lithonia 2VTL4) | 0.094 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F24T5/HO/2 | F22PHL | 24 | 2 | Fluorescent, (2) 22", T5/HO lamp, Instant Start Ballast | 0.052 | F24T5/HO/2 | F22PHL | 24 | No Change | 0.052 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F54T5/HO/2 | F42PHL | 54 | 2 | Fluorescent, (2) 46", T5/HO lamp, Instant Start Ballast | 0.117 | F54T5/HO/2 | F42PHL | 54 | No Change | 0.117 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F54T5/HO/4 | F44PHL/2 | 54 | 4 | Fluorescent, (4) 46", T5/HO lamp, (2) Instant Start Ballast | 0.234 | F54T5/HO/4 | F44PHL/2 | 54 | No Change | 0.234 |  |  | 0 | 0 | 0 | 0 | 0 | 0
F54T5/HO/6 | F46PHL/3 | 54 | 6 | Fluorescent, (6) 46", T5/HO lamp, (3) Instant Start Ballast | 0.351 | F54T5/HO/6 | F46PHL/3 | 54 | No Change | 0.351 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ10/1 | CFQ10/1 | 10 | 1 | Compact Fluorescent, quad, (1) 10W lamp | 0.015 | CFQ10/1 | CFQ10/1 | 10 | No Change | 0.015 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ13/1 | CFQ13/1 | 13 | 1 | Compact Fluorescent, quad, (1) 13W lamp | 0.017 | CFQ13/1 | CFQ13/1 | 13 | No Change | 0.017 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ13/2 | CFQ13/2 | 13 | 2 | Compact Fluorescent, quad, (2) 13W lamp | 0.031 | CFQ13/2 | CFQ13/2 | 13 | No Change | 0.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ13/3 | CFQ13/3 | 13 | 3 | Compact Fluorescent, quad, (3) 13W lamp | 0.048 | CFQ13/3 | CFQ13/3 | 13 | No Change | 0.048 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ15/1 | CFQ15/1 | 15 | 1 | Compact Fluorescent, quad, (1) 15W lamp | 0.02 | CFQ15/1 | CFQ15/1 | 15 | No Change | 0.02 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ17/1 | CFQ17/1 | 17 | 1 | Compact Fluorescent, quad, (1) 17W lamp | 0.024 | CFQ17/1 | CFQ17/1 | 17 | No Change | 0.024 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ17/2 | CFQ17/2 | 17 | 2 | Compact Fluorescent, quad, (2) 17W lamp | 0.048 | LED8.5 | LED8.5 | 8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 |  |  | 0 | 10 | 0.725 | 5 | 2.25 | 17.975
CFQ18/1 | CFQ18/1 | 18 | 1 | Compact Fluorescent, quad, (1) 18W lamp | 0.026 | CFQ18/1 | CFQ18/1 | 18 | No Change | 0.026 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ18/2 | CFQ18/2 | 18 | 2 | Compact Fluorescent, quad, (2) 18W lamp | 0.045 | CFQ18/2 | CFQ18/2 | 18 | No Change | 0.045 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ18/4 | CFQ18/4 | 18 | 2 | Compact Fluorescent, quad, (4) 18W lamp | 0.09 | CFQ18/4 | CFQ18/4 | 18 | No Change | 0.09 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ20/1 | CFQ20/1 | 20 | 1 | Compact Fluorescent, quad, (1) 20W lamp | 0.023 | CFQ20/1 | CFQ20/1 | 20 | No Change | 0.023 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ20/2 | CFQ20/2 | 20 | 2 | Compact Fluorescent, quad, (2) 20W lamp | 0.046 | CFQ20/2 | CFQ20/2 | 20 | No Change | 0.046 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ22/1 | CFQ22/1 | 22 | 1 | Compact Fluorescent, Quad, (1) 22W lamp | 0.024 | CFQ22/1 | CFQ22/1 | 22 | No Change | 0.024 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ22/2 | CFQ22/2 | 22 | 2 | Compact Fluorescent, Quad, (2) 22W lamp | 0.048 | CFQ22/2 | CFQ22/2 | 22 | No Change | 0.048 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ22/3 | CFQ22/3 | 22 | 3 | Compact Fluorescent, Quad, (3) 22W lamp | 0.072 | CFQ22/3 | CFQ22/3 | 22 | No Change | 0.072 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ25/1 | CFQ25/1 | 25 | 1 | Compact Fluorescent, Quad, (1) 25W lamp | 0.033 | CFQ25/1 | CFQ25/1 | 25 | No Change | 0.033 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ25/2 | CFQ25/2 | 25 | 2 | Compact Fluorescent, Quad, (2) 25W lamp | 0.066 | CFQ25/2 | CFQ25/2 | 25 | No Change | 0.066 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ26/1 | CFQ26/1 | 26 | 1 | Compact Fluorescent, quad, (1) 26W lamp | 0.033 | CFQ26/1 | CFQ26/1 | 26 | No Change | 0.033 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ26/2 | CFQ26/2 | 26 | 2 | Compact Fluorescent, quad, (2) 26W lamp | 0.066 | CFQ26/2 | CFQ26/2 | 26 | No Change | 0.066 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ26/3 | CFQ26/3 | 26 | 3 | Compact Fluorescent, quad, (3) 26W lamp | 0.099 | CFQ26/3 | CFQ26/3 | 26 | No Change | 0.099 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ28/1 | CFQ28/1 | 28 | 1 | Compact Fluorescent, quad, (1) 28W lamp | 0.033 | CFQ28/1 | CFQ28/1 | 28 | No Change | 0.033 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ42/1 | CFQ42/1 | 42 | 1 | Compact Fluorescent, quad, (1) 42W lamp | 0.047 | CFQ42/1 | CFQ42/1 | 42 | No Change | 0.047 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ42/2 | CFQ42/2 | 42 | 2 | Compact Fluorescent, quad, (2) 42W lamp | 0.094 | CFQ42/2 | CFQ42/2 | 42 | No Change | 0.094 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ9/1 | CFQ9/1 | 9 | 1 | Compact Fluorescent, Quad, (1) 9W lamp | 0.014 | CFQ9/1 | CFQ9/1 | 9 | No Change | 0.014 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFQ9/2 | CFQ9/2 | 9 | 2 | Compact Fluorescent, Quad, (2) 9W lamp | 0.023 | CFQ9/2 | CFQ9/2 | 9 | No Change | 0.023 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT13/1 | CFT13/1 | 13 | 1 | Compact Fluorescent, twin, (1) 13W lamp | 0.017 | CFT13/1 | CFT13/1 | 13 | No Change | 0.017 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT13/2 | CFT13/2 | 13 | 2 | Compact Fluorescent, twin, (2) 13W lamp | 0.031 | CFT13/2 | CFT13/2 | 13 | No Change | 0.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT13/3 | CFT13/3 | 13 | 3 | Compact Fluorescent, twin, (3) 13 W lamp | 0.048 | CFT13/3 | CFT13/3 | 13 | No Change | 0.048 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT18/1 | CFT18/1 | 18 | 1 | Compact Fluorescent, Long twin., (1) 18W lamp | 0.024 | CFT18/1 | CFT18/1 | 18 | No Change | 0.024 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT22/1 | CFT22/1 | 22 | 1 | Compact Fluorescent, twin, (1) 22W lamp | 0.027 | CFT22/1 | CFT22/1 | 22 | No Change | 0.027 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT22/2 | CFT22/2 | 22 | 2 | Compact Fluorescent, twin, (2) 22W lamp | 0.054 | CFT22/2 | CFT22/2 | 22 | No Change | 0.054 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT22/4 | CFT22/4 | 22 | 4 | Compact Fluorescent, twin, (4) 22W lamp | 0.108 | CFT22/4 | CFT22/4 | 22 | No Change | 0.108 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT24/1 | CFT24/1 | 24 | 1 | Compact Fluorescent, long twin, (1) 24W lamp | 0.032 | CFT24/1 | CFT24/1 | 24 | No Change | 0.032 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT28/1 | CFT28/1 | 28 | 1 | Compact Fluorescent, twin, (1) 28W lamp | 0.033 | CFT28/1 | CFT28/1 | 28 | No Change | 0.033 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT28/2 | CFT28/2 | 28 | 2 | Compact Fluorescent, twin, (2) 28W lamp | 0.066 | CFT28/2 | CFT28/2 | 28 | No Change | 0.066 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT36/1 | CFT36/1 | 36 | 1 | Compact Fluorescent, long twin, (1) 36W lamp | 0.051 | CFT36/1 | CFT36/1 | 36 | No Change | 0.051 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT40/1 | CFT40/1 | 40 | 1 | Compact Fluorescent, twin, (1) 40W lamp | 0.046 | CFT40/1 | CFT40/1 | 40 | No Change | 0.046 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT40/2 | CFT40/2 | 40 | 2 | Compact Fluorescent, twin, (2) 40W lamp | 0.085 | CFT40/2 | CFT40/2 | 40 | No Change | 0.085 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT40/3 | CFT40/3 | 40 | 3 | Compact Fluorescent, twin, (3) 40 W lamp | 0.133 | CFT40/3 | CFT40/3 | 40 | No Change | 0.133 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT52/1 | CFT52/1 | 52 | 1 | Compact Fluorescent, twin, (1) 52W lamp | 0.065 | CFT52/1 | CFT52/1 | 52 | No Change | 0.065 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT52/2 | CFT52/1 | 52 | 2 | Compact Fluorescent, twin, (2) 52W lamp | 0.13 | CFT52/2 | CFT52/1 | 52 | No Change | 0.13 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT5/1 | CFT5/1 | 5 | 1 | Compact Fluorescent, twin, (1) 5W lamp | 0.009 | CFT5/1 | CFT5/1 | 5 | No Change | 0.009 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT5/2 | CFT5/2 | 5 | 2 | Compact Fluorescent, twin, (2) 5W lamp | 0.018 | CFT5/2 | CFT5/2 | 5 | No Change | 0.018 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT6/1 | CFT6/1 | 6 | 1 | Compact Fluorescent, twin, (1) 6W lamp | 0.009 | CFT6/1 | CFT6/1 | 6 | No Change | 0.009 |  |  | 0 | 0 | 0 | 0 | 0 | 0
CFT7/1 | CFT7/1 | 7 | 1 | Compact Fluorescent, twin, (1) 7W lamp | 0.01 | CFT7/1 | CFT7/1 | 7 | No Change | 0.01 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
CFT7/2 | CFT7/2 | 7 | 2 | Compact Fluorescent, twin, (2) 7W lamp | 0.021 | CFT7/2 | CFT7/2 | 7 | No Change | 0.021 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
CFT9/1 | CFT9/1 | 9 | 1 | Compact Fluorescent, twin, (1) 9W lamp | 0.011 | CFT9/1 | CFT9/1 | 9 | No Change | 0.011 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
CFT9/2 | CFT9/2 | 9 | 2 | Compact Fluorescent, twin, (2) 9W lamp | 0.023 | CFT9/2 | CFT9/2 | 9 | No Change | 0.023 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
CFT9/3 | CFT9/3 | 9 | 3 | Compact Fluorescent, twin, (3) 9 W lamp | 0.034 | CFT9/3 | CFT9/3 | 9 | No Change | 0.034 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
CFT84/1 | CFT84/1 | 84 | 1 | Compact Fluorescent, twin, (1) 84W MR16 lamp | 0.1 | LED13/1 | LED13 | 12.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0125 |  |  | 0 | 0 | 0 | 0 | 0 | 0
H60/1 | H60/1 | 60 | 1 | Halogen Incandescent, (1) 60W lamp | 0.06 | LED13/1 | LED13 | 12.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0125 |  |  | 0 | 0 | 0 | 0 | 0 | 0
H75/1 | H75/1 | 75 | 1 | Halogen Incandescent, (1) 75W lamp | 0.075 | LED13/1 | LED13 | 12.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0125 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
H90/1 | H90/1 | 90 | 1 | Halogen Incandescent, (1) 90W lamp | 0.09 | LED22/1 | LED22 | 22 | LED A21 Lamp (e.g. Philips EnduraLED) | 0.022 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
H100/1 | H100/1 | 100 | 1 | Halogen Incandescent, (1) 100W lamp | 0.1 | LED22/1 | LED22 | 22 | LED A21 Lamp (e.g. Philips EnduraLED) | 0.022 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
H150/1 | H150/1 | 150 | 1 | Halogen Incandescent, (1) 150W lamp | 0.15 | LED22/1 | LED22 | 22 | LED A21 Lamp (e.g. Philips EnduraLED) | 0.022 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
H250/1 | H250/1 | 250 | 1 | Halogen Incandescent, (1) 250W lamp | 0.25 | LED75/1-WP | LED75 | 75 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.075 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
H500/1 | H500/1 | 500 | 1 | Halogen Incandescent, (1) 500W lamp | 0.5 | LED200/1 | LED200 | 200 | LED High Bay Pendant Light Fixture (e.g. Philips HBX) | 0.201 |  |  | 0 | 100 | 7.25 | 50 | 22.5 | 179.75
I36 | I36/1 | 36 | 1 | Incandescent, (1) 36W lamp | 0.036 | LED8.5 | LED8.5 | 8.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0085 |  |  | 0 | 10 | 0.725 | 5 | 2.25 | 17.975
I60/1 | I60/1 | 60 | 1 | Incandescent, (1) 60W lamp | 0.06 | LED13/1 | LED13 | 12.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0125 |  |  | 0 | 0 | 0 | 0 | 0 | 0
I65/1 | I65/1 | 65 | 1 | Incandescent, (1) 65W lamp | 0.065 | LED13/1 | LED13 | 12.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0125 |  |  | 0 | 600 | 43.5 | 300 | 135 | 1078.5
I75/1 | I75/1 | 75 | 1 | Incandescent, (1) 75W lamp | 0.075 | LED13/1 | LED13 | 12.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0125 |  |  | 0 | 600 | 43.5 | 300 | 135 | 1078.5
I100/1 | I100/1 | 100 | 1 | Incandescent, (1) 100W lamp | 0.1 | LED22/1 | LED22 | 22 | LED A21 Lamp (e.g. Philips EnduraLED) | 0.022 |  |  | 0 | 700 | 50.75 | 350 | 157.5 | 1258.25
I120/1 | I120/1 | 120 | 1 | Incandescent, (1) 120W lamp | 0.12 | LED22/1 | LED22 | 22 | LED A21 Lamp (e.g. Philips EnduraLED) | 0.022 |  |  | 0 | 800 | 58 | 400 | 180 | 1438
I150/1 | I150/1 | 150 | 1 | Incandescent, (1) 150W lamp | 0.15 | LED22/1 | LED22 | 22 | LED A21 Lamp (e.g. Philips EnduraLED) | 0.022 |  |  | 0 | 1070 | 77.575 | 535 | 240.75 | 1923.325
I250/1 | I250/1 | 250 | 1 | Incandescent, (1) 250W lamp | 0.25 | LED75/1-WP | LED75 | 75 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.075 |  |  | 0 | 1400 | 101.5 | 700 | 315 | 2516.5
HPS50/1 | HPS50/1 | 50 | 1 | High Pressure Sodium, (1) 50W lamp | 0.066 | LED35/1 | LED35 | 35 | LED Pole Fixture (e.g. Lithonia DSX) | 0.035 |  |  | 0 | 600 | 43.5 | 300 | 135 | 1078.5
HPS70/1 | HPS70/1 | 70 | 1 | High Pressure Sodium, (1) 70W lamp | 0.095 | LED35/1 | LED35 | 35 | LED Wall Pack Fixture (e.g. Lithonia DSXW1-20C-530-40K) | 0.035 |  |  | 30 | 330 | 23.925 | 165 | 74.25 | 593.175
HPS70/1-c | HPS70/1 | 70 | 1 | High Pressure Sodium, (1) 70W lamp | 0.095 | LED35/1-c | LED35 | 35 | LED Canopy Fixture (e.g. Lithonia KACM-20C-530) | 0.035 |  |  | 0 | 380 | 27.55 | 190 | 85.5 | 683.05
HPS100/1 | HPS100/1 | 100 | 1 | High Pressure Sodium, (1) 100W lamp | 0.138 | LED45/1 | LED45 | 45 | LED Pole Fixture (e.g. Lithonia DSX) | 0.045 |  |  | 0 | 700 | 50.75 | 350 | 157.5 | 1258.25
HPS150/1 | HPS150/1 | 150 | 1 | High Pressure Sodium, (1) 150W lamp | 0.188 | LED54/1-WP | LED54 | 54 | LED Wall Pack Fixture (e.g. Lithonia DSXW2-30C-530-40K-T3M) | 0.054 |  |  | 35 | 350 | 25.375 | 175 | 78.75 | 629.125
HPS250/1 | HPS250/1 | 250 | 1 | High Pressure Sodium, (1) 250W lamp | 0.295 | LED54/1-WP | LED54 | 54 | LED Wall Pack Fixture (e.g. Lithonia DSXW2-30C-530-40K-T3M) | 0.054 |  |  | 35 | 350 | 25.375 | 175 | 78.75 | 629.125
HPS250/1-CH | HPS250/1 | 250 | 1 | High Pressure Sodium, (1) 250W lamp | 0.295 | LED168/1 | LED168 | 168 | LED Pole Fixture (e.g. Holophane MGLED-04-5K) | 0.168 |  |  | 0 | 1350 | 97.875 | 675 | 303.75 | 2426.625
HPS400/1 | HPS400/1 | 400 | 1 | High Pressure Sodium, (1) 400W lamp | 0.465 | LED252/1 | LED252 | 252 | LED Pole Fixture (e.g. Holophane HMLED2-06-5K) | 0.252 |  |  | 0 | 1700 | 123.25 | 850 | 382.5 | 3055.75
HPS400/1a | HPS400/1 | 400 | 1 | High Pressure Sodium, (1) 400W lamp | 0.465 | LED255/1 | LED255 | 255 | LED Pole Fixture (e.g. Holophane MGLED-06-5K) | 0.255 |  |  | 0 | 1225 | 88.8125 | 612.5 | 275.625 | 2201.9375
HPS400/2 | HPS400/2 | 400 | 2 | High Pressure Sodium, (2) 400W lamp | 0.93 | LED255/2 | LED255 | 255 | LED Pole 2-Head Fixture (e.g. Holophane MGLED-06-5K) | 0.51 |  |  | 0 | 1450 | 105.125 | 725 | 326.25 | 2606.375
HPS400/4 | HPS400/4 | 400 | 4 | High Pressure Sodium, (4) 400W lamp | 1.86 | LED255/4 | LED255 | 255 | LED Pole 4-Head Fixture (e.g. Holophane MGLED-06-5K) | 1.02 |  |  | 0 | 2900 | 210.25 | 1450 | 652.5 | 5212.75
HPS400/1-WP | HPS400/1 | 400 | 1 | High Pressure Sodium, (1) 400W lamp | 0.465 | LED104/1 | LED104 | 104 | LED Wall Pack (e.g. Holophane W4GLED-30C-1000-50K) | 0.104 |  |  | 0 | 470 | 34.075 | 235 | 105.75 | 844.825
HPS1000/1 | HPS1000 | 1000 | 1 | High Pressure Sodium, (1) 1000W lamp | 1.1 | LED500/1 | LED500 | 500 | LED Pole Fixture (e.g. Holophane HMLED2-12-5K | 0.5 |  |  | 0 | 1700 | 123.25 | 850 | 382.5 | 3055.75
LPS180/1 | LPS180/1 | 180 | 1 | Low Pressure Sodium, (1) 180W lamp | 0.18 | LED138/1 | LED138 | 138 | LED Pole Fixture (e.g. Lithonia DSX) | 0.138 |  |  | 0 | 600 | 43.5 | 300 | 135 | 1078.5
MV50/1 | MV50/1 | 50 | 1 | Mercury Vapor, (1) 50W lamp | 0.074 | LED35/1 | LED35 | 35 | LED Pole Fixture (e.g. Lithonia DSX) | 0.035 |  |  | 0 | 700 | 50.75 | 350 | 157.5 | 1258.25
MV75/1 | MV75/1 | 75 | 1 | Mercury Vapor, (1) 75W lamp | 0.093 | LED35/1 | LED35 | 35 | LED Pole Fixture (e.g. Lithonia DSX) | 0.035 |  |  | 0 | 800 | 58 | 400 | 180 | 1438
MV100/1 | MV100/1 | 100 | 1 | Mercury Vapor, (1) 100W lamp | 0.125 | LED45/1 | LED45 | 45 | LED Pole Fixture (e.g. Lithonia DSX) | 0.045 |  |  | 0 | 1000 | 72.5 | 500 | 225 | 1797.5
MV175/1 | MV175/1 | 175 | 1 | Mercury Vapor, (1) 175W lamp | 0.205 | LED105/1 | LED105 | 105 | LED Pole Fixture (e.g. Lithonia DSX) | 0.105 |  |  | 0 | 1070 | 77.575 | 535 | 240.75 | 1923.325
MV250/1 | MV250/1 | 250 | 1 | Mercury Vapor, (1) 250W lamp | 0.29 | LED138/1 | LED138 | 138 | LED Pole Fixture (e.g. Lithonia DSX) | 0.138 |  |  | 0 | 1400 | 101.5 | 700 | 315 | 2516.5
MV400/1 | MV400/1 | 400 | 1 | Mercury Vapor, (1) 400W lamp | 0.455 | LED209/1 | LED209 | 209 | LED Pole Fixture (e.g. Lithonia DSX) | 0.209 |  |  | 0 | 1500 | 108.75 | 750 | 337.5 | 2696.25
MH39/1 | MH39/1 | 39 | 1 | Metal Halide, (1) 39W lamp | 0.05 | LED35/1 | LED35 | 35 | LED Pole Fixture (e.g. Lithonia DSX) | 0.035 |  |  | 0 | 300 | 21.75 | 150 | 67.5 | 539.25
MH50/1 | MH50/1 | 50 | 1 | Metal Halide, (1) 50W lamp | 0.072 | LED35/1 | LED35 | 35 | LED Pole Fixture (e.g. Lithonia DSX) | 0.035 |  |  | 0 | 350 | 25.375 | 175 | 78.75 | 629.125
MH70/1 | MH70/1 | 70 | 1 | Metal Halide, (1) 70W lamp | 0.095 | LED35/1 | LED35 | 35 | LED Pole Fixture (e.g. Lithonia DSX) | 0.035 |  |  | 0 | 400 | 29 | 200 | 90 | 719
MH100/1 | MH100/1 | 100 | 1 | Metal Halide, (1) 100W lamp | 0.128 | LED45/1 | LED45 | 45 | LED Pole Fixture (e.g. Lithonia DSX) | 0.045 |  |  | 0 | 500 | 36.25 | 250 | 112.5 | 898.75
MH150/1 | MH150/1 | 150 | 1 | Metal Halide, (1) 150W lamp | 0.19 | LED68/1 | LED68 | 68 | LED Pole Fixture (e.g. Lithonia DSX) | 0.068 |  |  | 0 |  | 0 | 0 | 0 | 0
MH175/1 | MH175/1 | 175 | 1 | Metal Halide, (1) 175W lamp | 0.215 | LED105/1 | LED105 | 105 | LED Pole Fixture (e.g. Lithonia DSX) | 0.105 |  |  | 0 |  | 0 | 0 | 0 | 0
MH250/1 | MH250/1 | 250 | 1 | Metal Halide, (1) 250W lamp | 0.295 | LED138/1 | LED138 | 138 | LED Pole Fixture (e.g. Lithonia DSX) | 0.138 |  |  | 0 |  | 0 | 0 | 0 | 0
MH400/1-p | MH400/1 | 400 | 1 | Metal Halide, (1) 400W lamp | 0.458 | LED140/1 | LED140 | 140 | LED High Bay Pendant (e.g. Lithonia JCBL-18000LM-ACCR-40K-70CRI | 0.14 | 18.17 | 129.7857 | 24 | 600 | 43.5 | 300 | 135 | 1078.5
MH750/1 | MH750/1 | 750 | 1 | Metal Halide, (1) 750W lamp | 0.85 | LED275/1 | LED275 | 275 | LED Pole Fixture (e.g. Lithonia DSX) | 0.275 |  |  | 0
HPS50/1-WP | HPS50/1 | 50 | 1 | High Pressure Sodium, (1) 50W lamp | 0.066 | LED20/1-WP | LED20 | 20 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.02 |  |  | 0
HPS70/1-WP | HPS70/1 | 70 | 1 | High Pressure Sodium, (1) 70W lamp | 0.095 | LED36/1-WP | LED36 | 36 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.036 |  |  | 0
HPS100/1-WP | HPS100/1 | 100 | 1 | High Pressure Sodium, (1) 100W lamp | 0.138 | LED47/1-WP | LED47 | 47 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.047 |  |  | 0
HPS150/1-WP | HPS150/1 | 150 | 1 | High Pressure Sodium, (1) 150W lamp | 0.188 | LED75/1-WP | LED75 | 75 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.075 |  |  | 0
MV50/1-WP | MV50/1 | 50 | 1 | Mercury Vapor, (1) 50W lamp | 0.074 | LED20/1-WP | LED20 | 20 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.02 |  |  | 0
MV75/1-WP | MV75/1 | 75 | 1 | Mercury Vapor, (1) 75W lamp | 0.093 | LED36/1-WP | LED36 | 36 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.036 |  |  | 0
MV100/1-WP | MV100/1 | 100 | 1 | Mercury Vapor, (1) 100W lamp | 0.125 | LED47/1-WP | LED47 | 47 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.047 |  |  | 0
MV175/1-WP | MV175/1 | 175 | 1 | Mercury Vapor, (1) 175W lamp | 0.205 | LED75/1-WP | LED75 | 75 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.075 |  |  | 0
MH32/1-WP | MH32/1 | 32 | 1 | Metal Halide, (1) 32W lamp | 0.043 | LED13/1-WP | LED13 | 13 | LED Wall Pack Fixture (e.g. Rab WPLED10) | 0.013 |  |  | 0
MH39/1-WP | MH39/1 | 39 | 1 | Metal Halide, (1) 39W lamp | 0.05 | LED13/1-WP | LED13 | 13 | LED Wall Pack Fixture (e.g. Rab WPLED10) | 0.013 |  |  | 0
MH70/1-WP | MH70/1 | 70 | 1 | Metal Halide, (1) 70W lamp | 0.095 | LED36/1-WP | LED36 | 36 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.036 |  |  | 0
MH84/1-WP | MH84/1 | 84 | 1 | Metal Halide, (1) 84W lamp | 0.11 | LED47/1-WP | LED47 | 47 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.047 |  |  | 0
MH100/1-WP | MH100/1 | 100 | 1 | Metal Halide, (1) 100W lamp | 0.128 | LED47/1-WP | LED47 | 47 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.047 |  |  | 0
MH150/1-WP | MH150/1 | 150 | 1 | Metal Halide, (1) 150W lamp | 0.19 | LED75/1-WP | LED75 | 75 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.075 |  |  | 0
MH175/1-WP | MH175/1 | 175 | 1 | Metal Halide, (1) 175W lamp | 0.215 | LED75/1-WP | LED75 | 75 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.075 |  |  | 0
MH250/1-WP | MH250/1 | 250 | 1 | Metal Halide, (1) 250W lamp | 0.295 | LED109/1-WP | LED109 | 109 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.109 |  |  | 0 | 300 | 26.25 | 110 | 45 | 481.25
MH400/1-WP | MH400/1 | 400 | 1 | Metal Halide, (1) 400W lamp | 0.458 | LED200/1-WP | LED200 | 200 | LED Wall Pack Fixture | 0.2 |  |  | 0 | 350 | 30.625 | 110 | 52.5 | 543.125
CFQ18/1-WP | CFQ18/1 | 18 | 1 | Compact Fluorescent, quad, (1) 18W lamp | 0.026 | LED13/1-WP | LED13 | 13 | LED Wall Pack Fixture (e.g. Rab WPLED10) | 0.013 |  |  | 0 | 400 | 35 | 110 | 60 | 605
CFQ26/2-WP | CFQ26/2 | 26 | 2 | Compact Fluorescent, quad, (2) 26W lamp | 0.066 | LED36/1-WP | LED36 | 36 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.036 |  |  | 0 | 500 | 43.75 | 110 | 75 | 728.75
CFQ42/2-WP | CFQ42/2 | 42 | 2 | Compact Fluorescent, quad, (2) 42W lamp | 0.094 | LED47/1-WP | LED47 | 47 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.047 |  |  | 0 | 350 | 30.625 | 110 | 52.5 | 543.125
CFQ26/1-WP | CFQ26/1 | 26 | 1 | Compact Fluorescent, quad, (1) 26W lamp | 0.033 | LED20/1-WP | LED20 | 20 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.02 |  |  | 0 | 400 | 35 | 110 | 60 | 605
CFQ42/1-WP | CFQ42/1 | 42 | 1 | Compact Fluorescent, quad, (1) 42W lamp | 0.047 | LED27/1-WP | LED27 | 27 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.027 |  |  | 0 | 500 | 43.75 | 110 | 75 | 728.75
CFQ32/1-WP | CFQ32/1 | 32 | 1 | Compact Fluorescent, quad, (1) 32W lamp | 0.034 | LED20/1-WP | LED20 | 20 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.02 |  |  | 0 | 500 | 43.75 | 110 | 75 | 728.75
CFQ28/1-WP | CFQ28/1 | 28 | 1 | Compact Fluorescent, quad, (1) 28W lamp | 0.033 | LED20/1-WP | LED20 | 20 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.02 |  |  | 0 | 350 | 30.625 | 110 | 52.5 | 543.125
CFQ52/1-WP | CFQ52/1 | 42 | 2 | Compact Fluorescent, quad, (2) 42W lamp | 0.094 | LED36/1-WP | LED36 | 36 | LED Wall Pack Fixture (e.g. Lithonia DSXW) | 0.036 |  |  | 0 | 400 | 35 | 110 | 60 | 605
HLV50/1 | HLV50/1 | 50 | 1 | Halogen, (1) Low Voltage MR16 lamp | 0.06 | LED13/1 | LED13 | 12.5 | LED A19 Lamp (e.g. Philips EnduraLED) | 0.0125 |  |  | 0 | 0 | 0 |  | 0 | 0
LED8/1 | LED8 | 150 | 1 | Highbay Induction Lighting 150W Fixture | 0.15 | LED8/1 | LED8 | 8 | No Change | 0.008 |  |  | 0 | 0 | 0 |  | 0 | 0
Ind150/1 | IND150 | 35 | 1 | Metal Halide, (1) 35W lamp | 0.046 | Ind150/1 | IND150 | 150 | No Change | 0.15 |  |  | 0 | 0 | 0 |  | 0 | 0
*Existing Fixture Wattage based on Appendix B Standard Fixture Wattage Table.
(1) Material costs are estimated conservatively based on past lighting projects and construction cost inventories
(2) Labor costs are estimated as 50% of material costs.
(3) O&P is estimated at 15% Contractor Overhead and Profit.