## Benchmarking
Benchmarking Calculator |  | Version 8.1
School Information
School Name | Moorpark High School
School CDS Code | 56739405633250
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021
Electric Utility: | SCE | PG&E or SCE etc
Gas Utility: | So Cal Gas Company |  | Energy Use Intensity (EUI) Calculator | [5 empty] | Source Energy Conversion Factors
Billing Period (Fiscal Year) | 07/01/2016 - 06/30/2017 | Fiscal year | Electricity |  | Natural Gas |  | Other Fuels |  | Electricity | 10716 | Btu/kWh | (Same as Energy Star and DOE)
Total Square Footage of School | 244633 |  | 4.1245 | W/SF | 0.021403 | Therms/SF/Yr | 0 | Propane gal/SF/Yr | Natural Gas | 100000 | Btu/therm
|  |  | 12.1221 | kWh/SF/Yr | 0.023366 | Gas Cost/SF/Yr | 0 | Fuel Oil gal/SF/Yr | Propane | 92500 | Btu/gal
|  |  | 2.2225 | Cost/SF/Yr |  |  | 0 | Fuel Cost/SF/Yr | Fuel Oil | 138500 | Btu/gal
Electricity |  |  | Energy Costs/SF/Year: | 2.2459 |  | Energy EUI(Kbtu)/SF/Year: | 132.0409
Average Maximum Demand (kW): | 1009
Annual PV Electricity Production(kWh) | 0 | Do you have onsite PV? enter 0 if no PV.
Electricity Purchase from Utility(kWh) | 2965469
Total Annual Electric Use (kWh): | 2965469
Cost paid to PPA vendor & other supplier ($) | 0
Total Annual Electric Charges ($) | 543702.16
Natural Gas
Total Annual Natural Gas Use (therms): | 5236
Total Annual Gas Charges ($): | 5716.16
Other Fuels (if applicable) |  |  | Average Cost
Total Annual Propane Use(gals): | 0 |  | Electricity | 0.18331 | $/kWh
Total Annual Propane Charges($): | 0 |  | Natural Gas | 1.0917 | $/therm
|  |  | Propane | 0 | $/gal
Total Annual Fuel Oil Use(gals): | 0 |  | Fuel Oil | 0 | $/gal
Total Annual Fuel Oil Costs($): | 0
Note: If multiple fuels are used, enter primary fuel only, otherwise savings will be calculated using natural gas cost.

## Lighting
Calculators for Simple Lighting Project |  | Version 8.1
School Information
School Name | Moorpark High School
School CDS Code | 56739405633250
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021
The following calculators can be used to calculate energy Savings for your energy efficiency project.
Pick the project you would like to install and answer the questions for that project (highlighted in yellow), energy and cost savings will be calculated for you.
It is assumed that all lights use about 30% of the total site kWh use, savings will be capped at 50% of the lighting kWh use or 15% of total site kWh.
Energy cost savings for all lighting projects will be prorated downed to 15% when the total saving exceed 15% site total kWh use.
ECM 1 | Replace incandescent light with compact fluorescent light | Go to cell A22
ECM 2 | Replace incandescent/ CFL light with LED light | Go to cell A32 | [7 empty] | Inflation rate | 2%
ECM 3,4 | Convert incandescent/CFL exit sign to LED exit sign | Go To cell A42 &A48 | [7 empty] | Discount Rate | 5%
ECM 5,6 | Convert T12 fluorescent to T8 with electronic ballast or LED lamps | Go To cell A54 & A62 | [7 empty] | Electricity Escalation | 4%
ECM 6A | Convert 32 Watt T8 fluorescent fixture to LED lamps | Go To cell A67 | [7 empty] | Non-Energy Benefit | 5%
ECM 7 | Replace 32 Watt T8 lamps with 28 Watt T8 Lamps | Go To cell A77 | [7 empty] | Maintenance saving | 3%
ECM 8,9 | Replace mercury vapor/HPS/Metal Halide with LED/Induction lights | Go To cell A89 & A94
ECM 10 | Install occupancy control for intermittently occupied rooms | Go To cell A101
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 4 years)
ECM 1 | Replace incandescent light with compact fluorescent light | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 1 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 |  |  | 0 | 1 | 2 | 3
Measure 1 | Quantity of incandescent lights to be replaced with CFLs? |  |  |  | This measure saves | 0 | kW peak demand |  | Existing | Incand./Halogen | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 |  |  | 2013 | 2014 | 2015 | 2016
| What is the total wattage of all new CFL lamps? |  |  |  | and | 0 | kWh energy use. |  | Proposed | CFL lights | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | or | 0 | gallons of | NA | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0
[5 empty] | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
[5 empty] | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
[5 empty] | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years)
ECM 2 | Replace incandescent /CFL light with LED light | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 2 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Measure 2A | Quantity of incandescent bulbs to be replaced with LED lights? |  |  |  | This measure saves | 0.0005164 | kW peak demand |  | Existing | Incand./CFL | 12988.7946 | 1.4096 | -78.6449 |  | This measure saves | 1.4096 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| What is the total wattage of all new LED lamps? |  |  |  | and | 12988.7946 | kWh energy use. |  | Proposed | Led Lights | 0 | 0 | 0 |  | and | 12988.7946 | kWh energy use. |  | Energy Cost Savings |  | 2295.1279 | 2386.933 | 2482.4104 | 2581.7068 | 2684.975 | 2792.374 | 2904.069 | 3020.2318 | 3141.041 | 3266.6827 | 3397.35 | 3533.244 | 3674.5737 | 3821.5567 | 3974.419 |  |  |  | 2336.1313 | 2429.5765 | 2526.7596 | 2627.83 | 2732.9432 | 2842.2609 | 2955.9513 | 3074.1894 | 3197.157 | 3325.0433 | 3458.045 | 3596.3668 | 3740.2215 | 3889.8303 | 4045.4235
| What is the total installed cost for this measure? |  |  |  | and | -41.0859 | therms natural gas |  |  | Savings | 12988.7946 | 1.4096 | -78.6449 |  | and | -78.6449 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Measure 2B | Quantity of CFL bulbs to be replaced with LED lights? | 172 |  |  | or | 2336.1313 | energy cost annually. | [7 empty] | or | 2295.1279 | energy cost annually. |  | Net Cost/Savings |  | 2295.1279 | 2386.933 | 2482.4104 | 2581.7068 | 2684.975 | 2792.374 | 2904.069 | 3020.2318 | 3141.041 | 3266.6827 | 3397.35 | 3533.244 | 3674.5737 | 3821.5567 | 3974.419 |  |  |  | 2336.1313 | 2429.5765 | 2526.7596 | 2627.83 | 2732.9432 | 2842.2609 | 2955.9513 | 3074.1894 | 3197.157 | 3325.0433 | 3458.045 | 3596.3668 | 3740.2215 | 3889.8303 | 4045.4235
| What is the total wattage of all new LED lamps? | 1841 |  |  | Simple Payback is | 5.0832 | years. | [7 empty] | Simple Payback is | 5.174 | years. |  | Present Value of Savings |  | 30689.3904
| What is the total installed cost for this measure? | 11875 |  |  | Saving to Investment Ratio | 2.769 | [8 empty] | Saving to Investment Ratio | 2.7204 |  |  | Adjusted NPV of Savings |  | 31237.6686
| What is the utility rebate for this measure? | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 16 years)
ECM 3&4 | Convert incandescent/CFL exit sign to LED exit sign | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 3&4 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Measure 3 | Quantity of CFL exit signs to be replaced with LEDs? |  |  |  | This measure saves | 0 | kW peak demand |  | Existing | CFL/incandescent | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
| What is the total wattage of new LED exit sign? |  |  |  | and | 0 | kWh energy use. |  | Proposed | LEDs | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Measure 4 | Quantity of incandescent exit signs to be replaced with LEDs? |  |  |  | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1
| What is the total wattage of new LED Exit sign? |  |  |  | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | -0.45811
| What is the total installed cost for this measure? |  |  |  | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | -0.45811
What is the utility rebate for this measure?
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years)
ECM 5&6 | Convert T12 fluorescent to T8 with electronic ballast or LED lamps | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 5&6 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| This ECM is for 4-foot linear fluorescent or 2 foot U-tube retrofit. If 8-foot fluorescent is converted to two 4-foot, multiply the quantity of lamp by two. |  |  |  | This measure saves | 0 | kW peak demand |  | Existing | T12 Fluorescent | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Measure 5 | Quantity of 34 watt T12 lamps to be replaced with T8? |  |  |  | and | 0 | kWh energy use. |  | Proposed | T8 or LED | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quantity of 40 watt T12 lamps to be replaced with T8? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the new T8 lamp wattage? |  | choose one |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
Measure 6 | Quantity of 34 watt T12 lamps to be replace with LED lamps? |  |  |  | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
Quantity of 40 watt T12 lamps to be replaced with LED lamps?
What is the total installed cost for this measure?
What is the utility rebate for this measure?
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years)
ECM 6A | Convert 32 Watt T8 fluorescent fixture to LED lamps | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 6A | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| This ECM is for 4-foot linear fluorescent. If 8-foot fluorescent is converted to two 4-foot, multiply the quantity of lamp by two. |  |  |  | This measure saves | 0.0093287 | kW peak demand |  | Existing | T8 Fluorescent | 680459.437 | 73.8489 | -4120.0657 |  | This measure saves | 25.4651 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Quantity of 32 watt T8 lamps to be replaced with LED lamps? | 9352 |  |  | and | 305033.5407 | kWh energy use. |  | Proposed | LED | 375425.8963 | 48.3838 | -2699.3534 |  | and | 305033.5407 | kWh energy use. |  | Energy Cost Savings |  | 54364.9112 | 56539.5077 | 58801.088 | 61153.1315 | 63599.2568 | 66143.227 | 68788.9561 | 71540.5144 | 74402.1349 | 77378.2203 | 80473.3491 | 83692.2831 | 87039.9744 | 90521.5734 | 94142.4364 |  |  |  | 55105.6328 | 57309.8581 | 59602.2525 | 61986.3425 | 64465.7962 | 67044.4281 | 69726.2052 | 72515.2534 | 75415.8636 | 78432.4981 | 81569.798 | 84832.59 | 88225.8936 | 91754.9293 | 95425.1265
| What is the total installed cost for this measure? | 663229 |  |  | and | -742.2117 | therms natural gas |  |  | Savings | 305033.5407 | 25.4651 | -1420.7123 |  | and | -1420.7123 | therms natural gas |  | Maintenance Savings |  | 19896.87 | 20294.8074 | 20700.7035 | 21114.7176 | 21537.012 | 21967.7522 | 22407.1073 | 22855.2494 | 23312.3544 | 23778.6015 | 24254.1735 | 24739.257 | 25234.0421 | 25738.723 | 26253.4974
| What is the utility rebate for this measure? | 0 |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 55105.6328 | energy cost annually. | [7 empty] | or | 54364.9112 | energy cost annually. |  | Net Cost/Savings |  | 74261.7812 | 76834.3151 | 79501.7915 | 82267.8491 | 85136.2687 | 88110.9792 | 91196.0634 | 94395.7638 | 97714.4893 | 101156.8218 | 104727.5227 | 108431.5401 | 112274.0166 | 116260.2964 | 120395.9338 |  |  |  | 75002.5028 | 77604.6655 | 80302.956 | 83101.0602 | 86002.8082 | 89012.1803 | 92133.3125 | 95370.5028 | 98728.218 | 102211.0996 | 105823.9715 | 109571.8469 | 113459.9357 | 117493.6523 | 121678.6239
[5 empty] | Simple Payback is | 12.0356 | years. | [7 empty] | Simple Payback is | 12.1996 | years. |  | Present Value of Savings |  | 960806.5238
[5 empty] | Saving to Investment Ratio | 1.5406 | [8 empty] | Saving to Investment Ratio | 1.5249 |  |  | Adjusted NPV of Savings |  | 970711.1107
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 4 years)
ECM 7 | Replace 32 Watt T8 lamps with 28 Watt T8 Lamps | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 7 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 |  | 0 | 1 | 2 | 3 | 4
| Quantity of 32 watt T8 lamps to be replaced? |  |  |  | This measure saves | 0 | kW peak demand |  | Existing | T8 32 Watt Lamps | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 |  | 2013 | 2014 | 2015 | 2016 | 2017
| What is the total installed cost for this measure? |  |  |  | and | 0 | kWh energy use. |  | Proposed | T8 28 Watt Lamps | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0
[5 empty] | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[5 empty] | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
[5 empty] | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years)
ECM 8&9 | Replace mercury vapor/HPS/Metal Halide with LED/Induction lights | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 8&9 | KWh Impact | KW Impact | Therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Measure 8 | Quantity of mercury vapor fixtures to be replaced? |  |  |  | This measure saves | 0 | kW peak demand |  | Existing | MV /HPS /MH | 161243.13 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| What is the total wattage of all new LED or Induction lamps? |  |  |  | and | 66394.23 | kWh energy use. |  | Proposed | Induction or LED | 94848.9 | 0 | 0 |  | and | 66394.23 | kWh energy use. |  | Energy Cost Savings |  | 9736.6175 | 10126.0822 | 10531.1255 | 10952.3705 | 11390.4654 | 11846.084 | 12319.9273 | 12812.7244 | 13325.2334 | 13858.2428 | 14412.5725 | 14989.0754 | 15588.6384 | 16212.1839 | 16860.6713 |  |  |  | 9736.6175 | 10126.0822 | 10531.1255 | 10952.3705 | 11390.4654 | 11846.084 | 12319.9273 | 12812.7244 | 13325.2334 | 13858.2428 | 14412.5725 | 14989.0754 | 15588.6384 | 16212.1839 | 16860.6713
| What is the total installed cost for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 66394.23 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 3632.4 | 3705.048 | 3779.149 | 3854.7319 | 3931.8266 | 4010.4631 | 4090.6724 | 4172.4858 | 4255.9355 | 4341.0542 | 4427.8753 | 4516.4328 | 4606.7615 | 4698.8967 | 4792.8747
| What is the utility rebate for this measure? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Measure 9 | Quantity of HPS/Metal Halide fixtures to be replaced? | 299 |  |  | or | 9736.6175 | energy cost annually. | [7 empty] | or | 9736.6175 | energy cost annually. |  | Net Cost/Savings |  | 13369.0175 | 13831.1302 | 14310.2745 | 14807.1025 | 15322.2919 | 15856.5471 | 16410.5997 | 16985.2103 | 17581.169 | 18199.297 | 18840.4478 | 19505.5082 | 20195.3999 | 20911.0806 | 21653.5459 |  |  |  | 13369.0175 | 13831.1302 | 14310.2745 | 14807.1025 | 15322.2919 | 15856.5471 | 16410.5997 | 16985.2103 | 17581.169 | 18199.297 | 18840.4478 | 19505.5082 | 20195.3999 | 20911.0806 | 21653.5459
| What is the total wattage of all new LED or Induction lamps? | 21655 |  |  | Simple Payback is | 12.4355 | years. | [7 empty] | Simple Payback is | 12.4355 | years. |  | Present Value of Savings |  | 172888.0941
| What is the total installed cost for this measure? | 121080 |  |  | Saving to Investment Ratio | 1.503 | [8 empty] | Saving to Investment Ratio | 1.503 |  |  | Adjusted NPV of Savings |  | 172888.0941
| What is the utility rebate for this measure? | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 8 years)
ECM 10 | Install occupancy control for intermittently occupied rooms | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 10 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | 0 | 1 | 2 | 3 | 4 | 5 |  | 6 | 7 | 8
| Quantity of occupancy sensors to be installed? | 237 |  |  | This measure saves | 0.0053264 | kW peak demand |  | Existing | Manual Control | 0 | 0 | 0 |  | This measure saves | 14.5399 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 |  | 2019 | 2020 | 2021
| What is the total installed cost for this measure? | 66894 |  |  | and | 28733.722 | kWh energy use. |  | Proposed | Occupancy controlled | -28733.722 | -14.5399 | 4.0245 |  | and | 28733.722 | kWh energy use. |  | Energy Cost Savings |  | 4209.3651 | 4377.7397 | 4552.8493 | 4734.9633 | 4924.3618 | 5121.3363 | 5326.1897 | 5539.2373 |  |  | 4211.4634 | 4379.9219 | 4555.1188 | 4737.3235 | 4926.8165 |  | 5123.8891 | 5328.8447 | 5541.9985
| What is the utility rebate for this measure? | 0 |  |  | and | -2.1025 | therms natural gas |  |  | Savings | 28733.722 | 14.5399 | -4.0245 |  | and | -4.0245 | therms natural gas |  | Maintenance Savings |  | 2006.82 | 2046.9564 | 2087.8955 | 2129.6534 | 2172.2465 | 2215.6914 | 2260.0053 | 2305.2054
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 4211.4634 | energy cost annually. | [7 empty] | or | 4209.3651 | energy cost annually. |  | Net Cost/Savings |  | 6216.1851 | 6424.6961 | 6640.7448 | 6864.6167 | 7096.6083 | 7337.0277 | 7586.195 | 7844.4427 |  |  | 6218.2834 | 6426.8783 | 6643.0143 | 6866.977 | 7099.063 |  | 7339.5806 | 7588.85 | 7847.2039
[5 empty] | Simple Payback is | 15.8838 | years. | [7 empty] | Simple Payback is | 15.8917 | years. |  | Present Value of Savings |  | 44867.8034
[5 empty] | Saving to Investment Ratio | 0.70627 | [8 empty] | Saving to Investment Ratio | 0.70603 |  |  | Adjusted NPV of Savings |  | 44883.2673

## HVAC
| Calculators for Simple HVAC Project |  |  | Version 8.1
School Information
School Name | Moorpark High School
School CDS Code | 56739405633250
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021
If your school would like to replace some HVAC systems, it is better to combine your HVAC project with short payback projects.
The following calculators can be used to calculate energy Savings for your energy efficiency project.
Pick the project you would like to install and answer the questions for that project (highlighted in yellow), energy and cost savings will be calculated for you.
It is assumed that HVAC uses about 50% of the total site kWh use, savings will be capped at 50% of the HVAC kWh use or 25% of total site kWh use.
Energy cost savings for all HVAC projects will be prorated downed to 25% when the total saving exceed 25% site total kWh use.
ECM 11 | Replace old packaged/split HVAC unit with high efficiency HVAC | Go to cell A23 | [7 empty] | Inflation rate | 2%
ECM 12 | Replace old heat pump with high efficiency heat pump | Go to cell A35 | [7 empty] | Discount Rate | 5%
ECM 13A | Replace boiler with high efficiency condensing boiler | Go To cell A49 | [7 empty] | Electricity Escalation | 4%
ECM 13B | Replace furnace with high efficiency condensing furnace | Go To cell A59 | [7 empty] | Non-Energy Benefit | 5%
ECM 14 | Seal existing HVAC leaky duct | Go To cell A51 | [7 empty] | Maintenance saving | 3%
ECM 15 | Install variable speed drive for pumps and fans | Go To cell A70
ECM 16 | Replace manual thermostat with programmable/smart thermostat | Go To cell A81
ECM 17 | Replace old motor with premium efficiency motor | Go To cell A92
ECM 18 | Replace storage water heater with gas-fired tankless water heater | Go To cell A103
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years) | [17 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 11 | Replace old packaged/split HVAC unit with high efficiency HVAC | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 11 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| This calculator only applies to AC up to 65KBtu/hr or 5.4 tons |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Old Packaged AC | 0 | 0 | 0 |  | This project saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Total quantity of AC and heat pump unit at school |  |  |  | and | 0 | kWh electricity use. |  | Proposed | New Packaged AC | 0 | 0 | 0 |  | and | 0 | kWh electricity use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total tonnage of air conditioner and heat pump unit at entire school |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quantity of vertical wall mount AC to be replaced with EER 11(or higher) unit? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | Fuel Oil | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quantity of packaged AC to be replaced with SEER 14 unit? |  |  |  | or | 0 | energy cost annually. |  | Prorated Annual Energy Savings | [5 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total vertical wall mount AC tonnage to be replaced with EER 11 & IPLV 14 unit? |  |  |  | Simple Payback is | 0 | years. |  |  | 0 | DEER kWh Impact | DEER kW Impact | DEER therm impact |  | Simple Payback is | 0 | years. |  | Net Present value of Savings |  | 0
| What is the total AC tonnage to be replaced with SEER 14 unit? |  |  |  | Saving to Investment Ratio | 0 |  |  | Existing | Old Packaged AC | 0 | 0 | 0 |  | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
| What is the IOU (or nearest IOU)area the unit is installed? |  | Choose your utility | [5 empty] | Proposed | New Packaged AC | 0 | 0 | 0
| What is the total installed cost for this measure? | [8 empty] | Savings | 0 | 0 | 0
What is the utility rebate for this measure?
Are there other non-repayable funds applied to this measure?
Please enter the total tonnage of air conditioner and heat pump at the school site in cell C26 and C41.
| Energy Savings will be prorated based on the ratio of replaced tonnage to total tonnage plus 10% inefficiency. | [7 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years) | [17 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 12 | Replace old heat pump with high efficiency heat pump | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 12 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| This calculator only applies to heat pump up to 65KBtu/hr or 5.4 tons |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Old Heat Pump | 0 | 0 | 0 |  | This project saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Total quantity of AC and heat pump unit at school |  |  |  | and | 0 | kWh electricity use. |  | Proposed | New Heat Pump | 0 | 0 | 0 |  | and | 0 | kWh electricity use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total tonnage of air conditioner and heat pump unit at entire school |  | same as c26 |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quantity of vertical wall mount HP to be replaced with EER 11(or higher) unit? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | Fuel Oil | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quantity of HP to be replaced with SEER 14 (HSPF 8.3) unit? |  |  |  | or | 0 | energy cost annually. |  | Prorated Annual Energy Savings | [5 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quantity of HP to be replaced with SEER 15 (HSPF 8.8) unit? |  |  |  | Simple Payback is | 0 | years. |  |  | 0 | DEER kWh Impact | DEER kW Impact | DEER therm impact |  | Simple Payback is | 0 | years. |  | Net Present value of Savings |  | 0
| What is the total vertical wall mount AC tonnage to be replaced with EER 11 & IPLV 14 unit? |  |  |  | Saving to Investment Ratio | 0 |  |  | Existing | Old Packaged AC | 0 | 0 | 0 |  | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
| What is the total HP tonnage to be replaced with SEER 14 unit? | [7 empty] | Proposed | New Packaged AC | 0 | 0 | 0
| What is the total HP tonnage to be replaced with SEER 15 unit? | [8 empty] | Savings | 0 | 0 | 0
| What is the IOU (or nearest IOU)area the unit is installed? |  | Choose your utility
What is the total installed cost for this measure?
What is the utility rebate for this measure?
Are there other non-repayable funds applied to this measure?
Please enter the total tonnage of air conditioner and heat pump at the school site in cell C26 and C41.
| Energy Savings will be prorated based on the ratio of replaced tonnage to total tonnage plus 10% inefficiency. | [7 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 20 years) | [22 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 13A | Replace boiler with high efficiency condensing boiler | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 13A | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Quantity of boiler to be replaced with AFUE 92-94 unit? |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Non Condensing Unit | 0 | 0 | 0 |  | This project saves | 0 | therms natural gas |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
| Quantity of boiler to be replaced with AFUE 95-97 unit? |  |  |  | and | 0 | kWh electricity use. |  | Proposed | Condensing Unit | 0 | 0 | 0 |  |  | 0 | gallons of | Fuel Oil | Energy Cost Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total kBtu/hr of the new AFUE92-94 units? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | or | 0 | energy cost annually. |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total kBtu/hr of the new AFUE95-97 units? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | Simple Payback is | 0 | years. |  | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the IOU (or nearest IOU)area the unit is installed? |  | choose your utility |  | or | 0 | energy cost annually. | [7 empty] | Saving to Investment Ratio | 0 |  |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | Simple Payback is | 0 | years. | [11 empty] | Present Value of Savings |  | 0
| What is the utility rebate for this measure? |  |  |  | Saving to Investment Ratio | 0 | [12 empty] | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years) | [17 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 13B | Replace furnace with high efficiency condensing furnace | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 13B | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| Quantity of furnace to be replaced with AFUE 92-94 unit? |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Non Condensing Unit | 0 | 0 | 0 |  | This project saves | 0 | therms natural gas |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Quantity of furnace to be replaced with AFUE 95-97 unit? |  |  |  | and | 0 | kWh electricity use. |  | Proposed | Condensing Unit | 0 | 0 | 0 |  |  | 0 | gallons of | Fuel Oil | Energy Cost Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total kBtu/hr of the new AFUE92-94 units? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | or | 0 | energy cost annually. |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total kBtu/hr of the new AFUE95-97 units? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | Simple Payback is | 0 | years. |  | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the IOU (or nearest IOU)area the unit is installed? |  | choose your utility |  | or | 0 | energy cost annually. | [7 empty] | Saving to Investment Ratio | 0 |  |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | Simple Payback is | 0 | years. | [11 empty] | Present Value of Savings |  | 0
| What is the utility rebate for this measure? |  |  |  | Saving to Investment Ratio | 0 | [12 empty] | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 11 years) | [13 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 14 | Seal existing HVAC leaky duct | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 14 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| How many total tons of AC where ducts will be sealed? |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Old duct | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
| What is the total installed cost? |  |  |  | and | 0 | kWh electricity use. |  | Proposed | Sealed duct | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
[5 empty] | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years) | [17 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 15 | Install variable speed drive for pumps and fans | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 15 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| What is the total motor horsepower that will have VSD? |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Old Drives | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| What is the total installed cost? |  |  |  | and | 0 | kWh electricity use. |  | Proposed | AC VFD | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
[5 empty] | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 11 years) | [13 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 16 | Replace manual thermostat with programmable/smart thermostat | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 16 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
| Quantity of old thermostats to be replaced? |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Manual Thermostat | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
| What is the total installed cost? |  |  |  | and | 0 | kWh electricity use. |  | Proposed | Programmable Type | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
[5 empty] | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 15 years) | [17 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 17 | Replace old motor with premium efficiency motor | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 17 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| What is the total premium efficiency horsepower capacity to be installed? |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Old Motor | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| What is the total installed cost? |  |  |  | and | 0 | kWh electricity use. |  | Proposed | Prem. Eff. Motor | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
[5 empty] | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
[9 empty] | Annual Energy Savings Analysis | [9 empty] | Life Cycle Cost Analysis (EUL= 20 years) | [22 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 18 | Replace storage water heater with gas-fired tankless water heater | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 18 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Quantity of storage heater to be replaced with new instantaneous water heater? |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Storage Water Heater | 0 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
| What is the total KBtu per hour capacity of the old water heater? |  |  |  | and | 0 | kWh electricity use. |  | Proposed | Tankless Water Heater | 0 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost? |  |  |  | and | 0 | therms natural gas |  |  | Savings |  | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
[5 empty] | Saving to Investment Ratio | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0

## Plug Load
| Calculators for Simple Plug Load Project | Version 8.1
School Information
School Name | Moorpark High School
School CDS Code | 56739405633250
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021
If you have the following plug loads but without control, the following calculators can be used to calculate energy Savings for your energy efficiency project.
Pick the project you would like to install and answer the questions for that project (highlighted in yellow), energy and cost savings will be calculated for you.
It is assumed that plug loads use about 10% of the total site kWh use, savings will be capped at 50% of the plug load kWh use or 5% of total site kWh use.
Energy cost savings for all plug load projects will be prorated downed to 5% when the total saving exceed 5% site total kWh use.
ECM 19 | Install smart strip/PC management to control computers/printers | Go to cell A19
ECM 20 | Install vending machine occupancy control | Go To cell A30 | [6 empty] | Inflation rate | 2%
[9 empty] | Discount Rate | 5%
[9 empty] | Electricity Escalation | 4%
[9 empty] | Non-Energy Benefit | 5%
[9 empty] | Maintenance saving | 3%
[8 empty] | Annual Energy Savings Analysis | [10 empty] | Life Cycle Cost Analysis (EUL= 4 years) | [6 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 19 | Install smart strip/PC management to control computers/printers | Fill in your answers | Adjusted Energy Savings Summary | [5 empty] | ECM 19 | kW Demand | Annual Hours | Integrated KWH Impact | Therm Impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 |  | 0 | 1 | 2 | 3 | 4
Measure 19 | How many smart strips or PC management tools will be installed? |  |  | This measure saves | 0 | kW peak demand |  | Existing | No Control | 0 | 2420 | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 |  | 2013 | 2014 | 2015 | 2016 | 2017
| What is the proposed computer control? |  |  | and | 0 | kWh energy use. |  | Proposed | 0 | 0 | 1210 | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| What is the total installed cost? |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 1210 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  | or | 0 | gallons of | NA | [7 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0
|  |  |  | or | 0 | energy cost annually. | [8 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0
|  |  |  | Simple Payback is | 0 | years. | [8 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
|  |  |  | Saving to Investment Ratio | 0 | [9 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
[8 empty] | Annual Energy Savings Analysis | [10 empty] | Life Cycle Cost Analysis (EUL= 5 years) | [7 empty] | Life Cycle Analysis Based on Adjusted Savings
ECM 20 | Install vending machine occupancy control | Fill in your answers | Adjusted Energy Savings Summary | [5 empty] | ECM 20 | kW Demand | Reduction Factor | Integrated KWH Impact | Therm Impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 |  | 0 | 1 | 2 | 3 | 4 | 5
Measure 20 | Quantity of vending machine misers to be installed in beverage machines? |  |  | This measure saves | 0 | kW peak demand |  | Existing | No Control | 0 | 0% | 0 | 0 |  | This measure saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
| Quantity of vending machine misers to be installed in snack machines? |  |  | and | 0 | kWh energy use. |  | Proposed | Vending Miser control | 0 | 42% | 0 | 0 |  | and | 0 | kWh energy use. |  | Energy Cost Savings | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost? |  |  | and | 0 | therms natural gas |  |  | Savings | 0 |  | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0
| What is the utility rebate for this measure? |  |  | or | 0 | gallons of | NA | [7 empty] | or | 0 | gallons of | NA | Financing cost |  | 0 | 0 | 0 | 0 | 0
|  |  |  | or | 0 | energy cost annually. | [5 empty] | 0 |  |  | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 |  | Adjusted Savings | 0 | 0 | 0 | 0 | 0
|  |  |  | Simple Payback is | 0 | years. | [8 empty] | Simple Payback is | 0 | years. |  | Present Value of Savings |  | 0
|  |  |  | Saving to Investment Ratio | 0 | [9 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0

## Bldg Envelope
Calculators for Building Envelope Project
School Information | [9 empty] | Inflation rate | 2%
School Name | Moorpark High School | [8 empty] | Discount Rate | 5%
School CDS Code | 56739405633250 | [8 empty] | Electricity Escalation | 4%
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021 | [8 empty] | Non-Energy Benefit | 5%
[10 empty] | Maintenance saving | 3%
ECM 21 | Building Envelope Windows Replacement | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 21 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
[5 empty] | This project saves | 0 | kW peak demand |  | Existing | Old windows | 0 | 0 | 0 |  | This project saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
| Square footage of EAST facing window replaced |  |  |  | and | 0 | kWh electricity use. |  | Proposed | New windows | 0 | 0 | 0 |  | and | 0 | kWh electricity use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Square footage of SOUTH facing window replaced |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Square footage of WEST facing window replaced |  |  |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | Fuel Oil | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the IOU (or nearest IOU)area the unit is installed? |  | Choose your utility |  | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Net Present value of Savings |  | 0
| What is the utility rebate for this measure? |  |  |  | SIR | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
Are there other non-repayable funds applied to this measure?
ECM 22 | Building Envelope Install Cool Roof | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 22 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
[5 empty] | This project saves | 0 | kW peak demand |  | Existing | Old Roof | 0 | 0 | 0 |  | This project saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | [5 empty] | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Square footage of cool roof installed |  |  |  | and | 0 | kWh electricity use. |  | Proposed | New cool roof | 0 | 0 | 0 |  | and | 0 | kWh electricity use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Increased R value of cool roof installation |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | Fuel Oil | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the IOU (or nearest IOU)area the unit is installed? |  | Choose your utility |  | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Net Present value of Savings |  | 0
| What is the utility rebate for this measure? |  |  |  | SIR | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
Are there other non-repayable funds applied to this measure?
ECM 23 | Building Envelope Install Additional Insulation | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 23 | DEER kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
[5 empty] | This project saves | 0 | kW peak demand |  | Existing | Existing insulation | 0 | 0 | 0 |  | This project saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
| Square footage of roof insulation installed |  |  |  | and | 0 | kWh electricity use. |  | Proposed | New insulation | 0 | 0 | 0 |  | and | 0 | kWh electricity use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Increased R value of roof insulation |  |  |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | Fuel Oil | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the IOU (or nearest IOU)area the unit is installed? |  | Choose your utility |  | or | 0 | energy cost annually. | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Adjusted Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total installed cost for this measure? |  |  |  | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | Net Present value of Savings |  | 0
| What is the utility rebate for this measure? |  |  |  | SIR | 0 | [8 empty] | Saving to Investment Ratio | 0 |  |  | Adjusted NPV of Savings |  | 0
Are there other non-repayable funds applied to this measure?

## EE Transformer
Calculators for Simple Low Voltage Distribution Transformer Project
School Information
School Name | Moorpark High School | [17 empty] | Inflation rate | 2%
School CDS Code | 56739405633250 | [17 empty] | Discount Rate | 5%
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021 | [17 empty] | Electricity Escalation | 4%
[19 empty] | Non-Energy Benefit | 5%
| 1. This calculator is based on new DOE/ TP1 & C802.2 approved efficiency standards. | [17 empty] | Maintenance saving | 3%
2. If you intend to use transformers that is the same as or higher than NEMA premium efficiency standard, you can perform your own savings calculation.
3. Only three phase dry type voltage levels are listed here.
4. Calculations based on tranformer efficincies at 35% load factor and assumed power factor of 0.9.
5. Calculator assumes transformer capacity is less than 3 times
ECM 24 | High Efficiency Dry-Type Low Voltage Distribution Transformer | Fill in your answers |  | Adjusted Energy Savings Summary | [5 empty] | ECM 24 | kWh Impact | DEER kW Impact | DEER therm impact | Energy Savings Summary |  |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
KVA level |  |  |  |  | This project saves | 0 | kW peak demand |  | Existing | Old | 0 | 0 | 0 |  | This project saves | 0 | kW peak demand |  | Year | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033
1000 | Quantity of 1000 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0 |  | and | 0 | kWh electricity use. |  | Proposed | New TRANS | 0 | 0 | 0 |  | and | 0 | kWh electricity use. |  | Energy Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 | Quantity of 750 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0 |  | and | 0 | therms natural gas |  |  | Savings | 0 | 0 | 0 |  | and | 0 | therms natural gas |  | Maintenance Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500 | Quantity of 500 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0 |  | or | 0 | gallons of | Fuel Oil | [6 empty] | or | 0 | gallons of | Fuel Oil | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | Quantity of 300 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0 |  | or | 0 | energy cost annually | [7 empty] | or | 0 | energy cost annually. |  | Net Cost/Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | Quantity of 225 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0 |  | Simple Payback is | 0 | years. | [7 empty] | Simple Payback is | 0 | years. |  | 20 year Net Present value |  | 0
150 | Quantity of 150 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0 |  | SIR | 0 | [8 empty] | SIR | 0
112.5 | Quantity of 112.5 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0
75 | Quantity of 75 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0
45 | Quantity of 45 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0
30 | Quantity of 30 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0
15 | Quantity of 15 kVA Transformer to be replaced with Premium Eff. Transformer? |  | 0
| What is the total installed cost for this measure? |  | 0
What is the utility rebate for this measure?
Are there other non-repayable funds applied to this measure?
Note: | Low voltage transformer is defined as an output voltage of 600 volts or less, and is rated at a frequency of 60 Hertz.
Efficiencies are determined at the following reference conditions: (1) for no-load losses, at the temperature of 20°C, and (2) for load-losses, at the temperature of 75°C and 35 percent of nameplate load.

## PV
| Calculators for Simple Photovoltaic Project | Version 8.1
School Information | [7 empty] | Inflation rate | 2%
School Name | Moorpark High School | [6 empty] | Discount Rate | 5%
School CDS Code | 56739405633250 | [6 empty] | Electricity Escalation | 4%
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021 | [6 empty] | Non-Energy Benefit | 5%
[8 empty] | Added Maintenance | 0.3%
Note:
1 | PV project needs to be sized properly and it can only save up to your last year's electricity bill amount.
2 | Assuming Net Energy Metering will be signed to claim credit.
3 | PV system only saves a portion of the demand due to rain, cloud shade and non-coincidental facility peak .
4 | Annual system maintenance cost is assumed to be 0.3% of project cost.
5 | Annual PV production degradation rate is assumed to be 0.7%.
6 | Assuming inverters will be replaced every 10 years and at a cost of | 0.6 | per Watt
7 | Annual kWh production for each kWac installed is assumed to be 1500 kWh/kW.
8 | To claim 25 year useful life, vendor must provide system warranty in writing.
9 | PV cost savings is calculated using 85% of the average electricity cost (due to little demand savings from PV system).
10 | Please use a separate life cycle cost analysis for PV project converting to PG&E A6 rate schedule.
Life Cycle Cost Analysis (EUL= 20 years)
ECM 25 | Installing Photovoltaic System | Fill in your answers |  | PV System Energy Savings Summary |  |  |  | Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
| How many PV panels will be installed? |  |  |  | This PV project produces | 0 | kWh first year | Year | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
| What is the PTC (PVUSA Test Con.) Wattage of each panel? |  |  |  | and approximately | 0 | kW demand | PV Annual kWh Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the name plate efficiency of the inverter? |  |  |  | or saves | 0 | energy cost first year. | Annual Cost Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total name plate capacity of the inverter? |  | kW |  | Maintenance cost | 0 | first year | Added Maintenance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| *For PV < 30 kW, What is the approved EPBB rebate amount? |  |  |  | Simple Payback is | 0 | years. | Inverter Replacement Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| *For PV >= 30 kW, What is the approved PBI rebate amount? |  |  |  | Saving to Investment Ratio | 0 |  | Financing cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other Non-repayable funds |  |  |  | **PV Size (kWac) | 0 | kW | Net Savings |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| What is the total project cost without rebate? | [6 empty] | Net Present value of Savings (20Yr) |  | 0
| Does PV vendor provide 25 year system warranty? | [6 empty] | Net Present value of Savings (25Yr) |  | 0
[8 empty] | Net Present value of Rebate |  | 0
* If you have rebate approved by utility, enter the total rebate amount. 5 year PBI rebate for systems >= 30 kW will be adjusted by discount rate for NPV. PV system < 30 kW, actual rebate amount will be used for SIR calculation.
**PV Size(CEC AC rating)=Number of panels x PTC panel wattage x inverter efficiency
***Simple payback is based on first year cost savings only.

## Total-Summary
School Information
School Name | Moorpark High School
School CDS Code | 56739405633250
Mailing Address | 5297 Maureen Lane, Moorpark, CA 93021
| Adjusted Energy Savings Summary* | [11 empty] | Estimated Energy Efficiency Measure Savings Summary
ECM | Energy Efficiency Project | Demand Savings | kWh Savings | Therm Savings | Propane Savings | Fuel Oil Savings | Annual Cost Savings | Project Cost | Utility Rebate & Non-repayable funds | Simple Payback | Adjusted SIR | ECM | Energy Efficiency Project | Demand Savings | kWh Savings | Therm Savings | Propane Savings | Fuel Oil Savings | Annual Cost Savings | Project Cost | Utility Rebate & Non-repayable funds | Simple Payback | SIR
|  | kW | kWh | Therms | Gallons | Gallons | $ | $ | $ | Years |  |  |  | kW | kWh | Therms | Gallons | Gallons | $ | $ | $ | Years
ECM 1 | Replace incandescent light with compact fluorescent light | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 1 | Replace incandescent light with compact fluorescent light | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 2A&2B | Replace incandescent/ CFL light with LED light | 0.0005164 | 12988.7946 | -41.0859 | 0 | 0 | 2336.1313 | 11875 | 0 | 5.0832 | 2.769 | ECM 2 | Replace incandescent/ CFL light with LED light | 1.4096 | 12988.7946 | -78.6449 | 0 | 0 | 2295.1279 | 11875 | 0 | 5.174 | 2.7204
ECM 3&4 | Convert incandescent/CFL exit sign to LED exit sign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 3&4 | Convert incandescent/CFL exit sign to LED exit sign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 5&6 | Convert T12 fluorescent to T8 with electronic ballast or LED lamps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 5&6 | Convert T12 fluorescent to T8 with electronic ballast or LED lamps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 6A | Convert 32 Watt T8 fluorescent fixture to LED lamps | 0.0093287 | 305033.5407 | -742.2117 | 0 | 0 | 55105.6328 | 663229 | 0 | 12.0356 | 1.5406 | ECM 6A | Convert 32 Watt T8 fluorescent fixture to LED lamps | 25.4651 | 305033.5407 | -1420.7123 | 0 | 0 | 54364.9112 | 663229 | 0 | 12.1996 | 1.5249
ECM 7 | Replace 32 Watt T8 lamps with 28 Watt T8 Lamps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 7 | Replace 32 Watt T8 lamps with 28 Watt T8 Lamps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 8&9 | Replace mercury vapor/HPS/Metal Halide with LED/Induction lights | 0 | 66394.23 | 0 | 0 | 0 | 9736.6175 | 121080 | 0 | 12.4355 | 1.503 | ECM 8&9 | Replace mercury vapor/HPS/Metal Halide with LED/Induction lights | 0 | 66394.23 | 0 | 0 | 0 | 9736.6175 | 121080 | 0 | 12.4355 | 1.503
ECM 10 | Install occupancy control for intermittently occupied rooms | 0.0053264 | 28733.722 | -2.1025 | 0 | 0 | 4211.4634 | 66894 | 0 | 15.8838 | 0.70627 | ECM 10 | Install occupancy control for intermittently occupied rooms | 14.5399 | 28733.722 | -4.0245 | 0 | 0 | 4209.3651 | 66894 | 0 | 15.8917 | 0.70603
ECM 11 | Replace old packaged/split HVAC unit with high efficiency HVAC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 11 | Replace old packaged/split HVAC unit with high efficiency HVAC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 12 | Replace old heat pump with high efficiency heat pump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 12 | Replace old heat pump with high efficiency heat pump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 13A | Replace boiler with high efficiency condensing boiler | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 13A | Replace boiler with high efficiency condensing boiler | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 13B | Replace furnace with high efficiency condensing furnace | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 13B | Replace furnace with high efficiency condensing furnace | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 14 | Seal existing HVAC leaky duct | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 14 | Seal existing HVAC leaky duct | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 15 | Install variable speed drive for pumps and fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 15 | Install variable speed drive for pumps and fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 16 | Replace manual thermostat with programmable/smart thermostat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 16 | Replace manual thermostat with programmable/smart thermostat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 17 | Replace old motor with premium efficiency motor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 17 | Replace old motor with premium efficiency motor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 18 | Replace storage water heater with gas-fired tankless water heater | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 18 | Replace storage water heater with gas-fired tankless water heater | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 19 | Install smart strip/PC management to control computers/printers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 19 | Install smart strip/PC management to control computers/printers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 20 | Install vending machine occupancy control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 20 | Install vending machine occupancy control | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 21 | Install new windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 21 | Install new windows | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 22 | Install cool roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 22 | Install cool roof | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 23 | Install additional insulation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 23 | Install additional insulation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 24 | Install new low voltage dry type distribution transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 24 | Install new low voltage dry type distribution transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECM 25 | Install photovoltaic system | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ECM 25 | Install photovoltaic system | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | 0.015172 | 413150.2874 | -785.4 | 0 | 0 | 71389.845 | 863078 | 0 | 12.0896 | 1.4876 |  | Total | 41.4147 | 413150.2874 | -1503.3817 | 0 | 0 | 70606.0218 | 863078 | 0 | 12.2239 | 1.4748
| *Energy Savings will be adjusted lower when lighting, HVAC and plug load savings exceed 50% of each end use technology category and capped at 45% of the total site kWh use. | [10 empty] | Grouped | Lighting Total | 41.4147 | 413150.2874 | -1503.3817 | 0 | 0 | 70606.0218 | 863078 | 0 | 12.2239 | 1.4748
| *Window energy savings will be Capped at 20% of the HVAC usage of new baseline data(by subtracting total saving from all ECMs from baseline). | [10 empty] | Grouped | HVAC/ENV Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| *Cool roof energy savings will be Capped at 15% of the HVAC usage of new baseline data(by subtracting total saving from all ECMs from baseline). | [10 empty] | Grouped | Plug Load Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| *Insulation energy savings will be Capped at 10% of the HVAC usage of new baseline data(by subtracting total saving from all ECMs from baseline). | [10 empty] | Grouped | Total | 41.4147 | 413150.2874 | -1503.3817 | 0 | 0
*Distribution transformer energy savings will be Capped at 6% of kWh usage of new baseline data(by subtracting total saving from all ECMs from baseline).

## AVG HVAC impact (hidden)
Average Energy Impact For Select DEER Database HVAC & Mechanical Measures
MeasureID | AvgOfkWh/unit | AvgOfkW/unit | AvgOftherm/unit | Ratio
airAC-SpltPkg-gte760kBtuh-10p0eer-wtd | 275.5 | 0.086875 | -0.49043 | (not used)
Com-RefrigCharge-wtd | 86.4333 | 0.072367 | -0.011177 | (not used)
Condensing Boiler/Furnace D03-065-AFUE 92-94 (PGE) | 0 | 0 | 6.54
Condensing Boiler/Furnace D03-065-AFUE 92-94 (SCE&SCG) | 0 | 0 | 3.073
Condensing Boiler/Furnace D03-065-AFUE 92-94 (SDGE) | 0 | 0 | 2.9633
Condensing Boiler/Furnace D03-065-AFUE 95-97 (PGE) | 0 | 0 | 8.0033
Condensing Boiler/Furnace D03-065-AFUE 95-97 (SCE&SCG) | 0 | 0 | 3.77
Condensing Boiler/Furnace D03-065-AFUE 95-97 (SDGE) | 0 | 0 | 3.6333
NE-HVAC-airAC-Pkg-lt65kBtuh-13p0seer (PGE) | 362.9167 | 0.091017 | -3.4708
NE-HVAC-airAC-Pkg-lt65kBtuh-13p0seer (SCE&SCG) | 394.7917 | 0.13725 | -2.1492 | 1.0878
NE-HVAC-airAC-Pkg-lt65kBtuh-13p0seer (SDGE) | 383.9167 | 0.20108 | -1.7493 | 1.0579
NE-HVAC-airAC-Pkg-lt65kBtuh-14p0seer (PGE) | 533.9167 | 0.14302 | -6.0658
NE-HVAC-airAC-Pkg-lt65kBtuh-14p0seer (SCE&SCG) | 553.8333 | 0.19737 | -4.03 | 1.0373
NE-HVAC-airAC-Pkg-lt65kBtuh-14p0seer (SDGE) | 467.6667 | 0.20063 | -3.2667 | 0.87592
dxHP-spltSEER-lt65kBtuh-13p0seer-7p7hspf (PGE) | 707 | 0.1186 | -0.001359
dxHP-spltSEER-lt65kBtuh-13p0seer-7p7hspf (SCE&SCG) | 625.8 | 0.2563 | -0.0009046 | 0.88515
dxHP-spltSEER-lt65kBtuh-13p0seer-7p7hspf (SDGE) | 525.8 | 0.19418 | -0.0007536 | 0.74371
dxHP-spltSEER-lt65kBtuh-14p0seer-8p3hspf (PGE) | 845.6667 | 0.16202 | 0.000214
dxHP-spltSEER-lt65kBtuh-14p0seer-8p3hspf (SCE&SCG) | 760.1667 | 0.27383 | -0.00031394 | 0.8989
dxHP-spltSEER-lt65kBtuh-14p0seer-8p3hspf (SDGE) | 745.5 | 0.40167 | -0.00043866 | 0.88155
dxHP-spltSEER-lt65kBtuh-15p0seer-8p8hspf (PGE) | 916.2 | 0.1601 | 0.0002568
dxHP-spltSEER-lt65kBtuh-15p0seer-8p8hspf (SCE&SCG) | 820.7 | 0.2965 | -0.00037673 | 0.89577
dxHP-spltSEER-lt65kBtuh-15p0seer-8p8hspf (SDGE) | 791.8 | 0.4308 | -0.0005264 | 0.86422
NB-HVAC-DuctSeal-high | 24.3 | 0.0072711 | -0.0096083
NB-HVAC-DuctSeal-low | 10.3025 | 0.0031777 | 0.000205 | (not used in calculator)
NG-WtrHt-LrgInst-Gas-gt225kBtuh-0p80Et | 0 | 0 | 2.3742
NG-WtrHt-LrgInst-Gas-gt225kBtuh-0p85Et | 0 | 0 | 3.1475
NG-WtrHt-LrgInst-Gas-gt225kBtuh-0p90Et | 0 | 0 | 3.8358
NG-WtrHt-MedInst-Gas-76to200kBtuh-0p80Et | 0 | 0 | 2.5533
NG-WtrHt-MedInst-Gas-76to200kBtuh-0p85Et | 0 | 0 | 3.3167
NG-WtrHt-MedInst-Gas-76to200kBtuh-0p90Et | 0 | 0 | 3.9958
NG-WtrHt-SmlInst-Gas-lte75kBtuh-lt2G-0p82EF | 0 | 0 | 2.0658
NG-WtrHt-SmlInst-Gas-lte75kBtuh-lt2G-0p82EF-AVG |  |  | 3.0413
Efficient HVAC Motors - Average-Epc-Epr-Ese | 45.2 | 0.098067 | -0.38479
Setback Network or Programmable Thermostats-Average-Epc-Epr-Ese | 620 | 0 | 31.3 | 190 | 18
VariableSpeedDrive HVAC-pumps- Fans -Average-ESe | 126.66 | 0.10007 | 5.4444
-0.0665

## AVG lighting impact (hidden)
Average Energy Impact for Select DEER Database Lighting Measures
MeasureID | AvgOfkWh/unit | AvgOfkW/unit | AvgOftherm/unit | AvgOfHours | AvgOfPeak Frac
Com-Iltg-dWatt-CFL-Avg-Epc-Epr-Ese | 2.6344 | 0.00028591 | -0.015951 | 2390 | 0.22989
Com-Iltg-dWatt-LED | 2.3835 | 0.00025868 | -0.014432 |  |  | Extrapolated from inc to CFL
Com-Iltg-dWatt-Exit-Avg-Epc-Epr-Ese | 9.3044 | 0.0011211 | -0.059722 | 8760 | 1
Com-Iltg-dWatt-LF-Avg-Epc-Epr-Ese | 2.55 | 0.00028863 | -0.015129 | 2300 | 0.22982
LF-Relamping-28 Watt-Avg-Epc-Epr-Ese | 2.55 | 0.00028863 | -0.015129 | 2300 | 0.22982 | extrapolated Linear retrofit
Occupancy Sensor(all)-Avg-Epc-Epr-Ese | 313.55 | 0.06135 | -2.0588 | 200
Com-Iltg-dWatt-LED | 2.509 | 0.0002723 | -0.015192 |  |  | Extrapolated from fluorescent to LED
PC power management interactive factor(extrapolated) | 106.2% |  | -0.01554 |  |  | kWh and therm impact extrapolated

## Lamp ratio (hidden)
DEER Database Lamp Replacement Ratio | [5 empty] | Lamp Ratio
CFL_Lamp | CFLratio0357 | CFL Ratio for all nonres CFLs |  |  | 4 ft. T12 linear fluorescent to T8 wattage ratio Total Watt (34 Watt) | 1.2203
ResInCFL_LampOth | CFLratio0347 | CFL Ratio for all res interior non-reflector CFLs |  |  | 4 ft. T12 linear fluorescent to T8 wattage ratio Total Watt (40 Watt) | 1.4576
ResInCFL_LampRefl | CFLratio0409 | CFL Ratio for res interior reflector CFLs |  |  | 4 ft. T8 Linear fluorescent to T8 (28 watt) or reduced ballast factor | 1.1837
ResOutCFL_Lamp | CFLratio0407 | CFL Ratio for all res exterior CFLs |  |  | 4 ft. T8 Linear fluorescent to LED (19 watt) tube | 1.5263
ResOutCFL_LampOth | CFLratio0407 | CFL Ratio for all res exterior CFLs |  |  | 4 ft. T12 40 watt Linear fluorescent to LED (19 watt) tube | 2.2632
ResOutCFL_LampRefl | CFLratio0407 | CFL Ratio for all res exterior CFLs |  |  | 4 ft. T12 34 watt Linear fluorescent to LED (19 watt) tube | 1.9474
CFL_Fixt | CFLratio0353 | CFL Ratio for all CFL fixtures
CFL_Lamp-CC | CFLratio0353 | IOU proposed value for cold cathode
LED_LampPAR20 | LEDratio0470 | LED PAR20 Basecase, Total Watts = 4.70 x Msr Watts
LED_LampPAR30 | LEDratio0342 | LED PAR30 Basecase, Total Watts = 3.42 x Msr Watts
LED_LampPAR38 | LEDratio0381 | LED PAR38 Basecase, Total Watts = 3.81 x Msr Watts
LED_LampA19 | LEDratio0296 | LED A19 Basecase, Total Watts = 2.96 x Msr Watts
LED_LampCandle | LEDratio0735 | LED Candelabra Basecase, Total Watts = 7.35 x Msr Watts
LED_LampGlb<3W | LEDratio0747 | LED Globe less than 3 Watts Basecase, Total Watts = 7.47 x Msr Watts
LED_LampGlb>=3W | LEDratio0494 | LED Globe greater than or equal to 3 Watts Basecase, Total Watts = 4.94 x Msr Watts
LED_LampMR16 | LEDratio0424 | LED MR16 Basecase, Total Watts = 4.24 x Msr Watts
LED_LampR<11W | LEDratio0609 | LED R/BR Basecase less than 11 Watts, Total Watts = 6.09 x Msr Watts
LED_LampR11-14W | LEDratio0480 | LED R/BR Basecase greater than or equal to 11, less than 14 Watts, Total Watts = 4.80 x Msr Watts
LED_LampR>=14W | LEDratio0434 | LED R/BR Basecase greater than or egual to 14 Watts, Total Watts = 4.34 x Msr Watts
LED_LampBR<11W | LEDratio0609 | LED R/BR Basecase less than 11 Watts, Total Watts = 6.09 x Msr Watts
LED_LampBR11-14W | LEDratio0480 | LED R/BR Basecase greater than or equal to 11, less than 14 Watts, Total Watts = 4.80 x Msr Watts
LED_LampBR>=14W | LEDratio0434 | LED R/BR Basecase greater than or egual to 14 Watts, Total Watts = 4.34 x Msr Watts
LED_Fixt | LEDratio0296 | LED_Fixture
LED_LampCanRet | LEDratio0342 | LED Can Retrofit
LED_LampAny | LEDratio0296 | LED Any Basecase, Total Watts = 2.96 x Msr Watts
CMH_Lamp | CMHratio0286 | Ballasted cermaic metal halide lamps
| Building Type |  |  | Savings Units |  |  | Lighting Measure Categories
| Code | Description |  | Code | Description |  | Energy Impact ID | Description
| ECC | Education - Community College |  | Cap-Tons | Capacity of equipment in Tons of cooling |  | Com-Iltg-dWatt-LF | Linear Fluorescent and HID lighting measures - savings are per deltaWatt for measure
| EPr | Education - Primary School |  | Cap-kBTUh | Capacity of equipment in kBTUh |  | Com-Iltg-dWatt-Exit | Exit fixture lighting measures - savings are per deltaWatt for measure
| ERC | Education - Relocatable Classroom |  | Cap-kW | Capacity of equipment in kW |  | Com-Iltg-dWatt-CFL | CFL and LED lamps and fixtures - savings are per deltaWatt for measure
| ESe | Education - Secondary School |  | Area-1kFP | Area of measure: 1000 square feet of footprint
| EUn | Education - University
|  | Measure type and application | Wattage Ratio
|  | CFL fixtures, interior and exterior: | 3.53
|  | Screw-in CFL lamps, interior and exterior: | 3.57
|  | LED lamps and fixtures, interior and exterior: | 3.23 | extrapolated
|  | CFL - LED fixtures, interior and exterior: | 2.96
|  | Incandescent to LED exit sign wattage ratio | 7.41 | average of above LED
|  | Mercury vapor fixtures to Induction or LED lights | 1.8 | extrapolated from ARRA data
|  | High Pressure sodium fixtures to Induction or LED lights | 1.7 | extrapolated from ARRA data
For CFL and LED measures, the delta Watts is determined as:
Measure deltaWatts = Measure Technology Watts x (WattageRatio - 1)
e.g. 13 Watt CFL fixture: dWatts = 13 * (3.53 -1) = 33 Watts

## Bldg Env Avg (hidden)
exante1314 database tables: Energy Impacts
This file created on 6/15/2015 2:37:12 PM while connected to localhost as sptviewer by READI (v2.2.0). | [7 empty] | 56640 |  | 2
Program/Database Description: READI v.2.2.0 (Current DEER and Non-DEER Ex Ante data. Includes data for review) | [7 empty] | 79.6199
EnergyImpactID | Version | BldgType | BldgVint | BldgHVAC | BldgLoc | NormUnit | NumUnit | MeasArea | ScaleBasis | APreEUkWh | APreEUkW | APreEUtherm | APreWBkWh | APreWBkW | APreWBtherm | AStdEUkWh | AStdEUkW | AStdEUtherm | AStdWBkWh | AStdWBkW | AStdWBtherm | ElecImpactProfileID | GasImpactProfileID | Flag | BldgType_desc | BldgVint_desc | BldgLoc_desc | IOUname | MeasureID | Qualifier | MeasureDesc | MeasImpactType | MeasTechEUL_ID | MeasTechDesc | StdTechDesc | BaseTechDesc | QualifierDesc
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | -10 | 0.0382 | 2.86 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Primary School | Existing | IOU Territory | PG&E | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | 3.58 | 8.12e-05 | 0.137 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCE | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | 3.03 | 0.000142 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCG | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | 8.32 | -0.00345 | -0.395 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SDG&E | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-016-Light Color Roof | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | 137 | 0.176 | -4.65 | 0 | 0 | 0 | 137 | 0.176 | -4.65 |  |  | 2 | Education - Primary School | Existing | IOU Territory | PG&E | D03-016 | None | Light Colored Roof | Standard |  | Roof absorptivity = 0.45 | T24 minimimum: cool roof per Section 118(i) | Roof absorptivity = 0.8 | Measure Definition does not have Energy Impact Qualifiers
D03-016-Light Color Roof | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | 175 | 0.156 | -3.61 | 0 | 0 | 0 | 175 | 0.156 | -3.61 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCE | D03-016 | None | Light Colored Roof | Standard |  | Roof absorptivity = 0.45 | T24 minimimum: cool roof per Section 118(i) | Roof absorptivity = 0.8 | Measure Definition does not have Energy Impact Qualifiers
D03-016-Light Color Roof | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | 179 | 0.155 | -3.52 | 0 | 0 | 0 | 179 | 0.155 | -3.52 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCG | D03-016 | None | Light Colored Roof | Standard |  | Roof absorptivity = 0.45 | T24 minimimum: cool roof per Section 118(i) | Roof absorptivity = 0.8 | Measure Definition does not have Energy Impact Qualifiers
D03-016-Light Color Roof | DEER2005 | EPr | Ex | Any | IOU | Area-1kR | 50 | 50000 | None | 0 | 0 | 0 | 162 | 0.136 | -3.27 | 0 | 0 | 0 | 162 | 0.136 | -3.27 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SDG&E | D03-016 | None | Light Colored Roof | Standard |  | Roof absorptivity = 0.45 | T24 minimimum: cool roof per Section 118(i) | Roof absorptivity = 0.8 | Measure Definition does not have Energy Impact Qualifiers
D03-022-East glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 473 | 0.389 | -21.1 | 0 | 0 | 0 | 135 | 0.107 | -7.1 |  |  | 2 | Education - Primary School | Existing | IOU Territory | PG&E | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022-East glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 463 | 0.223 | -12.1 | 0 | 0 | 0 | 184 | 0.0859 | -5.14 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCE | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022-East glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 464 | 0.218 | -11.7 | 0 | 0 | 0 | 193 | 0.088 | -5.17 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCG | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022-East glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 433 | 0.214 | -10.3 | 0 | 0 | 0 | 165 | 0.0828 | -4.44 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SDG&E | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023-South glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 620 | 0.657 | -35.4 | 0 | 0 | 0 | 179 | 0.202 | -11.9 |  |  | 2 | Education - Primary School | Existing | IOU Territory | PG&E | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023-South glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 648 | 0.494 | -23 | 0 | 0 | 0 | 260 | 0.201 | -9.72 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCE | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023-South glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 654 | 0.491 | -22.3 | 0 | 0 | 0 | 273 | 0.207 | -9.78 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCG | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023-South glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 7.6 | 50000 | None | 0 | 0 | 0 | 630 | 0.415 | -20.7 | 0 | 0 | 0 | 243 | 0.158 | -8.93 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SDG&E | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-West glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 9.29 | 50000 | None | 0 | 0 | 0 | 479 | 0.73 | -14.3 | 0 | 0 | 0 | 140 | 0.223 | -4.83 |  |  | 2 | Education - Primary School | Existing | IOU Territory | PG&E | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-West glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 9.29 | 50000 | None | 0 | 0 | 0 | 488 | 0.544 | -8.44 | 0 | 0 | 0 | 198 | 0.221 | -3.57 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCE | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-West glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 9.29 | 50000 | None | 0 | 0 | 0 | 492 | 0.537 | -8.12 | 0 | 0 | 0 | 208 | 0.228 | -3.56 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SCG | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-West glass SHGC 30% less than required | DEER2005 | EPr | Ex | Any | IOU | Area-100Win | 9.29 | 50000 | None | 0 | 0 | 0 | 472 | 0.453 | -7.48 | 0 | 0 | 0 | 186 | 0.171 | -3.29 |  |  | 2 | Education - Primary School | Existing | IOU Territory | SDG&E | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | ERC | Ex | Any | IOU | Area-1kR | 1.92 | 1920 | None | 0 | 0 | 0 | 305 | 0.287 | 0.443 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | PG&E | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | ERC | Ex | Any | IOU | Area-1kR | 1.92 | 1920 | None | 0 | 0 | 0 | 279 | 0.268 | 0.328 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCE | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | ERC | Ex | Any | IOU | Area-1kR | 1.92 | 1920 | None | 0 | 0 | 0 | 283 | 0.261 | 0.327 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCG | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation up to current standard | DEER2005 | ERC | Ex | Any | IOU | Area-1kR | 1.92 | 1920 | None | 0 | 0 | 0 | 241 | 0.226 | 0.314 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SDG&E | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | -60.3 | 0.121 | -0.588 | 0 | 0 | 0 | -25.7 | 0.0522 | -0.266 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | PG&E | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 72.6 | 0.102 | -0.553 | 0 | 0 | 0 | 32.6 | 0.0151 | -0.268 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCE | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 72.6 | 0.0879 | -0.538 | 0 | 0 | 0 | 33.1 | 0.0123 | -0.264 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCG | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 93.5 | 0.187 | -0.534 | 0 | 0 | 0 | 45 | 0.000957 | -0.263 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SDG&E | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 124 | 0.362 | 0 | 0 | 0 | 0 | 45.4 | 0.13 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | PG&E | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 277 | 0.318 | 0 | 0 | 0 | 0 | 127 | 0.194 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCE | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 282 | 0.316 | 0 | 0 | 0 | 0 | 131 | 0.209 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCG | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 312 | 0.289 | 0 | 0 | 0 | 0 | 144 | 0.0862 | 0 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SDG&E | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-South glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 123 | 0.364 | -0.845 | 0 | 0 | 0 | 48.8 | 0.088 | -0.38 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | PG&E | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024 West glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 226 | 0.367 | -0.777 | 0 | 0 | 0 | 105 | 0.229 | -0.378 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCE | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024 West glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 229 | 0.361 | -0.76 | 0 | 0 | 0 | 108 | 0.243 | -0.373 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SCG | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024 West glass SHGC 30% less than required | DEER2005 | ERC | Ex | Any | IOU | Area-100Win | 0.32 | 1920 | None | 0 | 0 | 0 | 236 | 0.327 | -0.767 | 0 | 0 | 0 | 112 | 0.122 | -0.384 |  |  | 2 | Education - Relocatable Classroom | Existing | IOU Territory | SDG&E | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation raised to current standard | DEER2005 | ESe | Ex | Any | IOU | Area-1kR | 93.8 | 150000 | None | 0 | 0 | 0 | -11.3 | 0.0186 | 3.16 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | PG&E | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation raised to current standard | DEER2005 | ESe | Ex | Any | IOU | Area-1kR | 93.8 | 150000 | None | 0 | 0 | 0 | 3.6 | 0.00549 | 0.118 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCE | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation raised to current standard | DEER2005 | ESe | Ex | Any | IOU | Area-1kR | 93.8 | 150000 | None | 0 | 0 | 0 | 3.01 | 0.00505 | 0.111 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCG | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-013-Ceiling/Roof insulation raised to current standard | DEER2005 | ESe | Ex | Any | IOU | Area-1kR | 93.8 | 150000 | None | 0 | 0 | 0 | 8.62 | 0.00125 | -0.47 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SDG&E | D03-013 | None | Ceiling/Roof Insulation | Standard |  | Ceiling R-value for oldest vintages increased to 'new' level | T24 maximum overall U-Factor per Table | Ceiling R-value based on vintage and climate zone | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 293 | 0.323 | -17.4 | 0 | 0 | 0 | 83.7 | 0.0915 | -6.17 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | PG&E | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 301 | 0.198 | -11.7 | 0 | 0 | 0 | 119 | 0.0796 | -5.1 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCE | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 299 | 0.194 | -11.5 | 0 | 0 | 0 | 123 | 0.0809 | -5.2 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCG | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022 East glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 288 | 0.177 | -9.76 | 0 | 0 | 0 | 112 | 0.0714 | -4.5 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SDG&E | D03-022 | None | Low SHGC Windows -30% - East | Standard |  | East glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 437 | 0.487 | -25.5 | 0 | 0 | 0 | 125 | 0.151 | -9.42 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | PG&E | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 496 | 0.392 | -14.4 | 0 | 0 | 0 | 198 | 0.162 | -6.23 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCE | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 497 | 0.388 | -13.7 | 0 | 0 | 0 | 207 | 0.167 | -6.13 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCG | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-023 South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 490 | 0.318 | -12.7 | 0 | 0 | 0 | 192 | 0.125 | -5.75 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SDG&E | D03-023 | None | Low SHGC Windows -30% - South | Standard |  | South glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 330 | 0.543 | -18.6 | 0 | 0 | 0 | 96.3 | 0.163 | -6.82 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | PG&E | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 367 | 0.398 | -11.1 | 0 | 0 | 0 | 150 | 0.164 | -4.55 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCE | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 367 | 0.391 | -10.8 | 0 | 0 | 0 | 156 | 0.167 | -4.5 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SCG | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-024-South glass SHGC 30% less than required | DEER2005 | ESe | Ex | Any | IOU | Area-100Win | 36.6 | 150000 | None | 0 | 0 | 0 | 365 | 0.338 | -9.32 | 0 | 0 | 0 | 147 | 0.134 | -4.09 |  |  | 2 | Education - Secondary School | Existing | IOU Territory | SDG&E | D03-024 | None | Low SHGC Windows -30% - West | Standard |  | West glass SHGC 30% less than required by T-24 | T24 maximum SHGC matches prototype level | glass type as defined by location and window-wall ratio | Measure Definition does not have Energy Impact Qualifiers
D03-022-East glass SHGC 30% less than required(2005) | PG&E | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 235.2333 | 0.27767 | -13.0293
D03-022-East glass SHGC 30% less than required(2005) | SCE/SCG | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 278.7 | 0.17048 | -8.0152
D03-022-East glass SHGC 30% less than required(2005) | SCG | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None
D03-022-East glass SHGC 30% less than required(2005) | SDG&E | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 271.5 | 0.19267 | -6.8647
D03-023-South glass SHGC 30% less than required(2005) | PG&E | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 393.6667 | 0.502 | -20.3
D03-023-South glass SHGC 30% less than required(2005) | SCE/SCG | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 475.6667 | 0.39983 | -12.2333
D03-023-South glass SHGC 30% less than required(2005) | SCG | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None
D03-023-South glass SHGC 30% less than required(2005) | SDG&E | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 477.3333 | 0.34067 | -11.1333
D03-024-West glass SHGC 30% less than required(2005) | PG&E | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 310.6667 | 0.54567 | -11.2483
D03-024-West glass SHGC 30% less than required(2005) | SCE/SCG | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 361.5 | 0.433 | -6.6662
D03-024-West glass SHGC 30% less than required(2005) | SCG | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None
D03-024-West glass SHGC 30% less than required(2005) | SDG&E | EPR_ERC_ES | Ex | Any | IOU | Area-100Win | 7.6_0.32_36.6 | 50000_1920_150000 | None |  |  |  | 357.6667 | 0.37267 | -5.8557
D03-013-Ceiling/Roof insulation up to current standard(2005) | PG&E | EPR_ERC_ES | Ex | Any | IOU | Area-1kR | 50_1.92_93.8 | 50000_1920_150000 |  |  |  |  | 94.5667 | 0.1146 | 2.1543
D03-013-Ceiling/Roof insulation up to current standard(2005) | SCE/SCG | EPR_ERC_ES | Ex | Any | IOU | Area-1kR | 50_1.92_93.8 | 50000_1920_150000 |  |  |  |  | 95.87 | 0.089961 | 0.19217
D03-013-Ceiling/Roof insulation up to current standard(2005) | SDG&E | EPR_ERC_ES | Ex | Any | IOU | Area-1kR | 50_1.92_93.8 | 50000_1920_150000 |  |  |  |  | 85.98 | 0.0746 | -0.18367
D03-016-Light Color Roof | PG&E | EPR |  | Any | IOU | Area-1kR | 50 | 50000 |  |  |  |  | 137 | 0.176 | -4.65
D03-016-Light Color Roof | SCE/SCG | EPR |  | Any | IOU | Area-1kR | 50 | 50000 |  |  |  |  | 177 | 0.1555 | -3.565
D03-016-Light Color Roof | SDG&E | EPR |  | Any | IOU | Area-1kR | 50 | 50000 |  |  |  |  | 162 | 0.136 | -3.27