## Lead Test Results
Water Testing Results - | Oakdale Elementary
Action Level is 15 parts per billion (ppb)
Fixture Location/Description | Fixture ID # | Test Date | Test Result
Kitchen Sink Faucet (new 2018) | 21900100-001KF | 2023-04-17 | ND
Kitchen Sink Faucet (new 2018) | 21900100-002KF | 2023-04-17 | ND
Kitchen Sink Faucet (new 2018) | 21900100-003KF | 2023-04-17 | 2.55
Kitchen Soup Pot (new sink2018) | 21900100-004KF | 2023-04-17 | ND
Music Room Sink Faucet (rm#20) | 21900100-005CF | 2023-04-18 | 1.44
Music Room Drinking Fountain (rm#20) | 21900100-006DW | 2023-04-18 | ND
Gym Drinking Fountain (new 2018) | 21900100-007DW | 2023-04-17 | ND
Rm19 Sink Faucet (Rm#22) | 21900100-008CF | 2023-04-19 | 6.14
Rm19 Drinking Fountain (Rm#22) | 21900100-009DW | Fixture N/A
Rm19 Sink Faucet (Rm#22) | 21900100-010CF | 2023-04-19 | 16.5
Rm1 Sink Faucet | 21900100-011CF | 2023-04-19 | 4.36
Rm1 Drinking Fountain | 21900100-012DW | 2023-04-19 | 1.48
Rm2 Sink Faucet | 21900100-013CF | 2023-04-19 | 9.41
Rm2 Drinking Fountain | 21900100-014DW | 2023-04-19 | 4.7
Rm3 Sink Faucet | 21900100-015CF | 2023-04-19 | 6.65
Rm3 Drinking Fountain | 21900100-016DW | 2023-04-19 | 5.41
Rm4 Sink Faucet | 21900100-017CF | 2023-04-19 | 3.62
Rm4 Drinking Fountain | 21900100-018DW | 2023-04-19 | 3.43
Rm5 Sink faucet | 21900100-019CF | 2023-04-19 | 26.7
Rm5 Drinking Fountain | 21900100-020DW | 2023-04-19 | 6.46
Rm6 Sink Faucet | 21900100-021CF | 2023-04-19 | 7.5
Rm6 Drinking Fountain | 21900100-022DW | 2023-04-19 | 21.2
Rm5/6 Sink Faucet | 21900100-023CF | 2023-04-19 | 17.4
Hallway Drinking Fountain #1 | 21900100-024DW | 2023-04-19 | ND
Rm7 Sink Faucet | 21900100-025CF | 2023-04-19 | 3.4
Rm7 Drinking Fountain | 21900100-026DW | 2023-04-19 | 2.71
Rm8 Sink Faucet | 21900100-027CF | 2023-04-19 | 2.47
Rm8 Drinking Fountain | 21900100-028DW | 2023-04-19 | 8.04
Rm 8/9 Sink Faucet | 21900100-029CF | 2023-04-19 | 4.64
Rm. 9 Sink Fountain | 21900100-030CF | 2023-04-19 | 1.56
Rm. 9 Drinking Fountain | 21900100-031DW | 2023-04-19 | 1.3
Rm. 10 Sink Faucet | 21900100-032CF | 2023-04-19 | 2.72
Rm. 10 Drinking Fountain | 21900100-033DW | 2023-04-19 | 1.72
Rm. 10/11 | 21900100-034CF | 2023-04-19 | 1.44
Rm. 11 Sink Faucet | 21900100-035CF | 2023-04-19 | 6.99
Rm. 11 Drinking Fountain | 21900100-036DW | 2023-04-19 | 4.22
Rm. 12 Sink Faucet | 21900100-037CF | 2023-04-19 | 2.26
Rm. 12 Drinking Fountian | 21900100-038DW | 2023-04-19 | 1.08
Rm. 13 Sink Faucet | 21900100-039CF | 2023-04-19 | 9.87
Rm. 13 Drinking Fountain | 21900100-040DW | 2023-04-19 | 27.1
Rm. 14 Sink Faucet | 21900100-041CF | 2023-04-19 | 8.41
Rm. 14 Drinking Fountain | 21900100-042DW | 2023-04-19 | 12.8
Rm. 14/15 Sink Faucet | 21900100-043CF | 2023-04-19 | 16
Rm. 15 Sink Faucet | 21900100-044CF | 2023-04-19 | 12.9
Rm. 15 Drinking Fountain | 21900100-045DW | 2023-04-19 | 8.41
Rm. 16 Sink Faucet | 21900100-046CF | 2023-04-19 | 28.4
Rm. 16 Drinking Fountain | 21900100-047DW | 2023-04-19 | ND
Rm . 16/17 Sink Faucet | 21900100-048CF | 2023-04-19 | 5.53
Hallway Drinking Fountain #2 | 21900100-049DW | 2023-04-19 | ND
Rm. 18 Sink Faucet | 21900100-050CF | 2023-04-19 | 4.85
Rm. 18 Drinking Fountain | 21900100-051DW | 2023-04-19 | 5.65
Library Sink Faucet (Work Room) | 21900100-052CF | 2023-04-18 | 13.1
Health Rm. Sink Faucet | 21900100-053CF | 2023-04-18 | 1.84
Faculty Lounge Sink Faucet | 21900100-054SF | 2023-04-18 | 13.9
Facilty Restroom | 21900100-055BF | 2023-04-18 | ND
Faculty Restroom | 21900100-056BF | 2023-04-18 | 4.41
Girls Restroom | 21900100-057BF | 2023-04-18 | 1.35
Girls Restroom | 21900100-058BF | 2023-04-18 | 3.82
Girls Restroom | 21900100-059BF | 2023-04-18 | 1.07
Boys Restroom | 21900100-060BF | 2023-04-18 | 5.91
Boys Restroom | 21900100-061BF | 2023-04-18 | 1
Boys Restroom | 21900100-062BF | 2023-04-18 | 1
Girls Restroom Sink Faucet | 21900100-063BF | 2023-04-18 | ND
Girls Restroom Sink Faucet | 21900100-064BF | 2023-04-18 | ND
Girls Restroom Sink Faucet | 21900100-065BF | 2023-04-18 | ND
Boys Restroom Sink Faucet | 21900100-066BF | 2023-04-18 | ND
Boys Restroom Sink Faucet | 21900100-067BF | 2023-04-18 | ND
Boys Restroom Sink Faucet | 21900100-068BF | 2023-04-18 | ND
Girls Restroom Sink Faucet | 21900100-069BF | Fixture N/A
Girls Restroom Sink Faucet | 21900100-070BF | Fixture N/A
Boys Restroom Sink Faucet | 21900100-071BF | Fixture N/A
Boys Restroom Sink Faucet | 21900100-072BF | Fixture N/A
Kitchen - Sink Faucet | 21900100-073KF | Fixture N/A
Kitchen - Soup Pot | 21900100-074KF | Fixture N/A
Music Room - Sink Faucet | 21900100-075CF | Fixture N/A
Classroom 19 - Sink Faucet | 21900100-076SF | Fixture N/A
Classroom 13 - Sink Faucet | 21900100-077SF | Fixture N/A
Classroom 12 - Drinking Fountain | 21900100-078DW | Fixture N/A
Classroom 16 - 17 - Sink Faucet | 21900100-079CF | Fixture N/A
Kitchen Sink Faucet (new 2018) | 21900100-080KF | 2023-04-17 | ND
Kitchen Sink Faucet (new 2018) | 21900100-081KF | 2023-04-17 | ND
MPR sink | 21900100-082KF | 2023-04-17 | ND
MPR Drinking fountain | 21900100-083DF | 2023-04-17 | ND
MPR Drinking fountain | 21900100-084DF | 2023-04-17 | ND
MPR Bottle fill | 21900100-085WB | 2023-04-18 | ND
Gym Bottle fill | 21900100-086WB | 2023-04-18 | ND
Gym Drinking Fountain | 21900100-087DF | 2023-04-18 | ND
Custodial closet mop sink | 21900100-088SF | 2023-04-18 | ND
Boys restroom gym hall | 21900100-089BF | 2023-04-18 | ND
Boys restroom gym hall | 21900100-090BF | 2023-04-18 | ND
Boys restroom gym hall | 21900100-091BF | 2023-04-18 | ND
Girls restroom gym hall | 21900100-092BF | 2023-04-18 | ND
Girls restroom gym hall | 21900100-093BF | 2023-04-18 | ND
Girls restroom gym hall | 21900100-094BF | 2023-04-18 | ND
Restroom gym hall | 21900100-095BF | 2023-04-18 | ND
Sick room faucet | 21900100-096BF | 2023-04-18 | 1.56
Sick room faucet | 21900100-097BF | 2023-04-18 | 4.53
Rm#22 sink faucet | 21900100-098SF | 2023-04-19 | ND
Rm#22 restroom | 21900100-099BF | 2023-04-19 | ND
Hallway Drinking Fountain #1B | 21900100-100DW | 2023-04-19 | ND
Hallway Bottle Fill #1C | 21900100-101WB | 2023-04-19 | ND
Hallway Drinking Fountain #2B | 21900100-102DW | 2023-04-19 | ND
Hallway Bottle Fill #2C | 21900100-103DW | 2023-04-19 | ND
Classroom 17 - Sink Faucet | 21900100-104SF | 2023-04-19 | 4.77
Classroom 17 drinking Fountain | 21900100-105DW | 2023-04-19 | 8.63
Classroom 21 sink faucet | 21900100-106SF | 2023-04-19 | 3.53
Classroom 21 Drinking Fountain | 21900100-107DW | 2023-04-19 | 1.73
Any fixture testing at or above the action level of 15 ppb is immediately removed from service and cannot be returned to service until it has been remediated and passed follow-up testing
RETESTS | 21900100-10CFB | 2023-06-15 | ND
Rm19 Sink Faucet (Rm#22) | 21900100-019CFB | 2023-06-15 | ND
Rm5 Sink faucet | 2190100-022DWB | 2023-06-15 | 2.16
Rm6 Drinking Fountain | 21900100-023CFB | 2023-06-15 | 4.98
Rm5/6 Sink Faucet | 21900100-046CF | 2023-06-15 | ND
Rm. 16 Sink Faucet
ND = Non Detect - Lead level is below the set detection limits |  |  | of 1 ppb