## Lead Test Results
Water Testing Results - | Dallas High School
Action Level is 15 parts per billion (ppb)
Fixture Location/Description | Fixture ID # | Test Date | Test Result
Kitchen Sink Faucet Hand Wash Sink | 21900500-001KF | 2024-04-09 | ND
Kitchen Sink Faucet SE | 21900500-002KF | 2024-04-09 | ND
Kitchen Sink Faucet SW Left | 21900500-003KF | 2024-04-09 | ND
Kitchen Sink Faucet SW Right | 21900500-004KF | 2024-04-09 | ND
Kitchen Sink Faucet Ala Carte | 21900500-005KF | 2024-04-09 | 7.44
Kitchen Soup Pot | 21900500-006KF | 2024-04-09 | ND
Girls' Restroom Sink Faucet Left | 21900500-007BF | 2024-04-09 | ND
Girls' Restroom Sink Faucet Center | 21900500-008BF | 2024-04-09 | ND
Girls' Restroom Sink Faucet Right | 21900500-009BF | 2024-04-09 | ND
Custodial Sink Faucet | 21900500-010SF | N/A
Boys' Restroom Sink Faucet Left | 21900500-011BF | 2024-04-09 | ND
Boys' Restroom Sink Faucet Center | 21900500-012BF | 2024-04-09 | ND
Boys' Restroom Sink Faucet Right | 21900500-013BF | 2024-04-09 | 9.86
Rm. 735 Sink Faucet | 21900500-014CF | 2024-04-09 | ND
Rm. 731 (Laundry) Sink Faucet | 21900500-015SF | 2024-04-09 | 2.21
Rm. 731 Restroom Sink Faucet | 21900500-016BF | 2024-04-09 | 1.56
Rm. 731 Sink Faucet Teacher | 21900500-017CF | 2024-04-09 | ND
Rm. 731 Sink Faucet South | 21900500-018CF | 2024-04-09 | 3.89
Rm. 731 Sink Faucet Southwest | 21900500-019CF | 2024-04-09 | ND
Rm. 731 Sink Faucet West Left | 21900500-020CF | 2024-04-09 | ND
Rm. 731 Sink Faucet West Right | 21900500-021CF | 2024-04-09 | ND
Rm. 731 Sink Faucet Northwest | 21900500-022CF | 2024-04-09 | ND
Rm. 731 Sink Faucet Noth | 21900500-023CF | 2024-04-09 | ND
Hallway Drink Fountain #1 (Left) | 21900500-024DW | 2024-04-11 | ND
Hallway Drink Fountain #2 (Right) | 21900500-025DW | 2024-04-11 | ND
Hallway Drink Fountain #3 (chilled) | 21900500-026DW | N/A
Rm. 306 Sink Faucet | 21900500-027CF | 2024-04-11 | ND
Women's Dressing Room Sink Faucet | 21900500-028CF | 2024-04-11 | ND
Men's Dressing Room Sink Faucet | 21900500-029CF | 2024-04-11 | ND
Unisex Restroom Sink Left | 21900500-030BF | 2024-04-11 | ND
Unisex Restroom Sink Right | 21900500-031BF | 2024-04-11 | ND
Rm. 314 Sink | 21900500-032CF | 2024-04-11 | 1.73
Rm. 314 Drink | 21900500-033DW | 2024-04-11 | ND
Rm. 313 Drink Fountain | 21900500-034DW | 2024-04-11 | ND
Water Bottle Refill #4(Chilled) Theater Hall | 21900500-035WB | 2024-04-11 | ND
Hallway Drink Fountain #5 (chilled) Theater Hall | 21900500-036DW | 2024-04-11 | ND
Girls' Restroom Sink Faucet Left | 21900500-037BF | 2024-04-11 | ND
Girls' Restroom Sink Faucet Center | 21900500-038BF | 2024-04-11 | ND
Girls' Restroom Sink Faucet Right | 21900500-039BF | 2024-04-11 | ND
Boys' Restroom Sink Faucet Left | 21900500-040BF | 2024-04-11 | ND
Boys' Restroom Sink Faucet Center | 21900500-041BF | 2024-04-11 | ND
Boys' Restroom Sink Faucet Right | 21900500-042BF | 2024-04-11 | ND
Office Staff Break Room Sink Faucet | 21900500-043SF | 2024-04-11 | ND
Office Staff Break Room Ice Maker | 21900500-044IM | 2024-04-11 | 2.86
Rm. 107 Custodial Sink Faucet | 21900500-045SF | N/A
Rm. 108 Sink Faucet | 21900500-046CF | 2024-04-11 | 7.71
Rm. 212 Sink Faucet | 21900500-047CF | N/A
Rm. 212 Sink Faucet | 21900500-048CF | N/A
Rm. 212 Sink Faucet | 21900500-049CF | N/A
Rm. 212 Sink Faucet | 21900500-050CF | N/A
Rm. 212 Sink Faucet | 21900500-051CF | N/A
Rm. 212 Sink Faucet | 21900500-052CF | N/A
Rm. 212 Sink Faucet | 21900500-053CF | N/A
Rm. 212 Sink Faucet | 21900500-054CF | N/A
Hallway Drink Fountain #6 Across From Library (Chilled) | 21900500-055DW | 2024-04-11 | ND
Hallway Drink Fountain #7 Across From Library(Chilled)w/WB | 21900500-056DW | 2024-04-11 | ND
Water Bottle Refill #1 Across from Library (Chilled) | 21900500-057WB | 2024-04-11 | ND
Rm. 124 Restroom Sink Faucet | 21900500-058BF | 2024-04-11 | ND
Rm. 120 Sink Faucet | 21900500-059CF | 2024-04-11 | 1.95
Rm. 120 Restroom Sink Faucet | 21900500-060BF | 2024-04-11 | ND
Custodial Office Sink Faucet | 21900500-061SF | N/A
Rm. 626 Sink Faucet Left | 21900500-062CF | 2024-04-12 | ND
Rm. 626 Sink Faucet Right | 21900500-063CF | 2024-04-12 | ND
Rm. 626 Storage Sink Faucet | 21900500-064SF | 2024-04-12 | ND
Rm. 626 Pottery Wheel Room Sink Faucet | 21900500-065CF | 2024-04-12 | ND
Rm. 630 Sink Faucet Left | 21900500-066CF | 2024-04-12 | ND
Rm. 630 Sink Faucet Right | 21900500-067CF | 2024-04-12 | ND
Girls' Locker Room Sink Faucet Left | 21900500-068BF | 2024-04-12 | ND
Girls' Locker Room Sink Faucet Center | 21900500-069BF | 2024-04-12 | ND
Girls' Locker Room Sink Faucet Right | 21900500-070BF | 2024-04-12 | ND
Girls' Locker Room Coaches Office Sink Faucet Left | 21900500-071SF | 2024-04-12 | ND
Girls' Locker Room Coaches Office Sink Faucet Right | 21900500-072SF | 2024-04-12 | ND
Girls' Locker Room Drink Fountain (left) | 21900500-073DW | 2024-04-12 | ND
Girls' Locker Room Drink Fountain (right) | 21900500-074DW | 2024-04-12 | ND
Training Room Sink Faucet | 21900500-075CF | 2024-04-12 | ND
Training Room Ice Maker | 21900500-076IM | 2024-04-12 | ND
Auxillary Gym Drink Fountain Left | 21900500-077DW | 2024-04-12 | ND
Auxillary Gym Drink Fountain Right | 21900500-078DW | 2024-04-12 | ND
Boys' Locker Room Coach's Office Sink Faucet Left | 21900500-079SF | 2024-04-12 | ND
Boys' Locker Room Coach's Office Sink Faucet Right | 21900500-080SF | 2024-04-12 | ND
Boys' Locker Room Drink Fountain Left | 21900500-081DW | 2024-04-12 | ND
Boys' Locker Room Drink Fountain Right | 21900500-082DW | 2024-04-12 | ND
Boys' Locker Room Sink Faucet Left | 21900500-083BF | 2024-04-12 | ND
Boys' Locker Room Sink Faucet Center | 21900500-084BF | 2024-04-12 | ND
Boys' Locker Room Sink Faucet Right | 21900500-085BF | 2024-04-12 | ND
Custodial Office Sink Faucet | 21900500-086SF | N/A
Custodial Office Sink Faucet | 21900500-087SF | N/A
Hallway Drink Fountain #8 Athletics Hall | 21900500-088DW | 2024-04-12 | ND
Hallway Drink Fountain #10 w/WB Athletics Hall | 21900500-089DW | 2024-04-12 | ND
Unisex Restroom Sink Faucet Upper Gym | 21900500-090BF | N/A
Men's Restroom Sink Upper Gym | 21900500-091BF | N/A
Teachers' Lounge Sink Faucet | 21900500-092SF | N/A
Boys' Locker Room Sink Faucet Left | 21900500-093BF | 2024-04-12 | 26.5
Boys' Locker Room Sink Faucet Right | 21900500-094BF | 2024-04-12 | 7.51
Boys' Locker Room Drink Fountain | 21900500-095BF | 2024-04-12 | 9.3
Concessions Sink Faucet | 21900500-096KF | N/A
Boys' Restroom Sink Faucet Left | 21900500-097BF | N/A
Boys' Restroom Sink Faucet CenLeft | 21900500-098BF | 2024-04-12 | ND
Boys' Restroom Sink Faucet Center | 21900500-099BF | 2024-04-12 | ND
Boys' Restroom Sink Faucet CenRight | 21900500-100BF | 2024-04-12 | ND
Boys' Restroom Sink Faucet Right | 21900500-101BF | 2024-04-12 | ND
Girls' Restroom Sink Faucet Left | 21900500-102BF | 2024-04-12 | ND
Girls' Restroom Sink Faucet CenLeft | 21900500-103BF | 2024-04-12 | ND
Girls' Restroom Sink Faucet Center | 21900500-104BF | 2024-04-12 | ND
Girls' Restroom Sink Faucet CenRight | 21900500-105BF | 2024-04-12 | ND
Girls' Restroom Sink Faucet Right | 21900500-106BF | 2024-04-12 | ND
Hallway Drink Fountain #11 | 21900500-107DW | N/A
Boiler Room Sink Faucet | 21900500-108SF | N/A
Rm. 902 Sink Faucet | 21900500-109CF | 2024-04-12 | ND
Hallway Drink Fountain #12 | 21900500-110DW | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-111CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-112CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-113CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-114CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-115CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-116CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-117CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-118CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-119CF | N/A
Rm. 918 Science Lab Sink Faucet | 21900500-120CF | N/A
Rm. 910 Sink Faucet | 21900500-121CF | N/A
Rm. 910 Sink Faucet | 21900500-122CF | N/A
Rm. 910 Sink Faucet | 21900500-123CF | N/A
Rm. 910 Sink Faucet | 21900500-124CF | N/A
Rm. 910 Sink Faucet | 21900500-125CF | N/A
Rm. 910 Sink Faucet | 21900500-126CF | N/A
Rm. 910 Sink Faucet | 21900500-127CF | N/A
Rm. 910 Sink Faucet | 21900500-128CF | N/A
Rm. 910 Sink Faucet | 21900500-129CF | N/A
Rm. 910 Storage Sink Faucet | 21900500-130CF | N/A
Rm. 910 Storage Sink Faucet | 21900500-131CF | N/A
Rm. 911 Sink Faucet | 21900500-132CF | N/A
Rm. 911 Sink Faucet | 21900500-133CF | N/A
Rm. 911 Sink Faucet | 21900500-134CF | N/A
Rm. 911 Sink Faucet | 21900500-135CF | N/A
Rm. 911 Sink Faucet | 21900500-136CF | N/A
Rm. 911 Sink Faucet | 21900500-137CF | N/A
Rm. 911 Sink Faucet | 21900500-138CF | N/A
Rm. 911 Sink Faucet | 21900500-139CF | N/A
Rm. 911 Sink Faucet | 21900500-140CF | N/A
Rm. 916 Sink Faucet | 21900500-141CF | N/A
Rm. 916 Sink Faucet | 21900500-142CF | N/A
Rm. 916 Sink Faucet | 21900500-143CF | N/A
Rm. 916 Sink Faucet | 21900500-144CF | N/A
Rm. 916 Sink Faucet | 21900500-145CF | N/A
Rm. 916 Sink Faucet | 21900500-146CF | N/A
Rm. 916 Sink Faucet | 21900500-147CF | N/A
Rm. 916 Sink Faucet | 21900500-148CF | N/A
Rm. 916 Sink Faucet | 21900500-149CF | N/A
Rm. 916 Sink Faucet | 21900500-150CF | N/A
Rm. 915 Sink Faucet | 21900500-151CF | N/A
Rm. 915 Sink Faucet | 21900500-152CF | N/A
Rm. 915 Sink Faucet | 21900500-153CF | N/A
Rm. 915 Sink Faucet | 21900500-154CF | N/A
Rm. 915 Sink Faucet | 21900500-155CF | N/A
Rm. 915 Sink Faucet | 21900500-156CF | N/A
Rm. 915 Sink Faucet | 21900500-157CF | N/A
Rm. 915 Sink Faucet | 21900500-158CF | N/A
Rm. 915 Sink Faucet | 21900500-159CF | N/A
Rm. 915 Sink Faucet | 21900500-160CF | N/A
Rm. 915 Storage Sink Faucet | 21900500-161CF | N/A
Rm. 915 Storage Sink Faucet | 21900500-162CF | N/A
Rm. 512 Sink Faucet | 21900500-163CF | N/A
Rm. 512 Drink Fountain | 21900500-164DW | N/A
Rm. 512 Restroom Sink Faucet | 21900500-165BF | 2024-04-15 | ND
Rm. 515 Sink Faucet East | 21900500-166CF | 2024-04-15 | 130.4
Rm. 515 Drink Fountain | 21900500-167DW | 2024-04-15 | 22
Rm. 515 Sink Faucet West | 21900500-168CF | 2024-04-15 | 4.38
RM. 506 Hand wash | 21900500-169CF | N/A
Rm. 506 Drink Fountain | 21900500-170DW | N/A
Rm. 501 Hand Wash | 21900500-171CF | N/A
Rm. 402 Sink Faucet | 21900500-172CF | N/A
Rm. 402 Restroom Sink Faucet | 21900500-173BF | N/A
West Concessions Sink Faucet | 21900500-174KF | 2024-04-15 | ND
Men's Restroom Sink Faucet | 21900500-175BF | N/A
Women's Restroom Sink Faucet | 21900500-176BF | N/A
Men's Restroom Sink Faucet Left | 21900500-177BF | N/A
Men's Restroom Sink Faucet Right | 21900500-178BF | N/A
Women's Restroom Sink Faucet Center | 21900500-179BF | N/A
Women's Restroom Sink Faucet Right | 21900500-180BF | N/A
East Concessions Sink Faucet Left | 21900500-181KF | 2024-04-15 | 4.75
East Concessions Sink Faucet Right | 21900500-182KF | 2024-04-15 | 1.57
Rm. 212 Sink Faucet | 21900500-183CF | N/A
East Concessions Sink Faucet Hand Wash | 21900500-184KF | 2024-04-15 | ND
Rm. 306 Sink Faucet | 21900500-185CF | N/A
Rm. 314 Sink Faucet Band room | 21900500-186CF | N/A
Rm. 212 Sink Faucet | 21900500-187CF | N/A
Rm. 212 Sink Faucet | 21900500-188CF | N/A
Rm. 212 Sink Faucet | 21900500-189CF | N/A
Rm. 212 Sink Faucet | 21900500-190CF | N/A
Girls' Locker Room Coach's Office Sink Faucet | 21900500-191BF | N/A
Rm. 902 Sink Faucet | 21900500-192CF | N/A
Rm. 910 Storage Sink Faucet | 21900500-193CF | N/A
Rm. 910 Storage Sink Faucet | 21900500-194CF | N/A
Rm. 915 Sink Faucet | 21900500-195CF | N/A
Rm. 915 Storage Rm. Sink Faucet | 21900500-196CF | N/A
Rm. 506 Hand Wash | 21900500-197CF | N/A
Rm. 506 Drink Fountain | 21900500-198DW | N/A
Rm. 501 Hand Wash | 21900500-199CF | N/A
Water Bottle Refill Fountain #10 Athletics Hall | 21900500-200WB | 2024-04-15 | ND
CTE Festroom faucet Left South | 21900500-201BF | 2024-04-15 | ND
CTE Festroom faucet Center South | 21900500-202BF | 2024-04-15 | ND
CTE Festroom faucet Right South | 21900500-203BF | 2024-04-15 | ND
CTE Festroom faucet Left North | 21900500-204BF | 2024-04-15 | ND
CTE Festroom faucet Center North | 21900500-205BF | 2024-04-15 | ND
CTE Festroom faucet Right North | 21900500-206BF | 2024-04-15 | ND
CTE Rm 821 South | 21900500-207CF | 2024-04-15 | ND
CTE Rm 821 West Left | 21900500-208CF | 2024-04-15 | ND
CTE Rm 821 West Right | 21900500-209CF | 2024-04-15 | ND
CTE Rm 821 North Left | 21900500-210CF | 2024-04-15 | ND
CTE Rm 821 North Right | 21900500-211CF | 2024-04-15 | ND
CTE Rm 820 South Left | 21900500-212CF | 2024-04-15 | ND
CTE Rm 820 South Right | 21900500-213CF | 2024-04-15 | ND
CTE Rm 820 West left | 21900500-214CF | 2024-04-15 | ND
CTE Rm 820 West Right | 21900500-215CF | 2024-04-15 | ND
CTE Rm 820 North | 21900500-216CF | 2024-04-15 | ND
Drinking Fountain | 21900500-217DW | 2024-04-15 | ND
Drinking Fountain W/WB | 21900500-218DW | 2024-04-15 | ND
Water Bottle Refill | 21900500-219WB | 2024-04-15 | ND
Metal Shop Sink | 21900500-220CF | 2024-04-15 | ND
Wood Shop Sink | 21900500-221CF | 2024-04-15 | ND
Any fixture testing at or above the action level of 15 ppb is immediately removed from service and cannot be returned to service until it has been remediated and passed follow-up testing
RETESTS | Fixture Number | Date | Result
Boys' Locker Room Sink Faucet Left | 21900500-093BF | 2024-05-15 | 7.07
Rm. 515 Sink Faucet East | 21900500-166CF |  | Removed from Service
Rm. 515 Drink Fountain | 21900500-167DW |  | Removed from Service
ND = Non Detect - Lead level is below the set detection limits |  |  | of X ppb