## Slide 1: Fire Prevention and Safety Tips August 17, 2020
Colorado Springs School District 11 Facilities

## Slide 2: Fire Safety, Code, and Regulations Tips Fire inspections are conducted by CSFD Fire Inspectors each year   Dozens of violations are documented across D11   Many of these violations are repeated occurrences   Many of these violations could lead to life threatening circumstances in the event of an actual fire   Principals are subject to court summons and fines, at a minimum, for blatant violations and for repeated occurrences   Director of Facilities is subject to the same consequences for building deficiencies When in doubt, ask for guidance

## Slide 3: Fire Safety and Building Egress Requirements Fire extinguishers Annual training required for all building staff on extinguisher locations, proper use, and maintenance (ELSO guidance to follow)   Should be inspected for serviceability monthly (BMs)   Don’t be afraid to ask how to operate! Could save …… Don’t block cabinets or hangars   Fire code requires 3-ft clear zone to front and sides of all extinguishers Extinguishers and fire blankets must be mounted

## Slide 4: Fire Safety and Building Egress Requirements Emergency Fire Pull Stations Same requirement as the clearance of fire extinguishers   Fire code requires a 3-ft clear zone on front and sides   Must have easy and direct access to all fire pull stations

## Slide 5: Fire Safety and Building Egress Requirements Fire Doors Fire Doors reduce the speed a fire may spread Fire rated doors cannot be altered in any way   i.e. No sanding, painting, drilling, etc   All alterations voids fire rating…replacement is costly   Fire doors must remain closed at all times in non-sprinklered building/area of school*     Exception: rooms/areas with secondary egress
*Automatically controlled door magnets may be installed if controlled by the fire alarm system (reimbursable cost not funded by Facilities Department)

## Slide 6: Fire Safety and Building Egress Requirements Ceiling decorations Hanging of items, decorations, and lights is prohibited Directional signs have been negotiated with CSFD, and approved Hanging of Sneeze Guards subject to review Damaged Ceiling tiles Violates fire rating of ceiling lid meant to slow spread of fire up to 20 minutes- place a work order for support

## Slide 7: Fire Safety and Building Egress Requirements Fire Rated doors Door coverings are prohibited ELSO Supervisor will give 24 hours notice before removing coverings CSFD will cite schools for this violation with little tolerance

## Slide 8: Fire Safety and Building Egress Requirements Excessive Combustibles on walls Maximum wall coverage is 20 percent in hallways, 50 percent in classrooms, and subject to CSFD inspection/judgement on % Tack strips, cork boards, etc. count toward the 50 percent Fabrics, tapestries Must be treated with fire retardant treatment spray Must have appropriate label on accessible corner No more than 10 percent of wall coverage

## Slide 9: Egress Pathway Requirements
Never block or store things near fire doors – a clear path of egress is critical to both occupants and fire teams
Exit Lights (e.g. frog eyes, EXIT lights, and combo lights) must be tested by Building Managers monthly

## Slide 10: Other Fire Safety Notes
Do not permanently use extension cords
Never daisy chained power strips and/or extension cords
                May cause fires due to wires overheating
Concerns: request help on a work order

## Slide 11: Other Fire Safety Notes Electrical, mechanical, and boiler rooms are not storage rooms Storing flammable items in these areas is a fire code violation Violations during CSFD inspections can result in citation on the report, fines and even a court summons Violations must be corrected within 2 weeks unless costly repairs are involved

## Slide 12: Questions? Brian Garcia, Environmental and Life Safety Supervisor Brian.Garcia@D11.org; 477-6021 Mike Willis, Senior Director of Facilities Mike.Willis@d11.org, 477-6013