## Property Information
PROPERTY INFORMATION SUMMARY
Coal City School District No.1
CAMPUS DETAILS
NO. | CAMPUS | FACILITY | ADDRESS | AREA | VISIT DATE | COMMENTS | YEARS BUILT | NO. OF FLOORS | FND TYPE | FRAME CONSTR. | EXT WALLS | ROOF CONSTR. | ROOF COVER | HVAC | PARKING STALLS | ROOF RPRT | DWGS
A | Early Childhood | Early Childhood Center | 755 S. Carbon Hill Rd. Coal City, IL 60416 | 73610 | 2018-09-12 |  | 2007 | 1 | Concrete | Concrete | Brick, Stone | Steel | Slate and Built up Asphalt | Boiler ,Hot Water,A/C | 99 | Y | Y | Gary Voss | O: (630) 406-7360 | KDOT Buildings
B | Elementary School | Elementary School | 300 N. Broadway St. Coal City, IL 60416 | 67976 | 2018-09-13 |  | 1955-1995 | 1 | Concrete | Steel | Brick, Block, Stone | Wood, Steel | Built-up Asphalt | Forced Air & Hot W | 102 | Y | Y |  | C: (630) 816-9706
C | Intermediate School | Intermediate School | 305 E. Division St. Coal City, IL 60416 | 72086 | 2018-09-12 |  | 1916-1989 | 2 | Concrete | Steel | Brick, Block | Steel | Built-up Asphalt | Gas Forced air w/ A/C | 110 | Y | Y
D | Middle School | Middle School | 500 S. Carbon Hill Rd. Coal City, IL 60416 | 98000 | 2018-09-11 |  | 2000 | 1 | Concrete | Wall Bearing | Block, Wd siding | Wood | Asphalt Shingles | None | - | Y | N
E | High School | High School | 655 W. Division St. Coal City, IL 60416 | 209922 | 2018-10-08 |  | 1971-2009 | 1 | Concrete | Wall Bearing | Brick, Block | Wood | Asphalt Shingles | Boiler, Gas, Forced air | 20 | Y | Y
F | High School | Operations & Maintenance Bldg. 1 | 655 W. Division St. Coal City, IL 60416 | 5600 | 2018-10-08 |  | 1976-1996 | 1 | Concrete | Wall Bearing | Masonry, Steel Siding | Wood / Metal | Metal | Hat Water Units | 5 | Y | Y
G | High School | High School Concessions Bldg. | 655 W. Division St. Coal City, IL 60416 | 5744 | 2018-10-08 |  | 2017 | 1 | Stone | Wall Bearing | Wood Siding | Wood | Asphalt Shingles | Hot Water | 15 | Y | Y
H | High School | High School Four Seasons Bldg. | 655 W. Division St. Coal City, IL 60416 | 797 | 2018-10-08 |  | 2013 | 1 | Stone/ Concrete | Concrete | Brick, Stone | Wood | Asphalt Sh, Copper | Low Press Steam |  | N | Y
I | Middle School | Operations & Maintenance Bldg. 2 | 500 S. Carbon Hill Rd. Coal City, IL 60416 | 2400 | 2019-01-16 | 2,862 Total SF. Basement is 400 | 2008 | 1 | Stone/ Concrete | Wall Bearing | Brick, Stone | Wood | Asphalt Sh, Copper | Low Press Steam |  | Y | N
J | Intermediate School | Help for Hope Building | 100 S. Baima St. Coal City, IL 60416 | 2560 | 2018-10-08 |  | 1969-1993 | 1 | Concrete | Wall Bearing | Brick, Block | Wood | Built-up Asphalt | Gas forced air. A/C |  | N | Y
K | Middle School | District Office | 550 S. Carbon Hill Rd. Coal City, IL 60416 | 6576 | Not assessed |  | 2016 | 1 | Concrete | Wall Bearing | Brick | Wood | Asphalt Sh, Built up | Hot Water, A/C |  | Y | N
545271

## Capital Needs
CAPITAL NEEDS SUMMARY
Coal City School District No.1
Facility Name |  | Gross SF | CRV (Current Replacement Value) | 2019 FCI (Facilities Cost Index) | DMB (Deferred Maintenace Backlog) | Capital Needs | [9 empty] | CHECK | COMMENTS
[6 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
A | Early Childhood Center | 73610 | 22083000 | 12.75% | 2815700 | 10500 | 107500 | 473500 | 190500 | 1557200 | 196000 | 73000 | 56000 | 94500 | 57000 | 2815700
B | Elementary School | 67976 | 20392800 | 11.13% | 2270000 | 0 | 358500 | 716500 | 207500 | 201500 | 98500 | 115500 | 86500 | 156500 | 329000 | 2270000
C | Intermediate School | 72086 | 21625800 | 16.96% | 3668000 | 236000 | 568000 | 299500 | 282500 | 146000 | 104000 | 79500 | 317500 | 363000 | 1272000 | 3668000
D | Middle School | 98000 | 29400000 | 9.701% | 2852000 | 55000 | 349500 | 204000 | 101000 | 250500 | 106000 | 96000 | 77500 | 1506000 | 106500 | 2852000
E | High School | 209922 | 73472700 | 4.574% | 3361000 | 163000 | 250000 | 283000 | 317000 | 208000 | 640500 | 166500 | 717000 | 433000 | 183000 | 3361000
F | Operations & Maintenance Bldg. 1 | 5600 | 588000 | 37.33% | 219500 | 0 | 211500 | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 219500
G | High School Concessions Bldg. | 5744 | 861600 | 3.215% | 27700 | 0 | 0 | 0 | 0 | 3000 | 0 | 5000 | 8000 | 5000 | 6700 | 27700
H | High School Four Seasons Bldg. | 797 | 119550 | 33.88% | 40500 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 20000 | 12500 | 0 | 40500
I | Operations & Maintenance Bldg. 2 | 2400 | 360000 | 10% | 36000 | 0 | 16000 | 0 | 0 | 4000 | 5000 | 3000 | 5000 | 0 | 3000 | 36000
J | Help for Hope Building | 2560 | 640000 | 15.99% | 102340 | 0 | 17000 | 53340 | 14000 | 4000 | 3000 | 3000 | 5000 | 0 | 3000 | 102340
TOTALS: |  | 538695 | 169543450 | 15.55% | 15392740 | 464500 | 1878000 | 2029840 | 1120500 | 2374200 | 1153000 | 549500 | 1292500 | 2570500 | 1960200 | 15392740
[7 empty] | 5% | 10% | 15% | 20% | 25% | 30% | 35% | 40% | 45%
[5 empty] | Inflation adjustment |  | 1971900 | 2232824 | 1288575 | 2849040 | 1441250 | 714350 | 1744875 | 3598700 | 2842290
|  | FCI = 0% to 15% |  | GOOD CONDITION
|  | FCI = 15% to 30% |  | FAIR CONDITION
|  | FCI = 30% to 100% |  | POOR CONDITION

## A
EARLY CHILDHOOD CENTER
Facility Condition Assessment
| Building: | Building A |  |  |  | Facility Function:
| Gross SF: | 73610 |  |  |  | Early Childhood Instruction
| Date of Visit | 2018-09-12
| Year Built: | 2007
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations | Concrete |  |  | 100 | possible settlement, not a safety hazzard | monitor yearly, Fix Hardware as Req'd | 0
| Slabs on Grade | Concrete |  |  | 100 | moderate cracking, moderate settlement and heaving throughout building | remove finished flooring, prep, floor leveler and seal cracks | 100000 | Recommended Capital Allocation Year & Amount 2022: 25000; Recommended Capital Allocation Year & Amount 2024: 25000; Recommended Capital Allocation Year & Amount 2026: 25000; Recommended Capital Allocation Year & Amount 2028: 25000
| Superstructure | Steel |  |  | 100 | possible movement, not a safety hazzard | monitor yearly | 0
Exterior Envelope
| Exterior Doors | Aluminum |  |  | 40 | good condition | monitor yearly | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Exterior Doors | Hollow Metal |  |  | 50 | good condition | monitor yearly, Repaint as Req'd | 20000 | Recommended Capital Allocation Year & Amount 2024: 10000; Recommended Capital Allocation Year & Amount 2029: 10000
| Exterior Lintels | Steel |  |  | 80 | good condition, some surface rust | monitor yearly, prep and repaint | 15000 | Recommended Capital Allocation Year & Amount 2021: 5000; Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2028: 5000
| Exterior Door Seals | Rubber |  |  | 15 | light wear | replacement | 10000 | Recommended Capital Allocation Year & Amount 2023: 10000
| Exterior Door Thresholds | Aluminum |  |  | 30 | light wear | replacement | 15000 | Recommended Capital Allocation Year & Amount 2027: 15000
| Exterior Windows | Aluminum Frames |  |  | 40 | glazing seals popping out of place throughout due to settement issues | window replacement with dimensional perimeter adjustment for continous movement | 42000 | Recommended Capital Allocation Year & Amount 2021: 42000
| Exterior Window Glazing | Double Glazed |  |  | 20 | good condition | monitor yearly | 0
| Exterior Walls/Cladding | Brick |  |  | 100 | good condition | monitor yearly | 0
| Exterior Walls/Cladding | Stone Sills |  |  | 100 | some mortar separation | tuckpointing | 22000 | Recommended Capital Allocation Year & Amount 2023: 22000
| Exterior Walls/Cladding | CMU |  |  | 100 | good contition | monitor yearly | 6000 | Recommended Capital Allocation Year & Amount 2024: 3000; Recommended Capital Allocation Year & Amount 2027: 3000
| Caulking at Openings | Silicone, etc. |  |  | 14 | light wear | monitor yearly | 3500 | Recommended Capital Allocation Year & Amount 2028: 3500
| Roofing | Single-Ply |  |  | 20 | good condition, some slight tenting in areas, some existing patching, some aluminum gravel stop separation | monitor quarterly, roof slightly past it's 20 year warranty, small spot repairs as required | 1472200 | Recommended Capital Allocation Year & Amount 2024: 1472200
Interior Construction
| Interior Partitions | CMU |  |  | 100 | moderate cracking, moderate settlement, not a safety hazzard | monitor quarterly, prep, caulk and paint | 67500 |  | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500
| Interior Partitions | Metal Stud |  |  | 100 | good condition | monitor yearly | 0
| Folding Partition | Cafeteria |  |  | 25 | seals at bottom of door panels fail to drop as panels are locked into place, and door binds at times | repair of door panels, or replacement | 45000 | Recommended Capital Allocation Year & Amount 2021: 45000
| Folding Lunch Tables | Cafeteria |  |  | 25 | some lunch tables are non-functioning, binding and delaminating, movable hardware issues | repair or replacement | 35000 | Recommended Capital Allocation Year & Amount 2022: 35000
| Interior Doors | Wood |  |  | 60 | good condition, some binding due to settlement issues | shim hinges, shave edges as required and monitor quarterly | 20000 | Recommended Capital Allocation Year & Amount 2022: 4000; Recommended Capital Allocation Year & Amount 2024: 4000; Recommended Capital Allocation Year & Amount 2026: 4000; Recommended Capital Allocation Year & Amount 2028: 4000; Recommended Capital Allocation Year & Amount 2029: 4000
| Interior Door Hardware | All |  |  | 25 | good condition | monitor yearly | 22500 |  | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
| Interior Storefronts | Aluminum |  |  | 80 | good condition | monitor yearly | 0
| Casework | Plam |  |  | 30 | good condition, some delamination in countertops and backsplashes in areas near sinks | monitory yearly, replace as required | 17500 | Recommended Capital Allocation Year & Amount 2021: 3500; Recommended Capital Allocation Year & Amount 2023: 3500; Recommended Capital Allocation Year & Amount 2025: 3500; Recommended Capital Allocation Year & Amount 2027: 3500; Recommended Capital Allocation Year & Amount 2029: 3500
Interior Finishes
| Floor Finish | Carpet |  |  | 15 | good condition, some seams coming up | monitor yearly | 172000 | Recommended Capital Allocation Year & Amount 2025: 172000
| Floor Finish | Vinyl Comp Tile |  |  | 35 | good condition, areas of cracked VCT due to settlement | replace as required | 16000 | Recommended Capital Allocation Year & Amount 2023: 8000; Recommended Capital Allocation Year & Amount 2026: 8000
| Floor Finish | Ceramic Tile |  |  | 60 | good condition | monitor yearly | 0
| Ceiling Finish | Gypsum Board |  |  | 30 | good condition, some cracking due to settlement | monitor quarterly, repair cracks as required | 20000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2024: 5000; Recommended Capital Allocation Year & Amount 2026: 5000; Recommended Capital Allocation Year & Amount 2028: 5000
| Ceiling Finish | ACT |  |  | 25 | good condition, some evidence of water damage | monitor yearly, replace damaged tiles | 10500 | Recommended Capital Allocation Year & Amount 2022: 3500; Recommended Capital Allocation Year & Amount 2025: 3500; Recommended Capital Allocation Year & Amount 2028: 3500
| Wall Finish | Paint |  |  | 10 | good condition | monitor yearly | 56000 | Recommended Capital Allocation Year & Amount 2022: 14000; Recommended Capital Allocation Year & Amount 2024: 14000; Recommended Capital Allocation Year & Amount 2026: 14000; Recommended Capital Allocation Year & Amount 2028: 14000
Plumbing
| Plumbing Fixtures | Water Closet |  |  | 30 | 37 +/- Count | corrective maintenance | 4500 | Recommended Capital Allocation Year & Amount 2027: 1500; Recommended Capital Allocation Year & Amount 2028: 1500; Recommended Capital Allocation Year & Amount 2029: 1500
| Plumbing Fixtures | Lavatories |  |  | 30 | 69 +/- Count | corrective maintenance | 4500 | Recommended Capital Allocation Year & Amount 2027: 1500; Recommended Capital Allocation Year & Amount 2028: 1500; Recommended Capital Allocation Year & Amount 2029: 1500
| Plumbing Fixtures | Urinals |  |  | 30 | 4 +/- Count | corrective maintenance | 3000 | Recommended Capital Allocation Year & Amount 2027: 1000; Recommended Capital Allocation Year & Amount 2028: 1000; Recommended Capital Allocation Year & Amount 2029: 1000
| Plumbing Fixtures | Flush Valves |  |  | 12 | 41 +/- Count | corrective maintenance | 10000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Faucets |  |  | 10 | 69 +/- Count | corrective maintenance | 10000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Sump Pump |  |  | 10 | Elevator Sump | condition-based maintenance | 3500 | Recommended Capital Allocation Year & Amount 2020: 3500
| Plumbing Fixtures | Drinking Fountain |  |  | 30 | Replace in kind | corrective maintenance | 9000 | Recommended Capital Allocation Year & Amount 2027: 3000; Recommended Capital Allocation Year & Amount 2028: 3000; Recommended Capital Allocation Year & Amount 2029: 3000
| Plumbing Fixtures | Backflow Prevntor |  |  | 6 | Replace in kind | condition-based maintenance | 10000 | Recommended Capital Allocation Year & Amount 2020: 5000; Recommended Capital Allocation Year & Amount 2026: 5000
| Plumbing Fixtures | Water heater |  |  | 10 | Replace in kind | planned maintenance | 10000 | Recommended Capital Allocation Year & Amount 2022: 10000
| Domestic Water Distribution | Piping |  |  | 30 | Repair domestic water leaks | condition-based maintenance | 10000 | Recommended Capital Allocation Year & Amount 2028: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
HVAC
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-1: Replace in kind | planned maintenance | 45000 | Recommended Capital Allocation Year & Amount 2022: 45000
| Packaged Rooftop Unit | Roof - Area A |  |  | 15 | RTU-2: Replace in kind | planned maintenance | 90000 | Recommended Capital Allocation Year & Amount 2022: 90000
| Packaged Rooftop Unit | Roof - Area C |  |  | 15 | RTU-3: Replace in kind | planned maintenance | 90000 | Recommended Capital Allocation Year & Amount 2022: 90000
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-4: Replace in kind | planned maintenance | 10000 | Recommended Capital Allocation Year & Amount 2022: 10000
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-5: Replace in kind | planned maintenance | 55000 | Recommended Capital Allocation Year & Amount 2022: 55000
| Gas piping | Roof |  |  |  | Add gas heat to RTU's above | planned maintenance | 65000 | Recommended Capital Allocation Year & Amount 2022: 65000
| Exhaust Fan | Roof |  |  | 20 | EF-1 TO EF-5 | corrective maintenance | 9000 | Recommended Capital Allocation Year & Amount 2027: 3000; Recommended Capital Allocation Year & Amount 2028: 3000; Recommended Capital Allocation Year & Amount 2029: 3000
| Radon Fan | Roof |  |  | 20 | RF-1 TO RF-3: Replace in kind | corrective maintenance | 3000 | Recommended Capital Allocation Year & Amount 2027: 1000; Recommended Capital Allocation Year & Amount 2028: 1000; Recommended Capital Allocation Year & Amount 2029: 1000
| Unit Heater | B-118 |  |  | 20 | HT-1 | corrective maintenance | 6000 | Recommended Capital Allocation Year & Amount 2027: 2000; Recommended Capital Allocation Year & Amount 2028: 2000; Recommended Capital Allocation Year & Amount 2029: 2000
| Wall Cabinet Heater | Vestibules |  |  | 20 | HT-2 | corrective maintenance | 6000 | Recommended Capital Allocation Year & Amount 2027: 2000; Recommended Capital Allocation Year & Amount 2028: 2000; Recommended Capital Allocation Year & Amount 2029: 2000
| Hydronic Heating System | Piping |  |  | 30 | Repair hydronic water leaks | condition-based maintenance | 7500 | Recommended Capital Allocation Year & Amount 2027: 2500; Recommended Capital Allocation Year & Amount 2028: 2500; Recommended Capital Allocation Year & Amount 2029: 2500
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
Kitchen / Commercial Equipment
Fixed Furnishings
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 135000 | Recommended Capital Allocation Year & Amount 2023: 135000
| Pedestrian Paving | Concrete |  |  | 40 | good condition | monitor yearly | 0
| Drainage | [6 empty] | 10000 | Recommended Capital Allocation Year & Amount 2025: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
| Landscaping | [6 empty] | 10000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2027: 5000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 2815700 | 10500 | 107500 | 473500 | 190500 | 1557200 | 196000 | 73000 | 56000 | 94500 | 57000
List of items recommended to be addressed in the near future:
1. Repair concrete slab settlement
2. Repair or replace folding partition in Gymnasium
3. Seal exterior masonry (only if recommended, may trap moisuture in wall cavities further investigation required)
4. Replace window seals
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## B
ELEMENTARY SCHOOL
Facility Condition Assessment
| Building: | Building B |  |  |  | Facility Function:
| Gross SF: | 67976 |  |  |  | Elementary School Instruction
| Date of Visit | 2018-09-13
| Year Built: | 1955-1995
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations | Concrete |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade | Concrete |  |  | 100 | moderate cracking, moderate settlement and heaving in adminstration area | remove finished flooring, prep, mudjack and seal cracks | 38000 | Recommended Capital Allocation Year & Amount 2026: 38000
| Superstructure | Load bearing CMU |  |  | 100 | good condition | monitor yearly | 33000 | Recommended Capital Allocation Year & Amount 2023: 15000; Recommended Capital Allocation Year & Amount 2027: 18000
Exterior Envelope
| Exterior Doors | Aluminum |  |  | 40 | good condition | monitor yearly | 28500 | Recommended Capital Allocation Year & Amount 2021: 6000; Recommended Capital Allocation Year & Amount 2024: 7500; Recommended Capital Allocation Year & Amount 2025: 7500; Recommended Capital Allocation Year & Amount 2026: 7500
| Exterior Doors | Hollow Metal |  |  | 50 | good condition | monitor yearly | 40000 | Recommended Capital Allocation Year & Amount 2022: 8000; Recommended Capital Allocation Year & Amount 2023: 8000; Recommended Capital Allocation Year & Amount 2027: 8000; Recommended Capital Allocation Year & Amount 2028: 8000; Recommended Capital Allocation Year & Amount 2029: 8000
| Exterior Lintels | Steel |  |  | 80 | good condition, some surface rust | monitor yearly, prep and repaint | 20000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2024: 5000; Recommended Capital Allocation Year & Amount 2026: 5000; Recommended Capital Allocation Year & Amount 2028: 5000
| Exterior Door Seals | Rubber |  |  | 15 | moderate wear | replacement | 25000 | Recommended Capital Allocation Year & Amount 2021: 25000
| Exterior Door Thresholds | Aluminum |  |  | 30 | moderate wear | replacement | 25000 | Recommended Capital Allocation Year & Amount 2021: 25000
| Exterior Windows | Aluminum Frames |  |  | 40 | moderate to end-of-service life wear | monitor yearly, replace as required | 235000 | Recommended Capital Allocation Year & Amount 2022: 235000
| Exterior Windows | Steel Frames |  |  | 40 | end-of-service life wear | replacement | 150000 | Recommended Capital Allocation Year & Amount 2022: 150000
| Exterior Window Glazing | Double Glazed |  |  | 20 | good condition to end-of-service life wear | monitor yearly, replace as required | 50000 | Recommended Capital Allocation Year & Amount 2022: 50000
| Exterior Window Glazing | Single Glazed |  |  | 20 | end-of-service life wear | replacement | 50000 | Recommended Capital Allocation Year & Amount 2022: 50000
| Exterior Walls/Cladding | Brick |  |  | 100 | some mortar separation and deterioration | tuckpointing | 100000 | Recommended Capital Allocation Year & Amount 2023: 50000; Recommended Capital Allocation Year & Amount 2028: 50000
| Exterior Walls/Cladding | Stone Sills |  |  | 100 | some mortar separation | tuckpointing | 25000 | Recommended Capital Allocation Year & Amount 2023: 25000
| Caulking at Openings | Silicone, etc. |  |  | 14 | moderate to end-of-service life wear | monitor yearly, replace as required | 30000 | Recommended Capital Allocation Year & Amount 2022: 15000; Recommended Capital Allocation Year & Amount 2026: 15000
| Roofing | Single-Ply / Ballasted |  |  | 25 | good condition, some seam separation in areas, some existing patching, some aluminum gravel stop separation, some missing flashing, ponding in some areas | monitor quarterly, small spot repairs as required | 245000 | Recommended Capital Allocation Year & Amount 2021: 10000; Recommended Capital Allocation Year & Amount 2023: 10000; Recommended Capital Allocation Year & Amount 2029: 225000
| Roofing | Gutters & Downspouts, soffit fascia |  |  | 25 | good condition, some localized damage | monitor yearly, replace as required | 58000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2024: 5000; Recommended Capital Allocation Year & Amount 2029: 48000
Interior Construction
| Interior Partitions | CMU |  |  | 100 | good condition, moderate wear | monitor yearly | 36000 | Recommended Capital Allocation Year & Amount 2022: 12000; Recommended Capital Allocation Year & Amount 2025: 12000; Recommended Capital Allocation Year & Amount 2028: 12000
| Interior Partitions | Metal Stud |  |  | 100 | good condition | monitor yearly | 32000 | Recommended Capital Allocation Year & Amount 2022: 8000; Recommended Capital Allocation Year & Amount 2024: 8000; Recommended Capital Allocation Year & Amount 2026: 8000; Recommended Capital Allocation Year & Amount 2028: 8000
| Interior Doors | Wood |  |  | 60 | good condition, some moderate wear | monitor yearly | 25000 | Recommended Capital Allocation Year & Amount 2021: 5000; Recommended Capital Allocation Year & Amount 2023: 5000; Recommended Capital Allocation Year & Amount 2025: 5000; Recommended Capital Allocation Year & Amount 2027: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
| Interior Door Hardware | All |  |  | 25 | good condition, some moderate wear | monitor yearly | 38000 | Recommended Capital Allocation Year & Amount 2023: 10000; Recommended Capital Allocation Year & Amount 2026: 18000; Recommended Capital Allocation Year & Amount 2029: 10000
| Casework | Plam |  |  | 30 | good condition, some delamination in countertops | monitory yearly, replace as required | 66000 | Recommended Capital Allocation Year & Amount 2021: 20000; Recommended Capital Allocation Year & Amount 2024: 28000; Recommended Capital Allocation Year & Amount 2027: 18000
| Casework | Solid Surface |  |  | 30 | good conditioin | monitor yearly | 32000 | Recommended Capital Allocation Year & Amount 2022: 16000; Recommended Capital Allocation Year & Amount 2025: 16000
Interior Finishes
| Floor Finish | Carpet |  |  | 15 | good condition | monitor yearly | 70000 | Recommended Capital Allocation Year & Amount 2023: 70000
| Floor Finish | Vinyl Comp Tile |  |  | 35 | good condition, some moderate wear | replace as required | 32000 | Recommended Capital Allocation Year & Amount 2021: 8000; Recommended Capital Allocation Year & Amount 2022: 8000; Recommended Capital Allocation Year & Amount 2026: 8000; Recommended Capital Allocation Year & Amount 2027: 8000
| Floor Finish | Ceramic Tile |  |  | 60 | good condition, some moderate wear | monitor yearly | 24000 | Recommended Capital Allocation Year & Amount 2024: 12000; Recommended Capital Allocation Year & Amount 2029: 12000
| Floor Finish | Terrazzo |  |  | 100 | good condition, some moderate wear | monitor yearly | 25500 | Recommended Capital Allocation Year & Amount 2022: 8500; Recommended Capital Allocation Year & Amount 2025: 8500; Recommended Capital Allocation Year & Amount 2028: 8500
| Wall Finish | Paint |  |  | 10 | good condition | monitor yearly | 45000 |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
Plumbing
| Plumbing Fixtures | Water Closet |  |  | 30 | 27 +/- Count, moderate-to-end of service life wear | corrective maintenance | 13500 |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
| Plumbing Fixtures | Lavatories |  |  | 30 | 31 +/- Count, moderate-to-end of service life wear | corrective maintenance | 13500 |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
| Plumbing Fixtures | Urinals |  |  | 30 | 16 +/- Count, moderate-to-end of service life wear | corrective maintenance | 9000 |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Flush Valves |  |  | 12 | 43 +/- Count, moderate-to-end of service life wear | corrective maintenance | 9000 |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Faucets |  |  | 10 | 31 +/- Count, moderate-to-end of service life wear | corrective maintenance | 9000 |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Sump Pump |  |  | 10 | Elevator Sump | condition-based maintenance | 3500 | Recommended Capital Allocation Year & Amount 2024: 3500
| Plumbing Fixtures | Drinking Fountain |  |  | 30 | Replace in kind | corrective maintenance | 14000 | Recommended Capital Allocation Year & Amount 2021: 3500; Recommended Capital Allocation Year & Amount 2023: 3500; Recommended Capital Allocation Year & Amount 2025: 3500; Recommended Capital Allocation Year & Amount 2027: 3500
| Plumbing Fixtures | Backflow Prevntor |  |  | 6 | Replace in kind | condition-based maintenance | 10000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
| Plumbing Fixtures | Water heater |  |  | 10 | Replace in kind | planned maintenance | 10000 | Recommended Capital Allocation Year & Amount 2027: 10000
| Domestic Water Distribution | Piping / Valves |  |  | 60 | original 1955 building piping walls are very thin, valves have seized, and are at the end of their useful service life | condition-based maintenance | 125000 | Recommended Capital Allocation Year & Amount 2021: 125000
HVAC
| Packaged Rooftop Unit | Roof - Area J |  |  | 15 | RTU-702: Replace in kind | planned maintenance | 7500 | Recommended Capital Allocation Year & Amount 2021: 7500
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-707: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-723: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-720: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-768: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-1: Replace in kind | planned maintenance | 7500 | Recommended Capital Allocation Year & Amount 2021: 7500
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-718: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-719: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-716: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area H |  |  | 15 | RTU-717: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area G |  |  | 15 | RTU-721: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2024: 8500
| Packaged Rooftop Unit | Roof - Area G |  |  | 15 | RTU-7: Replace in kind | planned maintenance | 12000 | Recommended Capital Allocation Year & Amount 2024: 12000
| Packaged Rooftop Unit | Roof - Area G |  |  | 15 | RTU-2: Replace in kind | planned maintenance | 20000 | Recommended Capital Allocation Year & Amount 2021: 20000
| Packaged Rooftop Unit | Roof - Area D |  |  | 15 | RTU-769: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2021: 15000
| Packaged Rooftop Unit | Roof - Area D |  |  | 15 | RTU-770: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2021: 15000
| Unit Ventilator | Third Grade |  |  | 25 | Replace in kind | planned maintenance | 125000 | Recommended Capital Allocation Year & Amount 2022: 125000
| CONDENSING UNIT | Roof - Area F |  |  | 20 | CU-8: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 4000 | Recommended Capital Allocation Year & Amount 2028: 4000
| CONDENSING UNIT | Roof - Area F |  |  | 20 | CU-9: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 5000 | Recommended Capital Allocation Year & Amount 2028: 5000
| SPLIT SYSTEM AC UNIT | A-120 |  |  | 20 | AC-1: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 4000 | Recommended Capital Allocation Year & Amount 2021: 4000
| SPLIT SYSTEM AC UNIT | A-119 |  |  | 20 | AC-2: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 4000 | Recommended Capital Allocation Year & Amount 2021: 4000
| SPLIT SYSTEM AC UNIT | A-118 |  |  | 20 | AC-3: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 4000 | Recommended Capital Allocation Year & Amount 2021: 4000
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures | condition-based maint. | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maint. | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
| Kitchen / Commercial Equipment | [6 empty] | 0
Site
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 25000 | Recommended Capital Allocation Year & Amount 2021: 15000; Recommended Capital Allocation Year & Amount 2024: 5000; Recommended Capital Allocation Year & Amount 2027: 5000
| Parking Lot / Drives | Asphalt |  |  | 20 | good condition | monitor yearly | 108000 | Recommended Capital Allocation Year & Amount 2021: 28000; Recommended Capital Allocation Year & Amount 2025: 35000; Recommended Capital Allocation Year & Amount 2028: 45000
| Drainage | [6 empty] | 0
| Landscaping | [6 empty] | 15000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2026: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 2270000 | 0 | 358500 | 716500 | 207500 | 201500 | 98500 | 115500 | 86500 | 156500 | 329000
List of items recommended to be addressed in the near future:
1. Tuckpoint exterior masonry walls
2. Repair or replace HVAC unit / system in Third Grade area
3. Repair or replace plumbing pipes / fixtures
4. Replace windows in Third Grade area
5. Repair slab settlement in Main Office area
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## C
INTERMEDIATE SCHOOL
Facility Condition Assessment
| Building: | Building C |  |  |  | Facility Function:
| Gross SF: | 72086 |  |  |  | Intermediate School Instruction
| Date of Visit | 2018-09-12
| Year Built: | 1916-1989
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations | Concrete / CMU |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade | Concrete |  |  | 100 | good condition, slight cracking, slight settlement | remove finished flooring, prep, mudjack and seal cracks | 15000 | Recommended Capital Allocation Year & Amount 2023: 15000
| Superstructure | Load bearing CMU |  |  | 100 | good condition | monitor yearly | 250000 | Recommended Capital Allocation Year & Amount 2027: 250000
Exterior Envelope
| Exterior Doors | Aluminum |  |  | 40 | moderate wear | monitor yearly | 30000 | Recommended Capital Allocation Year & Amount 2020: 6000; Recommended Capital Allocation Year & Amount 2022: 6000; Recommended Capital Allocation Year & Amount 2024: 6000; Recommended Capital Allocation Year & Amount 2026: 6000; Recommended Capital Allocation Year & Amount 2028: 6000
| Exterior Doors | Hollow Metal |  |  | 50 | moderate wear | monitor yearly | 40000 | Recommended Capital Allocation Year & Amount 2021: 8000; Recommended Capital Allocation Year & Amount 2023: 8000; Recommended Capital Allocation Year & Amount 2025: 8000; Recommended Capital Allocation Year & Amount 2027: 8000; Recommended Capital Allocation Year & Amount 2029: 8000
| Exterior Lintels | Steel |  |  | 80 | good condition, some surface rust | monitor yearly, prep and repaint | 30000 | Recommended Capital Allocation Year & Amount 2022: 15000; Recommended Capital Allocation Year & Amount 2026: 15000
| Exterior Door Seals | Rubber |  |  | 15 | moderate wear | replacement | 14000 | Recommended Capital Allocation Year & Amount 2021: 14000
| Exterior Door Thresholds | Aluminum |  |  | 30 | moderate wear | replacement | 24000 | Recommended Capital Allocation Year & Amount 2020: 24000
| Exterior Windows | Aluminum Frames |  |  | 40 | end-of-service life wear | replacement | 238000 | Recommended Capital Allocation Year & Amount 2021: 238000
| Exterior Windows | Steel Frames |  |  | 40 | end-of-service life wear | replacement | 85000 | Recommended Capital Allocation Year & Amount 2021: 85000
| Exterior Window Glazing | Double Glazed |  |  | 20 | end-of-service life wear | replacement | 45000 | Recommended Capital Allocation Year & Amount 2021: 45000
| Exterior Window Glazing | Single Glazed |  |  | 20 | end-of-service life wear | replacement | 76000 | Recommended Capital Allocation Year & Amount 2021: 76000
| Exterior Walls/Cladding | Brick |  |  | 100 | some mortar separation and deterioration | tuckpointing | 105000 | Recommended Capital Allocation Year & Amount 2022: 35000; Recommended Capital Allocation Year & Amount 2025: 35000; Recommended Capital Allocation Year & Amount 2028: 35000
| Exterior Walls/Cladding | Stone Sills |  |  | 100 | some mortar separation | tuckpointing | 30000 | Recommended Capital Allocation Year & Amount 2022: 10000; Recommended Capital Allocation Year & Amount 2025: 10000; Recommended Capital Allocation Year & Amount 2028: 10000
| Caulking at Openings | Silicone, etc. |  |  | 14 | end-of-service life wear | replacement | 84000 | Recommended Capital Allocation Year & Amount 2020: 28000; Recommended Capital Allocation Year & Amount 2024: 28000; Recommended Capital Allocation Year & Amount 2028: 28000
| Roofing | Built-up / Ballasted |  |  | 25 | good condition, some seam separation in areas, some existing patching, some aluminum gravel stop separation, some missing flashing, ponding in some areas | monitor quarterly, small spot repairs as required | 1220000 | Recommended Capital Allocation Year & Amount 2020: 5000; Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2024: 5000; Recommended Capital Allocation Year & Amount 2026: 5000; Recommended Capital Allocation Year & Amount 2029: 1200000
| Roofing | Gutters & Downspouts, soffit fascia |  |  | 25 | good condition, some localized damage | monitor yearly, replace as required | 30000 | Recommended Capital Allocation Year & Amount 2021: 7500; Recommended Capital Allocation Year & Amount 2023: 7500; Recommended Capital Allocation Year & Amount 2025: 7500; Recommended Capital Allocation Year & Amount 2027: 7500
Interior Construction
| Interior Partitions | CMU / Glazed CMU |  |  | 100 | good condition, moderate wear | monitor yearly | 15000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2026: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
| Interior Partitions | Metal Stud |  |  | 100 | good condition | monitor yearly | 45000 | Recommended Capital Allocation Year & Amount 2021: 15000; Recommended Capital Allocation Year & Amount 2024: 15000; Recommended Capital Allocation Year & Amount 2027: 15000
| Interior Partitions | Wood Stud |  |  | 40 | good condition | monitor yearly | 20000 | Recommended Capital Allocation Year & Amount 2020: 10000; Recommended Capital Allocation Year & Amount 2025: 10000
| Interior Doors | Wood |  |  | 60 | good condition, some moderate wear | monitor yearly | 36000 | Recommended Capital Allocation Year & Amount 2022: 12000; Recommended Capital Allocation Year & Amount 2026: 12000; Recommended Capital Allocation Year & Amount 2029: 12000
| Interior Door Hardware | All |  |  | 25 | good condition, some moderate wear | monitor yearly | 40000 | Recommended Capital Allocation Year & Amount 2020: 10000; Recommended Capital Allocation Year & Amount 2021: 10000; Recommended Capital Allocation Year & Amount 2024: 10000; Recommended Capital Allocation Year & Amount 2027: 10000
| Casework | Plam / Wood |  |  | 30 | good condition, some delamination in countertops | monitory yearly, replace as required | 45000 | Recommended Capital Allocation Year & Amount 2023: 45000
| Casework | Solid Surface |  |  | 30 | good conditioin | monitor yearly | 35000 | Recommended Capital Allocation Year & Amount 2023: 35000
Interior Finishes
| Floor Finish | Carpet |  |  | 15 | moderate wear to end-of-service life | replace | 175000 | Recommended Capital Allocation Year & Amount 2022: 175000
| Floor Finish | Vinyl Comp Tile |  |  | 35 | moderate wear to end-of-service life | replace | 160000 | Recommended Capital Allocation Year & Amount 2020: 10000; Recommended Capital Allocation Year & Amount 2023: 150000
| Floor Finish | Ceramic Tile |  |  | 60 | good condition, some moderate wear | monitor yearly | 30000 | Recommended Capital Allocation Year & Amount 2021: 10000; Recommended Capital Allocation Year & Amount 2026: 10000; Recommended Capital Allocation Year & Amount 2029: 10000
| Floor Finish | Terrazzo |  |  | 100 | good condition, some moderate wear | monitor yearly | 45000 | Recommended Capital Allocation Year & Amount 2020: 35000; Recommended Capital Allocation Year & Amount 2024: 10000
| Floor Finish | Athletic Wood |  |  | 50 | good condition | monitor yearly | 0
| Ceiling Finish | ACT |  |  | 25 | moderate wear to end-of-service life | replace as required | 30000 | Recommended Capital Allocation Year & Amount 2022: 10000; Recommended Capital Allocation Year & Amount 2025: 10000; Recommended Capital Allocation Year & Amount 2028: 10000
| Wall Finish (S. Gym) | Paint |  |  | 10 | moderate wear | monitor yearly | 80000 | Recommended Capital Allocation Year & Amount 2020: 80000
| Wall Finish | Paint |  |  | 10 | moderate wear | monitor yearly | 81500 | 5000 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500
Plumbing
| Plumbing Fixtures | Water Closet |  |  | 30 | 26 +/- Count, moderate-to-end of service life wear | corrective maintenance | 15000 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
| Plumbing Fixtures | Lavatories |  |  | 30 | 22 +/- Count, moderate-to-end of service life wear | corrective maintenance | 15000 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
| Plumbing Fixtures | Urinals |  |  | 30 | 13 +/- Count, moderate-to-end of service life wear | corrective maintenance | 10000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Flush Valves |  |  | 12 | 39 +/- Count, moderate-to-end of service life wear | corrective maintenance | 10000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Faucets |  |  | 10 | 22 +/- Count, moderate-to-end of service life wear | corrective maintenance | 10000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Sump Pump |  |  | 10 | Elevator Sump | condition-based maintenance | 3500 | Recommended Capital Allocation Year & Amount 2023: 3500
| Plumbing Fixtures | Drinking Fountain |  |  | 30 | Replace in kind | corrective maintenance | 14000 | Recommended Capital Allocation Year & Amount 2021: 3500; Recommended Capital Allocation Year & Amount 2024: 3500; Recommended Capital Allocation Year & Amount 2027: 3500; Recommended Capital Allocation Year & Amount 2029: 3500
| Plumbing Fixtures | Backflow Prevntor |  |  | 6 | Replace in kind | condition-based maintenance | 10000 | Recommended Capital Allocation Year & Amount 2020: 5000; Recommended Capital Allocation Year & Amount 2027: 5000
| Plumbing Fixtures | Water heater |  |  | 10 | Replace in kind | planned maintenance | 10000 | Recommended Capital Allocation Year & Amount 2020: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
| Domestic Water Distribution | Piping |  |  | 30 | Repair domestic water leaks | condition-based maintenance | 20000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
| Plumbing | Kitchen Drains |  |  | 60 | underfloor plumbing / drains in the kitchen are at the end of their useful service life | condition-based maintenance | 30000 | Recommended Capital Allocation Year & Amount 2021: 30000
| Plumbing | Locker Room Drains |  |  | 60 | underfloor plumbing / drains in the locker room are at the end of their useful service life | condition-based maintenance | 7500 | Recommended Capital Allocation Year & Amount 2021: 7500
HVAC
| Exhaust Fan | Roof |  |  | 20 | EF-1 TO EF-7 | corrective maintenance | 10000 | Recommended Capital Allocation Year & Amount 2021: 2000; Recommended Capital Allocation Year & Amount 2023: 2000; Recommended Capital Allocation Year & Amount 2025: 2000; Recommended Capital Allocation Year & Amount 2027: 2000; Recommended Capital Allocation Year & Amount 2029: 2000
| Packaged Rooftop Unit | Roof - Area A |  |  | 15 | RTU-782: Replace in kind | planned maintenance | 13000 | Recommended Capital Allocation Year & Amount 2024: 13000
| Packaged Rooftop Unit | Roof - Area A |  |  | 15 | RTU-783: Replace in kind | planned maintenance | 13000 | Recommended Capital Allocation Year & Amount 2024: 13000
| Packaged Rooftop Unit | Roof - Area A |  |  | 15 | RTU-3: Replace in kind | planned maintenance | 55000 | Recommended Capital Allocation Year & Amount 2028: 55000
| Packaged Rooftop Unit | Roof - Area A |  |  | 15 | RTU-4: Replace in kind | planned maintenance | 55000 | Recommended Capital Allocation Year & Amount 2028: 55000
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-5: Replace in kind | planned maintenance | 55000 | Recommended Capital Allocation Year & Amount 2028: 55000
| Packaged Rooftop Unit | Roof - Area E |  |  | 15 | RTU-798: Replace in kind | planned maintenance | 13000 | Recommended Capital Allocation Year & Amount 2024: 13000
| Packaged Rooftop Unit | Roof - Area F |  |  | 15 | RTU-788: Replace in kind | planned maintenance | 13000 | Recommended Capital Allocation Year & Amount 2024: 13000
| Packaged Rooftop Unit | Roof - Area G |  |  | 15 | RTU-2: Replace in kind | planned maintenance | 55000 | Recommended Capital Allocation Year & Amount 2028: 55000
| Packaged Rooftop Unit | Roof - Area M |  |  | 15 | RTU-6: Replace in kind | planned maintenance | 17500 | Recommended Capital Allocation Year & Amount 2028: 17500
| Packaged Rooftop Unit | Roof - Area I |  |  | 15 | RTU-1: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2028: 15000
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
| Kitchen / Commercial Equipment | [6 empty] | 0
| Fixed Furnishings | [6 empty] | 0
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 30000 | Recommended Capital Allocation Year & Amount 2022: 10000; Recommended Capital Allocation Year & Amount 2026: 10000; Recommended Capital Allocation Year & Amount 2029: 10000
| Pedestrian Paving | Concrete |  |  | 40 | good condition | monitor yearly | 0
| Drainage | [6 empty] | 0
| Landscaping | [6 empty] | 15000 | Recommended Capital Allocation Year & Amount 2020: 5000; Recommended Capital Allocation Year & Amount 2025: 5000; Recommended Capital Allocation Year & Amount 2028: 5000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 3668000 | 236000 | 568000 | 299500 | 282500 | 146000 | 104000 | 79500 | 317500 | 363000 | 1272000
List of items recommended to be addressed in the near future:
1. Tuckpoint exterior masonry walls
2. Replace windows
3. Replace / repair Kitchen floor drains
4. Replace / repair Lockeroom plumbing due to storm water back-ups
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## D
MIDDLE SCHOOL
Facility Condition Assessment
| Building: | Building D |  |  |  | Facility Function:
| Gross SF: | 98000 |  |  |  | Middle school instruction
| Date of Visit | 2018-09-11
| Year Built: | 2000
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations | Concrete |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade |  |  |  | 100 | good condition, slight cracking, some underground piping heaving / telegraphing in cafeteria | remove finished flooring, cut localized concrete damage, re-install pipe, replace flooring | 75000 | Recommended Capital Allocation Year & Amount 2022: 75000
| Superstructure | Load bearing CMU, Steel, Wood Glulam beams |  |  | 100 | good condition | monitor yearly | 38000 | Recommended Capital Allocation Year & Amount 2020: 8000; Recommended Capital Allocation Year & Amount 2023: 10000; Recommended Capital Allocation Year & Amount 2026: 10000; Recommended Capital Allocation Year & Amount 2029: 10000
Exterior Envelope
| Exterior Doors | Aluminum |  |  | 40 | good condition | monitor yearly | 22500 | Recommended Capital Allocation Year & Amount 2024: 7500; Recommended Capital Allocation Year & Amount 2027: 7500; Recommended Capital Allocation Year & Amount 2029: 7500
| Exterior Doors | Hollow Metal |  |  | 50 | good condition | monitor yearly | 24000 | Recommended Capital Allocation Year & Amount 2022: 8000; Recommended Capital Allocation Year & Amount 2025: 8000; Recommended Capital Allocation Year & Amount 2028: 8000
| Exterior Lintels | Steel |  |  | 80 | good condition, some surface rust | monitor yearly, prep and repaint | 34000 | Recommended Capital Allocation Year & Amount 2020: 10000; Recommended Capital Allocation Year & Amount 2023: 12000; Recommended Capital Allocation Year & Amount 2029: 12000
| Exterior Door Seals | Rubber |  |  | 15 | moderate wear | replacement | 28000 | Recommended Capital Allocation Year & Amount 2021: 14000; Recommended Capital Allocation Year & Amount 2025: 14000
| Exterior Door Thresholds | Aluminum |  |  | 30 | moderate wear | replacement | 36000 | Recommended Capital Allocation Year & Amount 2024: 18000; Recommended Capital Allocation Year & Amount 2027: 18000
| Exterior Windows | Aluminum Frames |  |  | 40 | moderate wear, some caulking failing, some seals deteriorating | remove old caulk and re-caulk, replace localized damaged seals | 35000 | Recommended Capital Allocation Year & Amount 2022: 35000
| Exterior Window Glazing | Double Glazed |  |  | 20 | good condition | monitory yearly | 0
| Exterior Walls/Cladding | CMU |  |  | 100 | mortar separation, some cracked pieces | tuckpoint, replace broken CMU | 38000 | Recommended Capital Allocation Year & Amount 2020: 8000; Recommended Capital Allocation Year & Amount 2025: 15000; Recommended Capital Allocation Year & Amount 2029: 15000
| Exterior Walls/Cladding | CMU Sills |  |  | 100 | mortar separation | CMU sills, tuckpoint | 16000 | Recommended Capital Allocation Year & Amount 2025: 8000; Recommended Capital Allocation Year & Amount 2029: 8000
| Caulking at Openings | Silicone, etc. |  |  | 14 | near end-of-service life wear | replacement | 35000 | Recommended Capital Allocation Year & Amount 2023: 35000
| Entrance Steel | Main Entrance |  |  | 50 | Steel at main entrance "mine shaft" | prepare and repaint | 15000 | Recommended Capital Allocation Year & Amount 2026: 15000
| Roofing | Built-up / Ballasted |  |  | 25 | End of service life wear, delamination, tenting, extensive patching, some seam separation in areas, missing ballast, etc. | replacement | 1460000 | Recommended Capital Allocation Year & Amount 2028: 1460000
| Roofing | Standing-Seam Metal |  |  | 35 | Moderate wear, small localized damage, missing / unattached snow guards | repair damaged panels (cosmetic), replace / anchor snow guards | 20000 | Recommended Capital Allocation Year & Amount 2024: 10000; Recommended Capital Allocation Year & Amount 2027: 10000
| Roofing | Gutters & Downspouts, soffit fascia |  |  | 25 | good condition, some localized damage | monitor yearly, replace as required | 20000 | Recommended Capital Allocation Year & Amount 2022: 10000; Recommended Capital Allocation Year & Amount 2026: 10000
Interior Construction
| Interior Partitions | CMU |  |  | 100 | good condition, moderate wear, some localized cracks | monitor yearly, infill cracks, replace cracked CMU | 32000 | Recommended Capital Allocation Year & Amount 2020: 8000; Recommended Capital Allocation Year & Amount 2023: 8000; Recommended Capital Allocation Year & Amount 2026: 8000; Recommended Capital Allocation Year & Amount 2029: 8000
| Interior Partitions | Metal Stud |  |  | 100 | good condition, small localized damage | monitor yearly, repair | 22500 | Recommended Capital Allocation Year & Amount 2021: 7500; Recommended Capital Allocation Year & Amount 2024: 7500; Recommended Capital Allocation Year & Amount 2027: 7500
| Interior Doors | Wood |  |  | 60 | good condition | monitor yearly | 0
| Interior Door Hardware | All |  |  | 25 | good condition, some moderate wear | monitor yearly | 20000 | Recommended Capital Allocation Year & Amount 2022: 10000; Recommended Capital Allocation Year & Amount 2027: 10000
| Casework | Plam / Wood |  |  | 30 | good condition | monitory yearly | 0
Interior Finishes
| Floor Finish | Carpet |  |  | 15 | good condition, some staining | monitor yearly | 45000 | Recommended Capital Allocation Year & Amount 2023: 15000; Recommended Capital Allocation Year & Amount 2026: 15000; Recommended Capital Allocation Year & Amount 2029: 15000
| Floor Finish | Vinyl Comp Tile |  |  | 35 | good conditioin, some cracking | monitory yearly, replace as required | 36000 | Recommended Capital Allocation Year & Amount 2024: 12000; Recommended Capital Allocation Year & Amount 2026: 12000; Recommended Capital Allocation Year & Amount 2028: 12000
| Floor Finish | Ceramic Tile |  |  | 60 | good condition, some moderate wear | monitor yearly | 0
| Floor Finish | Athletic Wood |  |  | 50 | good condition | monitor yearly | 0
| Ceiling Finish | ACT |  |  | 25 | moderate wear to end-of-service life | replace as required | 35000 | Recommended Capital Allocation Year & Amount 2022: 35000
| Wall Finish | Paint |  |  | 10 | good condition | monitor yearly | 100000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000
Plumbing
| Plumbing Fixtures | Water Closet |  |  | 30 | 42 +/- Count, moderate wear | replace as required | 20000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
| Plumbing Fixtures | Lavatories |  |  | 30 | 118 +/- Count, moderate wear | replace as required | 35000 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
| Plumbing Fixtures | Urinals |  |  | 30 | 15 +/- Count, moderate wear | replace as required | 15000 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
| Plumbing Fixtures | Flush Valves |  |  | 12 | 57 +/- Count, moderate wear | replace as required | 10000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Faucets |  |  | 10 | 118 +/- Count, moderate wear | corrective maintenance | 25000 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
| Plumbing Fixtures | Sump Pump |  |  | 10 | Elevator Sump | condition-based maintenance | 3500 | Recommended Capital Allocation Year & Amount 2021: 3500
| Plumbing Fixtures | Drinking Fountain |  |  | 30 | Replace in kind | corrective maintenance | 10500 | Recommended Capital Allocation Year & Amount 2021: 3500; Recommended Capital Allocation Year & Amount 2024: 3500; Recommended Capital Allocation Year & Amount 2027: 3500
| Plumbing Fixtures | Backflow Prevntor |  |  | 6 | Replace in kind | condition-based maintenance | 10000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
| Plumbing Fixtures | Water heater |  |  | 10 | Replace in kind | planned maintenance | 40000 | Recommended Capital Allocation Year & Amount 2025: 40000
| Domestic Water Distribution | Piping |  |  | 30 | Repair domestic water leaks | condition-based maintenance | 5000 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
HVAC
| Chiller | Grade - East B |  |  | 20 | CH-1: Replace in kind | planned maintenance | 300000 | Recommended Capital Allocation Year & Amount 2021: 300000
| Air Handling Unit | Mechanical 401 |  |  | 25 | AHU-6: Replace in kind | planned maintenance | 17000 | Recommended Capital Allocation Year & Amount 2024: 17000
| Air Handling Unit | Mechanical 401 |  |  | 25 | AHU-5B: Replace in kind | planned maintenance | 1500 | Recommended Capital Allocation Year & Amount 2024: 1500
| Air Handling Unit | Mechanical 400 |  |  | 25 | AHU-5A: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2024: 15000
| Air Handling Unit | Mechanical 400 |  |  | 25 | AHU-4: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2024: 15000
| Air Handling Unit | Mechanical 402 |  |  | 25 | AHU-1: Replace in kind | planned maintenance | 32000 | Recommended Capital Allocation Year & Amount 2024: 32000
| Air Handling Unit | Mechanical 402 |  |  | 25 | AHU-2A: Replace in kind | planned maintenance | 28000 | Recommended Capital Allocation Year & Amount 2024: 28000
| Air Handling Unit | Mechanical 402 |  |  | 25 | AHU-2B: Replace in kind | planned maintenance | 28000 | Recommended Capital Allocation Year & Amount 2024: 28000
| Air Handling Unit | Mechanical 402 |  |  | 25 | AHU-3: Replace in kind | planned maintenance | 22000 | Recommended Capital Allocation Year & Amount 2024: 22000
| Air Handling Unit | Mechanical 402 |  |  | 25 | AHU-8: Replace in kind | planned maintenance | 7500 | Recommended Capital Allocation Year & Amount 2024: 7500
Electrical
| Lighting: Interior |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting: Controls |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 15000 | Recommended Capital Allocation Year & Amount 2022: 5000; Recommended Capital Allocation Year & Amount 2026: 5000; Recommended Capital Allocation Year & Amount 2029: 5000
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 10000 | Recommended Capital Allocation Year & Amount 2024: 5000; Recommended Capital Allocation Year & Amount 2028: 5000
TOTAL COSTS: | [7 empty] | 2852000 | 55000 | 349500 | 204000 | 101000 | 250500 | 106000 | 96000 | 77500 | 1506000 | 106500
List of items recommended to be addressed in the near future:
1. Replace roofing system
2. Repair / reseal exterior windows
3. Seal exterior masonry (only if recommended, may trap moisuture in wall cavities further investigation required)
4. Tuckpoint exterior masonry
5. Replace rooftop unit in Art Room
6. Replace chiller unit
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## E
HIGH SCHOOL
Facility Condition Assessment
| Building: | Building E |  |  |  | Facility Function:
| Gross SF: | 209922 |  |  |  | High school instruction
| Date of Visit | 2018-10-08
| Year Built: | 1971-2009
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations | Concrete |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade | Concrete |  |  | 100 | good condition, slight cracking | monitor yearly | 0
| Superstructure | Load bearing CMU, steel, precast concrete |  |  | 100 | good condition | monitor yearly | 12000 | Recommended Capital Allocation Year & Amount 2028: 12000
Exterior Envelope
| Exterior Doors | Aluminum |  |  | 40 | good condition, some moderate wear | monitor yearly | 45000 | Recommended Capital Allocation Year & Amount 2023: 15000; Recommended Capital Allocation Year & Amount 2025: 15000; Recommended Capital Allocation Year & Amount 2027: 15000
| Exterior Doors | Hollow Metal |  |  | 50 | good condition, some moderate wear | monitor yearly, replace as required | 20000 | Recommended Capital Allocation Year & Amount 2024: 10000; Recommended Capital Allocation Year & Amount 2026: 10000
| Exterior Lintels | Steel |  |  | 80 | good condition, some surface rust | monitor yearly, prep and repaint as required | 30000 | Recommended Capital Allocation Year & Amount 2022: 15000; Recommended Capital Allocation Year & Amount 2028: 15000
| Exterior Door Seals | Rubber |  |  | 15 | moderate wear | replacement | 0
| Exterior Door Thresholds | Aluminum |  |  | 30 | moderate wear | replacement | 23000 | Recommended Capital Allocation Year & Amount 2021: 23000
| Exterior Windows | Aluminum Frames |  |  | 40 | moderate to end-of-service life wear | monitor yearly, replace in original section of the building | 49000 | Recommended Capital Allocation Year & Amount 2022: 35000; Recommended Capital Allocation Year & Amount 2027: 14000
| Exterior Window Glazing | Double Glazed |  |  | 20 | good condition to end-of-service life wear | monitor yearly, replace window seals as required | 85000 | Recommended Capital Allocation Year & Amount 2025: 85000
| Exterior Walls/Cladding | Brick |  |  | 100 | some mortar separation and deterioration | tuckpointing | 75000 | Recommended Capital Allocation Year & Amount 2023: 25000; Recommended Capital Allocation Year & Amount 2026: 25000; Recommended Capital Allocation Year & Amount 2029: 25000
| Exterior Walls/Cladding | Precast concrete |  |  | 100 | good condition | monitor yearly, seal as required | 35000 | Recommended Capital Allocation Year & Amount 2025: 35000
| Exterior Walls/Cladding | Corrugated metal panel |  |  | 40 | moderate wear, minor cosmetic damage | monitor yearly, touch up as required | 40000 | Recommended Capital Allocation Year & Amount 2024: 20000; Recommended Capital Allocation Year & Amount 2028: 20000
| Exterior Walls/Cladding | Stone Sills |  |  | 100 | some mortar separation | tuckpointing | 20000 | Recommended Capital Allocation Year & Amount 2024: 10000; Recommended Capital Allocation Year & Amount 2028: 10000
| Caulking at Openings | Silicone, etc. |  |  | 14 | moderate to end-of-service life wear | monitor yearly, replace as required | 25000 | Recommended Capital Allocation Year & Amount 2022: 25000
| Roofing | Single-Ply / Ballasted |  |  | 25 | good condition to end-of-service life in some areas, some seam separation in areas, some existing patching, some aluminum gravel stop separation, some missing flashing, ponding in some areas | monitor quarterly, small spot repairs as required, replace in '98 addition and 'server room' area | 520000 | Recommended Capital Allocation Year & Amount 2027: 520000
| Roofing | Gutters & Downspouts, soffit fascia |  |  | 25 | good condition, some localized damage | monitor yearly, replace as required | 45000 | Recommended Capital Allocation Year & Amount 2021: 20000; Recommended Capital Allocation Year & Amount 2025: 25000
Interior Construction
| Interior Partitions | CMU |  |  | 100 | good condition, moderate wear | monitor yearly | 36000 | Recommended Capital Allocation Year & Amount 2023: 12000; Recommended Capital Allocation Year & Amount 2026: 12000; Recommended Capital Allocation Year & Amount 2029: 12000
| Interior Partitions | Metal Stud |  |  | 100 | good condition, moderate wear | monitor yearly | 45000 | Recommended Capital Allocation Year & Amount 2021: 15000; Recommended Capital Allocation Year & Amount 2024: 15000; Recommended Capital Allocation Year & Amount 2028: 15000
| Lockers | Metal Stud |  |  | 20 | good condition, some moderate wear | monitor yearly | 30000 | Recommended Capital Allocation Year & Amount 2021: 15000; Recommended Capital Allocation Year & Amount 2022: 15000
| Interior Doors | Wood |  |  | 60 | good condition, some moderate wear | monitor yearly | 0
| Interior Door Hardware | All |  |  | 25 | good condition, some moderate wear | monitor yearly | 30000 | Recommended Capital Allocation Year & Amount 2021: 10000; Recommended Capital Allocation Year & Amount 2025: 10000; Recommended Capital Allocation Year & Amount 2029: 10000
| Casework | Plam |  |  | 30 | good condition, some delamination in countertops and vertical faces | monitory yearly, replace as required | 90000 | Recommended Capital Allocation Year & Amount 2022: 30000; Recommended Capital Allocation Year & Amount 2025: 30000; Recommended Capital Allocation Year & Amount 2027: 30000
| Casework | Solid Surface |  |  | 30 | good conditioin | monitor yearly | 54000 | Recommended Capital Allocation Year & Amount 2021: 18000; Recommended Capital Allocation Year & Amount 2024: 18000; Recommended Capital Allocation Year & Amount 2028: 18000
Interior Finishes
| Floor Finish | Carpet |  |  | 15 | good condition to moderate wear | monitor yearly | 100000 | Recommended Capital Allocation Year & Amount 2023: 50000; Recommended Capital Allocation Year & Amount 2029: 50000
| Floor Finish | Vinyl Comp Tile |  |  | 35 | good condition, some damage | monitor yearly, replace | 100000 | Recommended Capital Allocation Year & Amount 2022: 50000; Recommended Capital Allocation Year & Amount 2026: 50000
| Floor Finish | Ceramic Tile |  |  | 40 | good condition, some cracking, some missing pieces | monitor yearly, replace | 85000 | Recommended Capital Allocation Year & Amount 2021: 15000; Recommended Capital Allocation Year & Amount 2024: 35000; Recommended Capital Allocation Year & Amount 2028: 35000
| Floor Finish | Terrazzo |  |  | 100 | good condition, some moderate wear | monitor yearly | 0
| Floor Finish | Quarry tile |  |  | 40 | good condition to moderate wear | monitor yearly | 20000 | Recommended Capital Allocation Year & Amount 2022: 10000; Recommended Capital Allocation Year & Amount 2027: 10000
| Floor Finish | Epoxy |  |  | 50 | good condition | monitor yearly | 0
| Floor Finish | Athletic Wood |  |  | 50 | good condition | monitor yearly | 15000 | Recommended Capital Allocation Year & Amount 2028: 15000
| Ceiling Finish | Gypsum Board |  |  | 30 | good condition, some damage | monitor yearly, replace as required | 75000 | Recommended Capital Allocation Year & Amount 2021: 25000; Recommended Capital Allocation Year & Amount 2025: 25000; Recommended Capital Allocation Year & Amount 2029: 25000
| Ceiling Finish | ACT |  |  | 25 | good condition, some damage | monitor yearly, replace as required | 40000 | Recommended Capital Allocation Year & Amount 2024: 20000; Recommended Capital Allocation Year & Amount 2028: 20000
| Wall Finish | Paint |  |  | 10 | good condition, moderate wear | monitor yearly, repaint as required | 225000 |  | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000
| Wall Finish | Ceramic Tile |  |  | 40 | good condition, some cracking, some missing pieces | monitor yearly, replace as required | 54000 | Recommended Capital Allocation Year & Amount 2022: 18000; Recommended Capital Allocation Year & Amount 2026: 18000; Recommended Capital Allocation Year & Amount 2029: 18000
| Wall Base | Rubber |  |  | 30 | good condition to moderate wear | monitor yearly, replace as required | 45000 | Recommended Capital Allocation Year & Amount 2021: 15000; Recommended Capital Allocation Year & Amount 2025: 15000; Recommended Capital Allocation Year & Amount 2028: 15000
Plumbing
| Plumbing Fixtures | Water Closet |  |  | 30 | 70 +/- Count, moderate wear | corrective maintenance | 20000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
| Plumbing Fixtures | Lavatories |  |  | 30 | 91 +/- Count, moderate wear | corrective maintenance | 35000 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500 | 3500
| Plumbing Fixtures | Urinals |  |  | 30 | 21 +/- Count, moderate wear | corrective maintenance | 15000 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
| Plumbing Fixtures | Flush Valves |  |  | 12 | 112 +/- Count, moderate-to-end of service life wear | corrective maintenance | 10000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Plumbing Fixtures | Faucets |  |  | 10 | 91 +/- Count, moderate-to-end of service life wear | corrective maintenance | 25000 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
| Plumbing Fixtures | Sump Pump |  |  | 10 | Elevator Sump | condition-based maintenance | 3500 | Recommended Capital Allocation Year & Amount 2022: 3500
| Plumbing Fixtures | Drinking Fountain |  |  | 30 | Replace in kind | corrective maintenance | 14000 | Recommended Capital Allocation Year & Amount 2022: 3500; Recommended Capital Allocation Year & Amount 2024: 3500; Recommended Capital Allocation Year & Amount 2026: 3500; Recommended Capital Allocation Year & Amount 2028: 3500
| Plumbing Fixtures | Backflow Prevntor |  |  | 6 | Replace in kind | condition-based maintenance | 10000 | Recommended Capital Allocation Year & Amount 2020: 5000; Recommended Capital Allocation Year & Amount 2026: 5000
| Domestic Water Distribution | Piping |  |  | 30 | Repair domestic water leaks | condition-based maintenance | 15000 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
HVAC
| Condensing Unit | Roof - Area O |  |  | 20 | CU-2: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 30000 | Recommended Capital Allocation Year & Amount 2023: 30000
| Packaged Rooftop Unit | Roof - Area O |  |  | 15 | RTU-2: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2023: 15000
| Packaged Rooftop Unit | Roof - Area O |  |  | 15 | RTU-3: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2025: 15000
| Makeup Air Unit | Roof - Area O |  |  | 15 | MAU-1: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2024: 15000
| Makeup Air Unit | Roof - Area O |  |  | 15 | MAU-2: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2024: 15000
| Packaged Rooftop Unit | Roof - Area N |  |  | 15 | RTU-4: Replace in kind | planned maintenance | 30000 | Recommended Capital Allocation Year & Amount 2025: 30000
| Exhaust Fan | Roof |  |  | 20 | EF-1 TO EF-25 | corrective maintenance | 24000 | 6000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
| Condensing Unit | Roof - Area H |  |  | 20 | CU-3: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 65000 | Recommended Capital Allocation Year & Amount 2023: 65000
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-6: Replace in kind | planned maintenance | 20000 | Recommended Capital Allocation Year & Amount 2020: 20000
| Condensing Unit | Roof - Area B |  |  | 20 | CU-4: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 5000 | Recommended Capital Allocation Year & Amount 2023: 5000
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-340: Replace in kind | planned maintenance | 13000 | Recommended Capital Allocation Year & Amount 2025: 13000
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-7: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2025: 8500
| Packaged Rooftop Unit | Roof - Area B |  |  | 15 | RTU-341: Replace in kind | planned maintenance | 10000 | Recommended Capital Allocation Year & Amount 2020: 10000
| Condensing Unit | Roof - Area B |  |  | 20 | CU-5: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 5000 | Recommended Capital Allocation Year & Amount 2023: 5000
| Packaged Rooftop Unit | Roof - Area CY |  |  | 15 | RTU-361: Replace in kind | planned maintenance | 15000 | Recommended Capital Allocation Year & Amount 2020: 15000
| Condensing Unit | Roof - Area CY |  |  | 20 | CU-6: Replace in kind with new refrigerant piping and dx coil. | planned maintenance | 5000 | Recommended Capital Allocation Year & Amount 2023: 5000
| Packaged Rooftop Unit | Roof - Area C |  |  | 15 | RTU-365: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2020: 8500
| Packaged Rooftop Unit | Roof - Area C |  |  | 15 | RTU-342: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2020: 8500
| Packaged Rooftop Unit | Roof - Area C |  |  | 15 | RTU-364: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2020: 8500
| Packaged Rooftop Unit | Roof - Area C |  |  | 15 | RTU-362: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2020: 8500
| Packaged Rooftop Unit | Roof - Area C |  |  | 15 | RTU-363: Replace in kind | planned maintenance | 8000 | Recommended Capital Allocation Year & Amount 2025: 8000
| Packaged Rooftop Unit | Roof - Area D |  |  | 15 | RTU-370: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2020: 8500
| Packaged Rooftop Unit | Roof - Area E |  |  | 15 | RTU-11: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2020: 8500
| Packaged Rooftop Unit | Roof - Area E |  |  | 15 | RTU-12: Replace in kind | planned maintenance | 8000 | Recommended Capital Allocation Year & Amount 2025: 8000
| Packaged Rooftop Unit | Roof - Area Z |  |  | 15 | RTU-15: Replace in kind | planned maintenance | 65000 | Recommended Capital Allocation Year & Amount 2025: 65000
| Packaged Rooftop Unit | Roof - Area S |  |  | 15 | RTU-16: Replace in kind | planned maintenance | 38000 | Recommended Capital Allocation Year & Amount 2025: 38000
| Packaged Rooftop Unit | Roof - Area S |  |  | 15 | RTU-17: Replace in kind | planned maintenance | 38000 | Recommended Capital Allocation Year & Amount 2025: 38000
| Packaged Rooftop Unit | Roof - Area S |  |  | 15 | RTU-18: Replace in kind | planned maintenance | 65000 | Recommended Capital Allocation Year & Amount 2025: 65000
| Packaged Rooftop Unit | Roof - Area S |  |  | 15 | RTU-19: Replace in kind | planned maintenance | 65000 | Recommended Capital Allocation Year & Amount 2025: 65000
| Packaged Rooftop Unit | Roof - Area K |  |  | 15 | RTU-20: Replace in kind | planned maintenance | 16000 | Recommended Capital Allocation Year & Amount 2023: 16000
| Packaged Rooftop Unit | Roof - Area A |  |  | 15 | RTU-21: Replace in kind | planned maintenance | 8000 | Recommended Capital Allocation Year & Amount 2025: 8000
| Dust Collector System | E-120 |  |  | 25 | Rehab ductwork as needed for equipment layout | planned maintenance | 35000 | Recommended Capital Allocation Year & Amount 2020: 35000
| Boiler | B-3 |  |  | 25 | Not functioning | corrective maintenance | 6500 | Recommended Capital Allocation Year & Amount 2020: 6500
| Boiler Plant Pumps | A-118 |  |  | 10 | P-1 to P-2: Replace pumps in kind and inculde hot water piping/insulation in boiler room. | planned maintenance | 50000 | Recommended Capital Allocation Year & Amount 2021: 50000
| Air Handling Unit | A-118 |  |  | 25 | AHU-1: Replace in kind | planned maintenance | 18000 | Recommended Capital Allocation Year & Amount 2027: 18000
| Air Handling Unit | A-118 |  |  | 25 | AHU-2: Replace in kind | planned maintenance | 7500 | Recommended Capital Allocation Year & Amount 2027: 7500
| Air Handling Unit | B-142 |  |  | 25 | AHU-3: Replace in kind | planned maintenance | 50000 | Recommended Capital Allocation Year & Amount 2027: 50000
| Air Handling Unit | D-126 |  |  | 25 | AHU-4: Replace in kind | planned maintenance | 8500 | Recommended Capital Allocation Year & Amount 2027: 8500
| Unit Ventilator | Locker Room |  |  | 25 | UV-1 TO UV-2: Replace in kind | planned maintenance | 30000 | Recommended Capital Allocation Year & Amount 2028: 30000
| Unit Ventilator | E Classrooms |  |  | 25 | UV-3 TO UV-11: Replace in kind | planned maintenance | 135000 | Recommended Capital Allocation Year & Amount 2028: 135000
| Unit Ventilator | F Classrooms |  |  | 25 | UV-12 TO UV-15: Replace in kind | planned maintenance | 60000 | Recommended Capital Allocation Year & Amount 2028: 60000
Electrical
| General electrical |  |  |  | Min 15 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 15 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Branch Wiring |  |  |  | 2 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 40 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 1 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 20 |  | corrective maintenance | 0
Equipment
Kitchen / Commercial Equipment
Fixed Furnishings
Fire Protection
| Clean Agent | Main Distribution |  |  |  | New FM-200 Clean agenet system | monitor yearly | 35000 | Recommended Capital Allocation Year & Amount 2022: 35000
| Clean Agent | Server Room |  |  |  | New FM-200 Clean agenet system | monitor yearly | 35000 | Recommended Capital Allocation Year & Amount 2023: 35000
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 12000 | Recommended Capital Allocation Year & Amount 2022: 4000; Recommended Capital Allocation Year & Amount 2026: 4000; Recommended Capital Allocation Year & Amount 2029: 4000
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 7500 | Recommended Capital Allocation Year & Amount 2020: 2500; Recommended Capital Allocation Year & Amount 2024: 2500; Recommended Capital Allocation Year & Amount 2028: 2500
| Drainage | [6 empty] | 0
| Landscaping | [6 empty] | 15000 | Recommended Capital Allocation Year & Amount 2021: 5000; Recommended Capital Allocation Year & Amount 2024: 5000; Recommended Capital Allocation Year & Amount 2027: 5000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 3361000 | 163000 | 250000 | 283000 | 317000 | 208000 | 640500 | 166500 | 717000 | 433000 | 183000
List of items recommended to be addressed in the near future:
1. Tuckpoint exterior masonry
2. Seal exterior precast concrete walls (only if recommended, may trap moisuture in wall further investigation required)
3. Replace rooftop unit for room 307
4. Replace windows in original section of building
5. Replace piping, insulation in Boiler Room
6. Replace pumps in Boiler Room
7. Replace roofing system in 1998 section
8. Replace roofing system in Server Room section
9. Repair / replace dust collector system in Wood Shop
10. Repair / replace controls for unit ventilators in original section of building
11. Replace exahust fans in original lockerooms
12. Repair / replace flashing on North & South Gymnasiums
13. Repair / replace flashing on original section of building
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## F
OPERATIONS & MAINTENANCE BUILDING 1
Facility Condition Assessment
| Building: | Building F |  |  |  | Facility Function:
| Gross SF: | 5600 |  |  |  | Maintenance & Vehicle Storage
| Date of Visit | 2018-10-08
| Year Built: | 1976-1996
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations |  |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade |  |  |  | 100 | near end-of-service life wear | replacement | 25000 | Recommended Capital Allocation Year & Amount 2021: 25000
| Wood Roof Framing |  |  |  | 50 | good condition | monitor yearly | 0
| Steel Roof Framing |  |  |  | 100 | good condition | monitor yearly | 0
Exterior Envelope
| Exterior Doors | Hollow Metal |  |  | 50 | end-of-service life wear | replacement | 15000 | Recommended Capital Allocation Year & Amount 2021: 15000
| Exterior Door Seals | Rubber |  |  | 15 | end-of-service life wear | replacement | 5000 | Recommended Capital Allocation Year & Amount 2021: 5000
| Exterior Door Thresholds | Aluminum |  |  | 30 | end-of-service life wear | replacement | 3500 | Recommended Capital Allocation Year & Amount 2021: 3500
| Exterior Walls/Cladding | Al uminum Panels |  |  | 30 | end-of-service life wear | replacement | 95000 | Recommended Capital Allocation Year & Amount 2021: 95000
| Caulking at Openings | Silicone, etc. |  |  | 14 | end-of-service life wear | replacement | 8000 | Recommended Capital Allocation Year & Amount 2021: 8000
| Roofing | Standing-Seam Metal |  |  | 35 | end-of-service life wear | replacement | 12000 | Recommended Capital Allocation Year & Amount 2021: 12000
| Roofing | Gutters & Downspouts, soffit fascia |  |  | 25 | end-of-service life wear | replacement | 5000 | Recommended Capital Allocation Year & Amount 2021: 5000
Interior Construction
| Interior Partitions | metal panel |  |  | 30 | end-of-service life wear | replacement | 5000 | Recommended Capital Allocation Year & Amount 2021: 5000
| Interior Partitions | foil-faced insulation |  |  | 20 | end-of-service life wear | replacement | 5000 | Recommended Capital Allocation Year & Amount 2021: 5000
| Interior Doors | Hollow Metal |  |  | 80 | end-of-service life wear | replacement | 4500 | Recommended Capital Allocation Year & Amount 2021: 4500
Interior Finishes
| Floor Finish | Sealed Conc. |  |  | 25 | near end-of-service life wear | replacement | 10000 | Recommended Capital Allocation Year & Amount 2021: 10000
| Ceiling Finish | Exposed |  |  | 30 | near end-of-service life wear | replacement | 5000 | Recommended Capital Allocation Year & Amount 2021: 5000
| Wall Insulated Panels | foil-faced insulation |  |  | 25 | near end-of-service life wear | replacement | 5000 | Recommended Capital Allocation Year & Amount 2021: 5000
HVAC
| Modine-type heaters | Ceiling |  |  | 13 | good condition | corrective maintenance | 8000 | Recommended Capital Allocation Year & Amount 2023: 8000
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
| Kitchen / Commercial Equipment | [6 empty] | 0
| Fixed Furnishings | [6 empty] | 0
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 3500 | Recommended Capital Allocation Year & Amount 2021: 3500
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 3000 | Recommended Capital Allocation Year & Amount 2021: 3000
| Drainage | [6 empty] | 0 | Recommended Capital Allocation Year & Amount 2021: 0
| Landscaping | [6 empty] | 2000 | Recommended Capital Allocation Year & Amount 2021: 2000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 219500 | 0 | 211500 | 0 | 8000 | 0 | 0 | 0 | 0 | 0 | 0
List of items recommended to be addressed in the near future:
1. Extensively repair OR replace entire building
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## G
HIGH SCHOOL CONCESSIONS BUILDING
Facility Condition Assessment
| Building: | Building G |  |  |  | Facility Function:
| Gross SF: | 5744 |  |  |  | Athletic even concessions, public restrooms, storage
| Date of Visit | 2018-10-08
| Year Built: | 2017
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations | Concrete |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade | Concrete |  |  | 100 | good condition | monitor yearly | 0
| Superstructure | Wood |  |  | 100 | good condition | monitor yearly | 0
Exterior Envelope
| Exterior OH Doors | Aluminum |  |  | 40 | good condition | monitor yearly | 0
| Exterior Doors | Hollow Metal |  |  | 50 | good condition | monitor yearly | 0
| Exterior Door Seals | Rubber |  |  | 15 | good condition | monitor yearly | 3200 | Recommended Capital Allocation Year & Amount 2029: 3200
| Exterior Door Thresholds | Aluminum |  |  | 30 | good condition | monitor yearly | 0
| Exterior Walls/Cladding | Thin brick |  |  | 50 | good condition | monitor yearly | 0
| Caulking at Openings | Silicone, etc. |  |  | 14 | good condition | monitor yearly | 0
| Roofing | Corrugated metal roof |  |  | 40 | good condition | monitor yearly | 0
Interior Construction
| Interior Partitions | Wood Stud |  |  | 40 | good condition | monitor yearly | 0
| Interior Door Hardware | All |  |  | 25 | good condition | monitor yearly | 0
| Casework | Plam / Wood |  |  | 30 | good condition | monitor yearly | 0
| Casework | Stainless steel |  |  | 80 | good condition | monitor yearly | 0
Interior Finishes
| Floor Finish | Concrete |  |  | 100 | good condition | monitor yearly | 0
| Ceiling Finish | ACT |  |  | 25 | good condition | monitor yearly | 0
| Ceiling Finish | Gypsum Board |  |  | 30 | good condition | monitor yearly | 0
| Wall Finish | FRP |  |  | 40 | good condition | monitor yearly | 0
Plumbing
| Plumbing Fixtures | Flush Valves |  |  | 12 | 14 +/- Count, good condition | condition-based maintenance | 0 | bar: Recommended Capital Allocation Year & Amount 2029
| Plumbing Fixtures | Faucets |  |  | 10 | 6 +/- Count, good condition | condition-based maintenance | 0 | bar: Recommended Capital Allocation Year & Amount 2027
| Plumbing Fixtures | Backflow Preventor |  |  | 6 | Replace in kind | condition-based maintenance | 0 | bar: Recommended Capital Allocation Year & Amount 2023; Recommended Capital Allocation Year & Amount 2027
HVAC
| Electric fin-tube | Baseboard |  |  | 10 | good condition | condition-based maintenance | 5000 | Recommended Capital Allocation Year & Amount 2027: 5000
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
| Kitchen / Commercial Equipment | [6 empty] | 5000 | Recommended Capital Allocation Year & Amount 2028: 5000
| Fixed Furnishings | [6 empty] | 0
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 5000 | Recommended Capital Allocation Year & Amount 2026: 5000
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 6500 | Recommended Capital Allocation Year & Amount 2024: 3000; Recommended Capital Allocation Year & Amount 2029: 3500
| Drainage | [6 empty] | 0
| Landscaping | [6 empty] | 3000 | Recommended Capital Allocation Year & Amount 2027: 3000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 27700 | 0 | 0 | 0 | 0 | 3000 | 0 | 5000 | 8000 | 5000 | 6700
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## H
HIGH SCHOOL FOUR SEASONS BUILDING
Facility Condition Assessment
| Building: | Building H |  |  |  | Facility Function:
| Gross SF: | 797 |  |  |  | Multi-function gathering space
| Date of Visit | 2018-10-08
| Year Built: | 2013
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations |  |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade |  |  |  | 100 | good condition | monitor yearly | 0
| Steel Roof Framing |  |  |  | 100 | good condition | monitor yearly | 0
Exterior Envelope
| Exterior Doors | Aluminum |  |  | 40 | good condition | monitor yearly | 0
| Exterior Door Thresholds | Steel |  |  | 30 | good condition | monitor yearly | 0
| Exterior Windows | Aluminum Double Glazed |  |  | 40 | good condition | monitor yearly | 0
| Exterior Walls/Cladding | Metal panels |  |  | 35 | good condition | monitor yearly | 0
| Caulking at Openings | Silicone, etc. |  |  | 14 | good condition | monitor yearly | 5000 | Recommended Capital Allocation Year & Amount 2027: 5000
| Roofing | Metal panels |  |  | 35 | good condition | monitor yearly | 0
Interior Construction
| Interior Partitions | metal panel |  |  | 35 | good condition | monitor yearly | 0
Interior Finishes
| Floor Finish | Carpet |  |  | 15 | good condition | monitor yearly | 7500 | Recommended Capital Allocation Year & Amount 2028: 7500
| Wall Finish | metal panel |  |  | 20 | good condition | monitor yearly | 5000 | Recommended Capital Allocation Year & Amount 2027: 5000
HVAC
| Modine-type heater | Ceiling |  |  | 13 | good condition | condition based maintenance | 8000 | Recommended Capital Allocation Year & Amount 2026: 8000
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
| Kitchen / Commercial Equipment | [6 empty] | 0
| Fixed Furnishings | [6 empty] | 0
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 5000 | Recommended Capital Allocation Year & Amount 2027: 5000
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 5000 | Recommended Capital Allocation Year & Amount 2028: 5000
| Drainage | [6 empty] | 0
| Landscaping | [6 empty] | 5000 | Recommended Capital Allocation Year & Amount 2027: 5000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 40500 | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 20000 | 12500 | 0
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## I
OPERATIONS & MAINTENANCE BUILDING 2
Facility Condition Assessment
| Building: | Building I |  |  |  | Facility Function:
| Gross SF: | 2400 |  |  |  | Maintenance & Vehicle Storage
| Date of Visit | 2019-01-16
| Year Built: | 2008
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations |  |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade |  |  |  | 100 | good condition | monitor yearly | 0
| Wood Roof Framing |  |  |  | 50 | good condition | monitor yearly | 0
| Steel Roof Framing |  |  |  | 100 | good condition | monitor yearly | 0
Exterior Envelope
| Exterior Doors | Hollow Metal |  |  | 50 | good condition | monitor yearly | 0
| Exterior Door Seals | Rubber |  |  | 15 | good condition | monitor yearly | 0
| Exterior Door Thresholds | Aluminum |  |  | 30 | good condition | monitor yearly | 0
| Exterior Walls/Cladding | Al uminum Panels |  |  | 30 | good condition | monitor yearly | 0
| Caulking at Openings | Silicone, etc. |  |  | 14 | good condition | monitor yearly | 4000 | Recommended Capital Allocation Year & Amount 2024: 4000
| Roofing | Standing-Seam Metal |  |  | 35 | good condition | monitor yearly | 0
| Roofing | Gutters & Downspouts, soffit fascia |  |  | 25 | good condition | monitor yearly | 0
Interior Construction
| Interior Partitions | metal panel |  |  | 30 | good condition | monitor yearly | 0
| Interior Partitions | faced insulation |  |  | 20 | good condition | monitor yearly | 0
| Interior Doors | Hollow Metal |  |  | 80 | good condition | monitor yearly | 0
Interior Finishes
| Floor Finish | Sealed Conc. |  |  | 25 | good condition | monitor yearly | 0
| Ceiling Finish | Exposed |  |  | 30 | good condition | monitor yearly | 0
| Wall Insulated Panels | faced insulation |  |  | 25 | good condition | monitor yearly | 0
HVAC
| Gas fired heaters | Ceiling |  |  | 13 | Replace in kind | condition-based maintenance | 16000 | Recommended Capital Allocation Year & Amount 2021: 16000
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
| Kitchen / Commercial Equipment | [6 empty] | 0
| Fixed Furnishings | [6 empty] | 0
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 5000 | Recommended Capital Allocation Year & Amount 2025: 5000
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 5000 | Recommended Capital Allocation Year & Amount 2027: 5000
| Drainage | [6 empty] | 0
| Landscaping | [6 empty] | 6000 | Recommended Capital Allocation Year & Amount 2026: 3000; Recommended Capital Allocation Year & Amount 2029: 3000
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 36000 | 0 | 16000 | 0 | 0 | 4000 | 5000 | 3000 | 5000 | 0 | 3000 | 36000
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## J
HELP FOR HOPE BUILDING
Facility Condition Assessment
| Building: | Building J |  |  |  | Facility Function:
| Gross SF: | 2560 |  |  |  | Community Food Pantry
| Date of Visit | 2018-10-08
| Year Built: | 1969-1993
Property Components |  | Area / Type / Location | * Initial Installation | Renovated Date * | Life Exp. | Comments / Equipment Tag | Improvement Type | Improv. Cost | Recommended Capital Allocation Year & Amount
[9 empty] | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Substructure
| Foundations | Concrete |  |  | 100 | good condition | monitor yearly | 0
| Slabs on Grade | Concrete |  |  | 100 | good condition | monitor yearly | 0
Exterior Envelope
| Exterior Doors | Wood |  |  | 35 | moderate wear | monitor yearly | 0
| Exterior Door Seals | Rubber |  |  | 15 | end-of-service life wear | replacement | 4000 | Recommended Capital Allocation Year & Amount 2021: 4000
| Exterior Door Thresholds | Aluminum |  |  | 30 | end-of-service life wear | replacement | 3500 | Recommended Capital Allocation Year & Amount 2022: 3500
| Exterior Windows | Wood |  |  | 40 | moderate wear | monitor yearly | 0
| Exterior Walls/Cladding | Siding |  |  | 30 | moderate wear | monitor yearly | 3500 | Recommended Capital Allocation Year & Amount 2023: 3500
| Caulking at Openings | Silicone, etc. |  |  | 14 | end-of-service life wear | replacement | 4000 | Recommended Capital Allocation Year & Amount 2024: 4000
| Fascia | Aluminum |  |  | 50 | moderate wear | monitor yearly | 0
| Soffit | Aluminum |  |  | 40 | moderate wear | monitor yearly | 0
| Roofing | Asphalt Shingles |  |  | 20 | end-of-service life wear | replacement | 35840 | Recommended Capital Allocation Year & Amount 2022: 35840
Interior Construction
| Interior Partitions | Stud |  |  | 100 | moderate wear | monitor yearly | 0
| Interior Doors | Wood |  |  | 60 | moderate wear | monitor yearly | 0
Interior Finishes
| Floor Finish | Carpet |  |  | 15 | moderate wear | monitor yearly | 0
| Floor Finish | Ceramic Tile |  |  | 40 | moderate wear | monitor yearly | 0
| Ceiling Finish | Gypsum Board |  |  | 30 | moderate wear | monitor yearly | 0
| Ceiling Finish | ACT |  |  | 25 | some water damaged tiles | monitor yearly, replace as required | 10000 | Recommended Capital Allocation Year & Amount 2021: 5000; Recommended Capital Allocation Year & Amount 2027: 5000
| Wall Finish | Paint |  |  | 10 | moderate wear | monitor yearly | 6000 | Recommended Capital Allocation Year & Amount 2023: 3000; Recommended Capital Allocation Year & Amount 2026: 3000
Interior Miscellaneous
| Countertops | Plastic Lam. |  |  | 20 | moderate wear | monitor yearly | 6000 | Recommended Capital Allocation Year & Amount 2025: 3000; Recommended Capital Allocation Year & Amount 2029: 3000
Plumbing
| Plumbing Fixtures | Water Closet |  |  | 30 | 2 +/- Count, moderate wear | replace as required | 4500 | Recommended Capital Allocation Year & Amount 2022: 4500
| Plumbing Fixtures | Lavatories |  |  | 30 | 4 +/- Count, moderate wear | replace as required | 6500 | Recommended Capital Allocation Year & Amount 2022: 6500
| Plumbing Fixtures | Faucets |  |  | 10 | 4 +/- Count, moderate wear | replace as required | 3000 | Recommended Capital Allocation Year & Amount 2022: 3000
HVAC
| Residential type furnace |  |  |  | 18 | moderate wear | planned maintenance | 7500 | Recommended Capital Allocation Year & Amount 2023: 7500
| Residential air conditioner |  |  |  | 18 | moderate wear | planned maintenance | 8000 | Recommended Capital Allocation Year & Amount 2021: 8000
Electrical
| General electrical |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Lighting/Control: Interior |  |  |  | 20 | Upgrade to LED Fixtures with wireless controls | condition-based maintenance | 0
| Lighting: Exterior |  |  |  | 20 | Upgrade to LED fixtures | condition-based maintenance | 0
| Branch Wiring |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Electrical Service/Distribution |  |  |  | 30 | Replace in kind | corrective maintenance | 0
| Fire Alarm |  |  |  | 15 | Replace in kind | corrective maintenance | 0
| Information Technology |  |  |  | 10 |  | corrective maintenance | 0
Equipment
| Kitchen / Commercial Equipment | [6 empty] | 0
| Fixed Furnishings | [6 empty] | 0
Site
| Driveways | Asphalt |  |  | 20 | good condition, some irregularities | monitor yearly | 0
| Pedestrian Paving | Concrete |  |  | 40 | good condition, some irregularities | monitor yearly | 0
| Drainage | [6 empty] | 0
| Landscaping | [6 empty] | 0
Site Utilities
| Storm Sewer | [6 empty] | 0
| Sanitary Sewer | [6 empty] | 0
| Site Fuel Distribution - Gas | [6 empty] | 0
| Site Electrical Distribution | [6 empty] | 0
TOTAL COSTS: | [7 empty] | 102340 | 0 | 17000 | 53340 | 14000 | 4000 | 3000 | 3000 | 5000 | 0 | 3000
Existing Mechanical System Replacement Priorities
Based on the mechanical system evaluation, a priority list was established. Please refer to the priority key below and the notes area on the facility equipment list for individual equipment recommendations.
Immediate Need - Replace Immediately (Systems that are currently not operating or consistently being repaired)
Priority Level 1 - Replace in 1-2 years (Systems that are well beyond their useful service life and on the verge of failure)
Priority Level 2 - Replace in 2-5 years (Systems that are nearing their useful service life)
Priority Level 3 - Replace in 5+ years (Systems that should be scheduled for replacement based on anticipated remaining life and current condition)

## A MECH EQUIPMENT
EARLY CHILDHOOD CENTER
Facility Equipment List - Mechanical
Mechanical Equipment |  | Manufacturer Information |  | Operational Capacity |  | Notes
TAG | RTU-1 | MANUFACTURER | MCQUAY | COOLING CAPACITIES (TONS) | 32 | YEAR MANUFACTURED | 2007
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RPS030CLY | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA B | SERIAL NUMBER | FBOU071200365 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-2 | MANUFACTURER | MCQUAY | COOLING CAPACITIES (TONS) | 66 | YEAR MANUFACTURED | 2007
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RPS060CSY | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA A | SERIAL NUMBER | FBOU071200013 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-3 | MANUFACTURER | MCQUAY | COOLING CAPACITIES (TONS) | 66 | YEAR MANUFACTURED | 2007
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RPS060CSY | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA C | SERIAL NUMBER | FBOU071200363 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-4 | MANUFACTURER | MCQUAY | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2007
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | MPS003AYCK | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA B | SERIAL NUMBER | 7368F140705639 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-5 | MANUFACTURER | MCQUAY | COOLING CAPACITIES (TONS) | 46 | YEAR MANUFACTURED | 2007
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RPS045CSY | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA B | SERIAL NUMBER | FBOU071200364 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | EF-1 TO EF-5 | MANUFACTURER | GREENHECK | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2008
EQUIPMENT | EXHAUST FAN | MODEL NUMBER | CUBE-131-5-X | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF | SERIAL NUMBER | 111649120801 | REFRIGERATION TYPE | NA | QUANTITY | 5
TAG | RF-1 TO RF-3 | MANUFACTURER | FANTECH | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2016
EQUIPMENT | RADON FAN | MODEL NUMBER | FR250 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF | SERIAL NUMBER | 2374724 | REFRIGERATION TYPE | NA | QUANTITY | 3
TAG | B-1 | MANUFACTURER | AERCO | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2008
EQUIPMENT | BOILER | MODEL NUMBER | BMK2.0 | HEATING CAPACITIES (MBH) | 1500 | PRIORITY | 3
LOCATION | B-118 | SERIAL NUMBER | G-08-0022 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-2 | MANUFACTURER | AERCO | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2008
EQUIPMENT | BOILER | MODEL NUMBER | BMK2.0 | HEATING CAPACITIES (MBH) | 1500 | PRIORITY | 3
LOCATION | B-118 | SERIAL NUMBER | G-08-0023 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | HT-1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2008
EQUIPMENT | UNIT HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | 37 | PRIORITY | 3
LOCATION | B-118 | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | KH-1 | MANUFACTURER | GREENHECK | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2008
EQUIPMENT | KITCHEN HOOD | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | B-133 | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | HT | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | WALL CABINET HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | VARIES | PRIORITY | 3
LOCATION | VESTIBULES | SERIAL NUMBER | NA | REFRIGERATION TYPE | - | QUANTITY | 9

## B MECH EQUIPMENT
ELEMENTARY SCHOOL
Facility Equipment List - Mechanical
Mechanical Equipment |  | Manufacturer Information |  | Operational Capacity |  | Notes
TAG | CU-1 | MANUFACTURER | LENNOX | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2013
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | TSA048S4N43Y | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA J | SERIAL NUMBER | 5813E18197 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-7 | MANUFACTURER | LENNOX | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2013
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | TSA048S4N43Y | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA J | SERIAL NUMBER | 5813D19857 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-2 | MANUFACTURER | LENNOX | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2012
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | TSA048S4N43Y | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA J | SERIAL NUMBER | 5812K06335 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-6 | MANUFACTURER | LENNOX | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2012
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | TSA048S4N43Y | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA J | SERIAL NUMBER | 5812H07822 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-702 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 1.5 | YEAR MANUFACTURED | 1995
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48SS-018040311 | HEATING CAPACITIES (MBH) | 40 | PRIORITY | 1
LOCATION | ROOF - AREA J | SERIAL NUMBER | 0395G10185 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | CU-4 | MANUFACTURER | LENNOX | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2013
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | TSA048S4N43Y | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA J | SERIAL NUMBER | 5813D19870 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-5 | MANUFACTURER | LENNOX | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2012
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | TSA048S4N43Y | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA J | SERIAL NUMBER | 5812M00701 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | EF-1 TO EF-6 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | TBD
EQUIPMENT | EXHAUST FAN | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 6
TAG | RTU-707 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G50005 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-723 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G40010 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-720 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G50001 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-768 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G40011 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-1 | MANUFACTURER | STERLING | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2002
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | E1G-RT15C6C01K42J2AB3ABE3H | HEATING CAPACITIES (MBH) | 150 | PRIORITY | 1
LOCATION | ROOF - AREA H | SERIAL NUMBER | H0230526_ | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-718 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G50004 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-719 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G40014 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-716 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G50003 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-717 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA H | SERIAL NUMBER | 3409G40012 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-767 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 2015
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCRD08A2M5A0B5F0 | HEATING CAPACITIES (MBH) | 180 | PRIORITY | 3
LOCATION | ROOF - AREA I | SERIAL NUMBER | 2815P82332 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | HP-1 | MANUFACTURER | MITSUBISHI | COOLING CAPACITIES (TONS) | 2.5 | YEAR MANUFACTURED | 2014
EQUIPMENT | SPLIT SYSTEM HEAT PUMP | MODEL NUMBER | MXZ-3C30NAHZ | HEATING CAPACITIES (MBH) | 27 | PRIORITY | 3
LOCATION | ROOF - AREA I | SERIAL NUMBER | 4ZP01296 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-721 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 1.5 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48ES-018040301TP | HEATING CAPACITIES (MBH) | 40 | PRIORITY | 2
LOCATION | ROOF - AREA G | SERIAL NUMBER | 0509G50711 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-7 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA G | SERIAL NUMBER | 3409G50006 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-715 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 20 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCTD25A6M5A2B4J0 | HEATING CAPACITIES (MBH) | 400 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2416P15955 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-714 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2A5A2F0C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2313C86152 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-2 | MANUFACTURER | STERLING | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2002
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | E1G-RT15C6C01K42J2AB3ABE3H | HEATING CAPACITIES (MBH) | 150 | PRIORITY | 1
LOCATION | ROOF - AREA G | SERIAL NUMBER | H02305261 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-713 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2A5A2F0C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2313C86156 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-712 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2A5A2F0C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2313C86154 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-711 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2A5A2F0C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2313C86153 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-710 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2A5A2F0C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2313C86151 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-708 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2A5A2F0C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2313C86157 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-709 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2A5A2F0C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 2313C86155 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-769 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 1998
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | YCD090C3HABE | HEATING CAPACITIES (MBH) | 205 | PRIORITY | 1
LOCATION | ROOF - AREA D | SERIAL NUMBER | N31104515D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-770 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 1998
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | YCD090C3HABE | HEATING CAPACITIES (MBH) | 205 | PRIORITY | 1
LOCATION | ROOF - AREA D | SERIAL NUMBER | N31101570D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-685 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA04A1M5A2B4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA C | SERIAL NUMBER | 2316C89875 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-686 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA04A1M5A2B4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA C | SERIAL NUMBER | 2316C89872 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-6 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA04A1M5A2B4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA C | SERIAL NUMBER | 2316C89874 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-696 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA04A1M5A2B4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA C | SERIAL NUMBER | 2316C89873 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-8 | MANUFACTURER | HEATCRAFT | COOLING CAPACITIES (TONS) | 1.5 | YEAR MANUFACTURED | 2009
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | LHT015X68 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA F | SERIAL NUMBER | T09H02993 | REFRIGERATION TYPE | R-404A | QUANTITY | 1
TAG | CU-9 | MANUFACTURER | HEATCRAFT | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2009
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | LZT030L6C | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA F | SERIAL NUMBER | T09H02994 | REFRIGERATION TYPE | R-404A | QUANTITY | 1
TAG | UV-1 TO UV-6 | MANUFACTURER | UL | COOLING CAPACITIES (TONS) | VARIES | YEAR MANUFACTURED | 2013
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | U.AVS.6.S15.A.G.66.A.17.AL.22.GBB1 | HEATING CAPACITIES (MBH) | VARIES | PRIORITY | 3
LOCATION | CLASSROOMS | SERIAL NUMBER | AUBU132901612 | REFRIGERATION TYPE | NA | QUANTITY | 6
TAG | UV-7 | MANUFACTURER | UL | COOLING CAPACITIES (TONS) | VARIES | YEAR MANUFACTURED | 2006
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | U.AZV.5.048.B.G.13.Z.B7.AL.22.G.I.B.3 | HEATING CAPACITIES (MBH) | VARIES | PRIORITY | 3
LOCATION | CLASSROOM 114 | SERIAL NUMBER | E798981010 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | UV-8 | MANUFACTURER | UL | COOLING CAPACITIES (TONS) | VARIES | YEAR MANUFACTURED | 2002
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | U.AZR.4.040.B.G.13.Z.19.AL.22.G.1.B.1 | HEATING CAPACITIES (MBH) | VARIES | PRIORITY | 3
LOCATION | CLASSROOM 102 | SERIAL NUMBER | E734799010 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | UV-9 TO UV-16 | MANUFACTURER | UL | COOLING CAPACITIES (TONS) | VARIES | YEAR MANUFACTURED | 1999
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | U.AZS.3.040.B.13.Z.19.AL.22.G.I.B.1 | HEATING CAPACITIES (MBH) | VARIES | PRIORITY | 2
LOCATION | CLASSROOMS | SERIAL NUMBER | 210416100 | REFRIGERATION TYPE | R-22 | QUANTITY | 7
TAG | AC-1 | MANUFACTURER | SANYO | COOLING CAPACITIES (TONS) | 1 | YEAR MANUFACTURED | 1990
EQUIPMENT | SPLIT SYSTEM AC UNIT | MODEL NUMBER | K1812W | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | A-120 | SERIAL NUMBER | 0168304 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | AC-2 | MANUFACTURER | SANYO | COOLING CAPACITIES (TONS) | 1 | YEAR MANUFACTURED | 1990
EQUIPMENT | SPLIT SYSTEM AC UNIT | MODEL NUMBER | K1812W | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | A-119 | SERIAL NUMBER | 0168204 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | AC-3 | MANUFACTURER | SANYO | COOLING CAPACITIES (TONS) | 1 | YEAR MANUFACTURED | 1990
EQUIPMENT | SPLIT SYSTEM AC UNIT | MODEL NUMBER | K1812W | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | A-118 | SERIAL NUMBER | 0168104 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | B-1 | MANUFACTURER | LOCHINVAR | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2015
EQUIPMENT | BOILER | MODEL NUMBER | FBN1251 | HEATING CAPACITIES (MBH) | 1250 | PRIORITY | 3
LOCATION | A-157 | SERIAL NUMBER | 1619102945534 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-2 | MANUFACTURER | LOCHINVAR | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2015
EQUIPMENT | BOILER | MODEL NUMBER | FBN1251 | HEATING CAPACITIES (MBH) | 1250 | PRIORITY | 3
LOCATION | A-157 | SERIAL NUMBER | 1619102945535 | REFRIGERATION TYPE | NA | QUANTITY | 1

## C MECH EQUIPMENT
INTERMEDIATE SCHOOL
Facility Equipment List - Mechanical
Mechanical Equipment |  | Manufacturer Information |  | Operational Capacity |  | Notes
TAG | EF-1 TO EF-7 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | EXHAUST FAN | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 7
TAG | RTU-782 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA A | SERIAL NUMBER | 3409G40009 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-783 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA A | SERIAL NUMBER | 3409G40013 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-3 | MANUFACTURER | VALENT | COOLING CAPACITIES (TONS) | 45 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | VPRX-350-50E-60I-A-1DX | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 13298893 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-4 | MANUFACTURER | VALENT | COOLING CAPACITIES (TONS) | 45 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | VPRX-350-40E-90I-A-4DX | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 13298894 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-5 | MANUFACTURER | VALENT | COOLING CAPACITIES (TONS) | 45 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | VPRX-350-50E-60I-A-1DX | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - AREA B | SERIAL NUMBER | 13298895 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-798 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA E | SERIAL NUMBER | 3409G50002 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-788 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2009
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48PDMC05-M-50-B3 | HEATING CAPACITIES (MBH) | 75 | PRIORITY | 2
LOCATION | ROOF - AREA F | SERIAL NUMBER | 3409G50015 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-2 | MANUFACTURER | VALENT | COOLING CAPACITIES (TONS) | 45 | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | VPRX-350-30E-60I-A-4DX | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - AREA G | SERIAL NUMBER | 13298856 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-6 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 10 | YEAR MANUFACTURED | 2014
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | YSC120F3RZA0BD6 | HEATING CAPACITIES (MBH) | 250 | PRIORITY | 3
LOCATION | ROOF - AREA M | SERIAL NUMBER | 143113028L | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-1 | MANUFACTURER | STERLING | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | 2013
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | M1P-PV80A6G03M53S5QB5L4 | HEATING CAPACITIES (MBH) | 800 | PRIORITY | 3
LOCATION | ROOF - AREA I | SERIAL NUMBER | E1301224870001001 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-1 | MANUFACTURER | HEATCRAFT | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2016
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - SOUTH | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | CU-2 | MANUFACTURER | HEATCRAFT | COOLING CAPACITIES (TONS) | 3 HP | YEAR MANUFACTURED | 2016
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | LHT030X6CFM | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - SOUTH | SERIAL NUMBER | T16D08845 | REFRIGERATION TYPE | R-404A | QUANTITY | 1
TAG | B-1 | MANUFACTURER | AERCO | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2013
EQUIPMENT | BOILER | MODEL NUMBER | BENCHMARK 2.0LN | HEATING CAPACITIES (MBH) | 1500 | PRIORITY | 3
LOCATION | 22A | SERIAL NUMBER | G-13-0903 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-2 | MANUFACTURER | AERCO | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2013
EQUIPMENT | BOILER | MODEL NUMBER | BENCHMARK 2.0LN | HEATING CAPACITIES (MBH) | 1500 | PRIORITY | 3
LOCATION | 22A | SERIAL NUMBER | G-13-0903 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | HT-1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | CABINET WALL HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | NE STAIRS | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | F-2 | MANUFACTURER | JACKSON & CHURCH | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | NA
EQUIPMENT | FURNACE | MODEL NUMBER | SDF25-GMSH-MB-RH | HEATING CAPACITIES (MBH) | 313 | PRIORITY
LOCATION | 44B | SERIAL NUMBER | B92-479 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | KH-1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | KITCHEN HOOD | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | 44C | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1

## D MECH EQUIPMENT
MIDDLE SCHOOL
Facility Equipment List - Mechanical
Mechanical Equipment |  | Manufacturer Information |  | Operational Capacity |  | Notes
TAG | RTU-MS6 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2M6A2B4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 2316C89903 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-MS7 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA06A2M6A2B4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | Facility Equipment List - Mechanical | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-MS1 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 10 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCRD12A2M6A2A4J0 | HEATING CAPACITIES (MBH) | 224 | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 2316P96897 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-MS8 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 12.5 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48LCSB14A7M6A1B4C0 | HEATING CAPACITIES (MBH) | 176 | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 2416P15930 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-MS5 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA05A2M6A2A4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 2316C89894 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-MS2 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 10 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCRD12A2M6A2A4J0 | HEATING CAPACITIES (MBH) | 224 | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 2316P96896 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-MS3 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 10 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCRD12A2M6A2A4J0 | HEATING CAPACITIES (MBH) | 224 | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 2316P96895 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-MS4 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCRD08A2M62A4J0 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | 2316P96847 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | EF-1 | MANUFACTURER | TWIN CITY | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | EXHAUST FAN | MODEL NUMBER | DCRD130BE1 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA B | SERIAL NUMBER | E16-000000183573 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | CH-1 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 300 | YEAR MANUFACTURED | 2000
EQUIPMENT | CHILLER | MODEL NUMBER | RTAA3004XT0IA3D0BFGKM | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | GRADE - EAST B | SERIAL NUMBER | U00006706 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | UV-1 TO UV-9 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | VARIES | YEAR MANUFACTURED | 2016
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | MAUVF411AFB223X0M1AAALAXA1A | HEATING CAPACITIES (MBH) | VARIES | PRIORITY | 3
LOCATION | CLASSROOMS | SERIAL NUMBER | W160789057 | REFRIGERATION TYPE | NA | QUANTITY | 44
TAG | KH-1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | KITCHEN HOOD | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | -
LOCATION | KITCHEN 127 | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | HT-1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | UNIT HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | 14.3 | PRIORITY | 3
LOCATION | CORRIDOR 130 | SERIAL NUMBER | NA | REFRIGERATION TYPE | - | QUANTITY | 1
TAG | HT-2 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | CABINET WALL HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | 14.5 | PRIORITY | 3
LOCATION | CORRIDOR 300C | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-6 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 25 | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA014BBJ0B0CA | HEATING CAPACITIES (MBH) | 630 | PRIORITY | 2
LOCATION | MECHANICAL 401 | SERIAL NUMBER | K99H50329N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-5B | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 25 | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA014GAW0ABA | HEATING CAPACITIES (MBH) | 622 | PRIORITY | 2
LOCATION | MECHANICAL 401 | SERIAL NUMBER | K99H50318N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-5A | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 25 | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA014GAW0ABA | HEATING CAPACITIES (MBH) | 622 | PRIORITY | 2
LOCATION | MECHANICAL 400 | SERIAL NUMBER | K99H50303N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-4 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA008ABH0B0A | HEATING CAPACITIES (MBH) | 208 | PRIORITY | 2
LOCATION | MECHANICAL 400 | SERIAL NUMBER | K99H50368N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-1 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 36 | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA030GAW0AAA | HEATING CAPACITIES (MBH) | 972 | PRIORITY | 2
LOCATION | MECHANICAL 402 | SERIAL NUMBER | K99H50258N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-2A | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 37.5 | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA025GAW0ABA | HEATING CAPACITIES (MBH) | 994 | PRIORITY | 2
LOCATION | MECHANICAL 402 | SERIAL NUMBER | K99H50266N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-2B | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 37.5 | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA025GAW0ABA | HEATING CAPACITIES (MBH) | 994 | PRIORITY | 2
LOCATION | MECHANIGAL 402 | SERIAL NUMBER | K99H50279N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-3 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 24 | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA021UB000A | HEATING CAPACITIES (MBH) | 572 | PRIORITY | 2
LOCATION | MECHANICAL 402 | SERIAL NUMBER | K99H50284N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-8 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | 1999
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | MCCA006GAW0AAA | HEATING CAPACITIES (MBH) | 125 | PRIORITY | 2
LOCATION | MECHANICAL 402 | SERIAL NUMBER | K99H50377N | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-1 | MANUFACTURER | LOCHINVAR | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2016
EQUIPMENT | BOILER | MODEL NUMBER | FBN2500 | HEATING CAPACITIES (MBH) | 2500 | PRIORITY | 3
LOCATION | MECHANICAL 402 | SERIAL NUMBER | 1608102642359 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-2 | MANUFACTURER | LOCHINVAR | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2016
EQUIPMENT | BOILER | MODEL NUMBER | FBN2500 | HEATING CAPACITIES (MBH) | 2500 | PRIORITY | 3
LOCATION | MECHANICAL 402 | SERIAL NUMBER | 1608102642361 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-3 | MANUFACTURER | LOCHINVAR | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2014
EQUIPMENT | BOILER | MODEL NUMBER | CHN1802 | HEATING CAPACITIES (MBH) | 1800 | PRIORITY | 3
LOCATION | MECHANICAL 402 | SERIAL NUMBER | H14H00267368 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | HT-3 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | NA
EQUIPMENT | UNIT HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | MECHANICAL 402 | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1

## E MECH EQUIPMENT
HIGH SCHOOL
Facility Equipment List - Mechanical
Mechanical Equipment |  | Manufacturer Information |  | Operational Capacity |  | Notes
TAG | RTU-1 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 25 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCTD28A2M6A2B4J0 | HEATING CAPACITIES (MBH) | 400 | PRIORITY | 3
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | 2416P15949 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-1 | MANUFACTURER | HEATCRAFT | COOLING CAPACITIES (TONS) | 1 | YEAR MANUFACTURED | 2010
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | MOZ045L63CF | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | T10D05574 | REFRIGERATION TYPE | R-404A | QUANTITY | 1
TAG | CU-2 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 20 | YEAR MANUFACTURED | 2003
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | RAUCC204BX03A0DF | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | C03B01213 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-2 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 2008
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J07HAC00A4AAA1A | HEATING CAPACITIES (MBH) | - | PRIORITY | 2
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | (S)N0H8226938 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-3 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J07ZHN15Q4AZZ50001A | HEATING CAPACITIES (MBH) | 180 | PRIORITY | 3
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | N1A0548042 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | MAU-1 | MANUFACTURER | BANANZA | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | 2009
EQUIPMENT | MAKEUP AIR UNIT | MODEL NUMBER | B650 | HEATING CAPACITIES (MBH) | 540 | PRIORITY | 3
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | 0912650.8 | REFRIGERATION TYPE | - | QUANTITY | 1
TAG | MAU-2 | MANUFACTURER | BANANZA | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | 2009
EQUIPMENT | MAKEUP AIR UNIT | MODEL NUMBER | B650 | HEATING CAPACITIES (MBH) | 648 | PRIORITY | 3
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | 09102650.7 | REFRIGERATION TYPE | - | QUANTITY | 1
TAG | RTU-4 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 25 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J25ZJC00Q4AZZ10007B | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - AREA 0 | SERIAL NUMBER | N1A0538170 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | EF-1 TO EF-25 | MANUFACTURER | CARNES | COOLING CAPACITIES (TONS) | - | YEAR MANUFACTURED | 2009
EQUIPMENT | EXHAUST FAN | MODEL NUMBER | VEBK08L#A1UA108PC1 | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - AREA N | SERIAL NUMBER | 652401.003 | REFRIGERATION TYPE | - | QUANTITY | 1
TAG | RTU-5 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 25 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48A3S025-NM62AFP | HEATING CAPACITIES (MBH) | 350 | PRIORITY | 3
LOCATION | ROOF - AREA H | SERIAL NUMBER | 2616U47654 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | CU-3 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 60 | YEAR MANUFACTURED | 2003
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | RAUCC604BX03A0DF | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | ROOF - AREA H | SERIAL NUMBER | C03B01214 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-6 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 15 | YEAR MANUFACTURED | 2002
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 50TJ-016-681AA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | ROOF - AREA B | SERIAL NUMBER | 2602F63551 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | CU-4 | MANUFACTURER | COMFORTMAKER | COOLING CAPACITIES (TONS) | 3.5 | YEAR MANUFACTURED | 2003
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | CAC042AKA5 | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA B | SERIAL NUMBER | E031431563 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-340 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J05ZJE1504AZZ100031C | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA B | SERIAL NUMBER | N1A0538198 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-7 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J03ZJE07U4AZZ10002 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA B | SERIAL NUMBER | N1A0541452 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-341 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TCD048C40ABC | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA B | SERIAL NUMBER | M29103326D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | CU-5 | MANUFACTURER | COMFORTMAKER | COOLING CAPACITIES (TONS) | 3.5 | YEAR MANUFACTURED | 2003
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | CAC042AKA5 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA B | SERIAL NUMBER | NA | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-8 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCRA06A2M6A2B4C0 | HEATING CAPACITIES (MBH) | 115 | PRIORITY | 3
LOCATION | ROOF - AREA CY | SERIAL NUMBER | 2316C89900 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-9 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCRA06A2M6A2B4C0 | HEATING CAPACITIES (MBH) | 115 | PRIORITY | 3
LOCATION | ROOF - AREA CY | SERIAL NUMBER | 2316C89901 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-361 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | YCD090C4HCBE | HEATING CAPACITIES (MBH) | 205 | PRIORITY | 1
LOCATION | ROOF - AREA CY | SERIAL NUMBER | M20100767D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | CU-6 | MANUFACTURER | COMFORTMAKER | COOLING CAPACITIES (TONS) | 3.5 | YEAR MANUFACTURED | 2003
EQUIPMENT | CONDENSING UNIT | MODEL NUMBER | CAC042AKA5 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 1
LOCATION | ROOF - AREA CY | SERIAL NUMBER | NA | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-10 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCSA04A1M6A2B4C0 | HEATING CAPACITIES (MBH) | 72 | PRIORITY | 3
LOCATION | ROOF - AREA CY | SERIAL NUMBER | 2316c89877 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-365 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 5 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TCD060C40ABC | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA C | SERIAL NUMBER | M29103336D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-342 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TCD048C40ABC | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA C | SERIAL NUMBER | NA | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-364 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TCD048C40ABC | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA C | SERIAL NUMBER | M29103323D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-362 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TCD048C40ABC | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA C | SERIAL NUMBER | M29103327D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-363 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J03ZJE15U4AZZ10001C | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | ROOF - AREA C | SERIAL NUMBER | N1A0541453 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-370 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TCD048C40ABC | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA D | SERIAL NUMBER | M29101510D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-11 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 1997
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TCD036C40ABC | HEATING CAPACITIES (MBH) | - | PRIORITY | 1
LOCATION | ROOF - AREA E | SERIAL NUMBER | M29103316D | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-12 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 3 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | TSC036E4E0A | HEATING CAPACITIES (MBH) | - | PRIORITY | 3
LOCATION | ROOF - AREA E | SERIAL NUMBER | 101211123L | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-13 | MANUFACTURER | CARRIER | COOLING CAPACITIES (TONS) | 20 | YEAR MANUFACTURED | 2016
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | 48TCTD24A2M6A2B4J0 | HEATING CAPACITIES (MBH) | 400 | PRIORITY | 3
LOCATION | ROOF - AREA I | SERIAL NUMBER | 2416P15941 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-14 | MANUFACTURER | TRANE | COOLING CAPACITIES (TONS) | 20 | YEAR MANUFACTURED | 2014
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | YSD240F4RZA03D6 | HEATING CAPACITIES (MBH) | 400 | PRIORITY | 3
LOCATION | ROOF - AREA J | SERIAL NUMBER | 143010812D | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-15 | MANUFACTURER | AAON | COOLING CAPACITIES (TONS) | 50 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RN-050-3-0-EB09 | HEATING CAPACITIES (MBH) | 540 | PRIORITY | 3
LOCATION | ROOF - AREA Z | SERIAL NUMBER | 201002-BNGW08967 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-16 | MANUFACTURER | AAON | COOLING CAPACITIES (TONS) | 31 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RN-031-3-0-000-3E9 | HEATING CAPACITIES (MBH) | 1080 | PRIORITY | 3
LOCATION | ROOF - AREA S | SERIAL NUMBER | 201002-BNGU08965 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-17 | MANUFACTURER | AAON | COOLING CAPACITIES (TONS) | 31 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RN-031-3-0-000-3E9 | HEATING CAPACITIES (MBH) | 1080 | PRIORITY | 3
LOCATION | ROOF - AREA S | SERIAL NUMBER | 201002-BNGU08966 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-18 | MANUFACTURER | AAON | COOLING CAPACITIES (TONS) | 50 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RN-050-3-0-EA09-000 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA S | SERIAL NUMBER | 201002-BNCW02366 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-19 | MANUFACTURER | AAON | COOLING CAPACITIES (TONS) | 50 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | RN-050-3-0-EA09-000 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA S | SERIAL NUMBER | 201002-BNCW02367 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | RTU-20 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 10 | YEAR MANUFACTURED | 2008
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J10HAC00A4AAA1A | HEATING CAPACITIES (MBH) | - | PRIORITY | 2
LOCATION | ROOF - AREA K | SERIAL NUMBER | (S)N0H8215018 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | RTU-21 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 4 | YEAR MANUFACTURED | 2010
EQUIPMENT | PACKAGED ROOFTOP UNIT | MODEL NUMBER | J04ZJE15U4AZZ10001C | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | ROOF - AREA A | SERIAL NUMBER | N1A0541451 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | KH-1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | KITCHEN HOOD | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION |  | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | HT-1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | UNIT HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION |  | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-A1 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | 20 | YEAR MANUFACTURED | 2009
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | 235 | PRIORITY | 2
LOCATION | A-113 | SERIAL NUMBER | NA | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | AHU-A2 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | 7.5 | YEAR MANUFACTURED | 2009
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | 110 | PRIORITY | 2
LOCATION | A-113 | SERIAL NUMBER | NA | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | B-1 | MANUFACTURER | DE DIETRICH GAS | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2010
EQUIPMENT | BOILER | MODEL NUMBER | GAS 310-5 | HEATING CAPACITIES (MBH) | 1017 | PRIORITY | 3
LOCATION |  | SERIAL NUMBER | 100096730009000027 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-2 | MANUFACTURER | DE DIETRICH GAS | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2010
EQUIPMENT | BOILER | MODEL NUMBER | GAS 310-5 | HEATING CAPACITIES (MBH) | 1017 | PRIORITY | 3
LOCATION |  | SERIAL NUMBER | 100096730009000027 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | B-3 | MANUFACTURER | CAMUS | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2009
EQUIPMENT | BOILER | MODEL NUMBER | DFNH-3001-MHI | HEATING CAPACITIES (MBH) | 3000 | PRIORITY | IMMEDIATE REPAIR
LOCATION |  | SERIAL NUMBER | 110909981 | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | KH-2 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | KITCHEN HOOD | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION |  | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 1
TAG | AHU-D2 | MANUFACTURER | CHANGEAIR | COOLING CAPACITIES (TONS) | 10 | YEAR MANUFACTURED | 1987
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | 135 | PRIORITY | 1
LOCATION | D-126 | SERIAL NUMBER | NA | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | AHU-D1 | MANUFACTURER | YORK | COOLING CAPACITIES (TONS) | 60 | YEAR MANUFACTURED | NA
EQUIPMENT | AIR HANDLING UNIT | MODEL NUMBER | NT1-036X048-BAGA046A | HEATING CAPACITIES (MBH) | NA | PRIORITY | 2
LOCATION | D-201 | SERIAL NUMBER | AHTM XT0113 | REFRIGERATION TYPE | R-22 | QUANTITY | 1
TAG | UV-1 TO UV-2 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | VARIES | YEAR MANUFACTURED | 2003
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | VARIES | PRIORITY | 3
LOCATION |  | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 2
TAG | AC-1 TO AC-3 | MANUFACTURER | PANASONIC | COOLING CAPACITIES (TONS) | 4.5 | YEAR MANUFACTURED | NA
EQUIPMENT | SPLIT SYSTEM | MODEL NUMBER | U-52LE1U6 | HEATING CAPACITIES (MBH) | 52 | PRIORITY | 2
LOCATION | E CLASSROOMS | SERIAL NUMBER | 0002961 | REFRIGERATION TYPE | R-410A | QUANTITY | 1
TAG | UV-3 TO UV-11 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2003
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | E CLASSROOMS | SERIAL NUMBER | NA | REFRIGERATION TYPE | R-22 | QUANTITY | 8
TAG | UV-12 TO UV-15 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | 2003
EQUIPMENT | UNIT VENTILATOR | MODEL NUMBER | U.AZU.5.040.K.G.12.Z.B5.AL.22.G.W.B.2 | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | F CLASSROOMS | SERIAL NUMBER | E747933050 | REFRIGERATION TYPE | R-22 | QUANTITY | 4
TAG | HT-2 TO HT-3 | MANUFACTURER | NA | COOLING CAPACITIES (TONS) | NA | YEAR MANUFACTURED | NA
EQUIPMENT | UNIT HEATER | MODEL NUMBER | NA | HEATING CAPACITIES (MBH) | NA | PRIORITY | 3
LOCATION | VESTIBULES | SERIAL NUMBER | NA | REFRIGERATION TYPE | NA | QUANTITY | 3

## ALL MECHANICAL
COAL CITY SCHOOLS
Facility Equipment List - Mechanical
BUILDING | EQUIPMENT | LOCATION | TAG | MANUFACTURER | MODEL NUMBER | SERIAL NUMBER | COOLING CAPACITIES (Tons) | HEATING CAPACITIES (MBH) | YEAR MANUFACTURED | REFRIGERANT TYPE | NOTES
HIGH SCHOOL
| PACKAGED ROOFTOP UNIT | ROOF - AREA O | RTU-1 | CARRIER | 48TCTD28A2M6A2B4J0 | 2416P15949 | 25 | 400 | 2016 | R-410A
| CONDENSING UNIT | ROOF - AREA O | CU-1 | HEATCRAFT | MOZ045L63CF | T10D05574 | 1 | - | 2010 | R-404A
| CONDENSING UNIT | ROOF - AREA O | CU-2 | TRANE | RAUCC204BX03A0DF | C03B01213 | 20 | - | 2003 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA O | RTU-2 | YORK | J07HAC00A4AAA1A | (S)N0H8226938 | 7.5 | - | 2008 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA O | RTU-3 | YORK | J07ZHN15Q4AZZ50001A | N1A0548042 | 7.5 | 180 | 2010 | R-410A
| MAKEUP AIR UNIT | ROOF - AREA O | MAU-1 | BANANZA | B650 | 0912650.8 | - | 540 | 2009 | -
| MAKEUP AIR UNIT | ROOF - AREA O | MAU-2 | BANANZA | B650 | 09102650.7 | - | 648 | 2009 | -
| PACKAGED ROOFTOP UNIT | ROOF - AREA N | RTU-4 | YORK | J25ZJC00Q4AZZ10007B | N1A0538170 | 25 | - | 2010 | R-410A
| EXHAUST FAN | ROOF | EF-1 TO EF-25 | CARNES | VEBK08L#A1UA108PC1 | 652401.003 | - | - | 2009 | - | 115 V @ 1/4 HP
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-5 | CARRIER | 48A3S025-NM62AFP | 2616U47654 | 25 | 350 | 2016 | R-410A
| CONDENSING UNIT | ROOF - AREA H | CU-3 | TRANE | RAUCC604BX03A0DF | C03B01214 | 60 | - | 2003 | R-22 | Abandoned
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-6 | CARRIER | 50TJ-016-681AA | 2602F63551 | 15 | - | 2002 | R-22 | W/ Electric Duct Heater
| CONDENSING UNIT | ROOF - AREA B | CU-4 | COMFORTMAKER | CAC042AKA5 | E031431563 | 3.5 | - | 2003 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-340 | YORK | J05ZJE1504AZZ100031C | N1A0538198 | 5 | NA | 2010 | R-410A | LABEL PARTIALLY HIDDEN
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-7 | YORK | J03ZJE07U4AZZ10002 | N1A0541452 | 3 | NA | 2010 | R-410A | LABEL PARTIALLY HIDDEN
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-341 | TRANE | TCD048C40ABC | M29103326D | 4 | - | 1997 | R-22
| CONDENSING UNIT | ROOF - AREA B | CU-5 | COMFORTMAKER | CAC042AKA5 | NA | 3.5 | - | 2003 | R-22 | LABEL NOT VISIBLE
| PACKAGED ROOFTOP UNIT | ROOF - AREA CY | RTU-8 | CARRIER | 48TCRA06A2M6A2B4C0 | 2316C89900 | 5 | 115 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA CY | RTU-9 | CARRIER | 48TCRA06A2M6A2B4C0 | 2316C89901 | 5 | 115 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA CY | RTU-361 | TRANE | YCD090C4HCBE | M20100767D | 7.5 | 205 | 1997 | R-22
| CONDENSING UNIT | ROOF - AREA CY | CU-6 | COMFORTMAKER | CAC042AKA5 | NA | 3.5 | - | 2003 | R-22 | LABEL NOT VISIBLE
| PACKAGED ROOFTOP UNIT | ROOF - AREA CY | RTU-10 | CARRIER | 48TCSA04A1M6A2B4C0 | 2316c89877 | 3 | 72 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-365 | TRANE | TCD060C40ABC | M29103336D | 5 | - | 1997 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-342 | TRANE | TCD048C40ABC | NA | 4 | - | 1997 | R-22 | LABEL PARTIALLY HIDDEN
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-364 | TRANE | TCD048C40ABC | M29103323D | 4 | - | 1997 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-362 | TRANE | TCD048C40ABC | M29103327D | 4 | - | 1997 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-363 | YORK | J03ZJE15U4AZZ10001C | N1A0541453 | 3 | NA | 2010 | R-410A | LABEL PARTIALLY HIDDEN
| PACKAGED ROOFTOP UNIT | ROOF - AREA D | RTU-370 | TRANE | TCD048C40ABC | M29101510D | 4 | - | 1997 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA E | RTU-11 | TRANE | TCD036C40ABC | M29103316D | 3 | - | 1997 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA E | RTU-12 | TRANE | TSC036E4E0A | 101211123L | 3 | - | 2010 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA I | RTU-13 | CARRIER | 48TCTD24A2M6A2B4J0 | 2416P15941 | 20 | 400 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA J | RTU-14 | TRANE | YSD240F4RZA03D6 | 143010812D | 20 | 400 | 2014 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA Z | RTU-15 | AAON | RN-050-3-0-EB09 | 201002-BNGW08967 | 50 | 540 | 2010 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA S | RTU-16 | AAON | RN-031-3-0-000-3E9 | 201002-BNGU08965 | 31 | 1080 | 2010 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA S | RTU-17 | AAON | RN-031-3-0-000-3E9 | 201002-BNGU08966 | 31 | 1080 | 2010 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA S | RTU-18 | AAON | RN-050-3-0-EA09-000 | 201002-BNCW02366 | 50 | NA | 2010 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA S | RTU-19 | AAON | RN-050-3-0-EA09-000 | 201002-BNCW02367 | 50 | NA | 2010 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA K | RTU-20 | YORK | J10HAC00A4AAA1A | (S)N0H8215018 | 10 | - | 2008 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-21 | YORK | J04ZJE15U4AZZ10001C | N1A0541451 | 4 | NA | 2010 | R-410A | LABEL PARTIALLY HIDDEN
| KITCHEN HOOD | A-108 | KH-1 | NA | NA | NA | - | - | NA | - | LABEL NOT VISIBLE
| UNIT HEATER | A-111 | HT-1 | NA | NA | NA | - | NA | NA | - | LABEL NOT VISIBLE
| AIR HANDLING UNIT | A-118 | AHU-1 | NA | NA | NA | - | - | NA | NA | LABEL NOT VISIBLE
| AIR HANDLING UNIT | A-118 | AHU-2 | NA | NA | NA | - | - | NA | NA | LABEL NOT VISIBLE
| BOILER | A-118 | B-1 | DE DIETRICH GAS | GAS 310-5 | 100096730009000027 | NA | 1017 | 2010 | -
| BOILER | A-118 | B-2 | DE DIETRICH GAS | GAS 310-5 | 100096730009000027 | NA | 1017 | 2010 | -
| BOILER | A-118 | B-3 | CAMUS | DFNH-3001-MHI | 110909981 | NA | 3000 | 2009 | - | CANNOT FIRE
| KITCHEN HOOD | A-119 | KH-2 | NA | NA | NA | - | - | NA | - | LABEL NOT VISIBLE
| AIR HANDLING UNIT | B-142 | AHU-3 | CHANGEAIR | NA | NA | NA | NA | NA | NA | VERTICAL AHU, LABEL NV
| AIR HANDLING UNIT | D-126 | AHU-4 | YORK | NT1-036X048-BAGA046A | AHTM XT0113 | - | - | 1987 | R-12 | POSSIBLE USE OF CFCs
| UNIT VENTILATOR | LOCKER ROOMS | UV-1 TO UV-2 | NA | NA | NA | NA | NA | 2003 | R-22 | LABEL NOT VISIBLE
| SPLIT SYSTEM | E CLASSROOMS | AC-1 TO AC-3 | PANASONIC | U-52LE1U6 | 0002961 | 4.5 | 52 | NA | R-410A | INDOOR UNIT LABEL NV
| UNIT VENTILATOR | E CLASSROOMS | UV-3 TO UV-11 | NA | NA | NA | NA | NA | 2003 | R-22 | LABEL NOT VISIBLE
| UNIT VENTILATOR | F CLASSROOMS | UV-12 TO UV-15 | NA | U.AZU.5.040.K.G.12.Z.B5.AL.22.G.W.B.2 | E747933050 | NA | NA | 2003 | R-22 | LABEL PARTIALLY HIDDEN
| UNIT HEATER | VESTIBULES | HT-2 TO HT-3 | NA | NA | NA | NA | NA | NA | NA | LABEL NOT VISIBLE
INTERMEDIATE
| EXHAUST FAN | ROOF | EF-1 TO EF-7 | NA | NA | NA | - | - | NA | NA | LABEL NOT VISIBLE
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-782 | CARRIER | 48PDMC05-M-50-B3 | 3409G40009 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-783 | CARRIER | 48PDMC05-M-50-B3 | 3409G40013 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-3 | VALENT | VPRX-350-50E-60I-A-1DX | 13298893 | 45 | - | 2013 | R-410A | BACKUP HEAT ONLY
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-4 | VALENT | VPRX-350-40E-90I-A-4DX | 13298894 | 45 | NA | 2013 | R-410A | DENNY HAS HEAT INFO
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-5 | VALENT | VPRX-350-50E-60I-A-1DX | 13298895 | 45 | - | 2013 | R-410A | BACKUP HEAT ONLY
| PACKAGED ROOFTOP UNIT | ROOF - AREA E | RTU-798 | CARRIER | 48PDMC05-M-50-B3 | 3409G50002 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA F | RTU-788 | CARRIER | 48PDMC05-M-50-B3 | 3409G50015 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-2 | VALENT | VPRX-350-30E-60I-A-4DX | 13298856 | 45 | - | 2013 | R-410A | BACKUP HEAT ONLY
| PACKAGED ROOFTOP UNIT | ROOF - AREA M | RTU-6 | TRANE | YSC120F3RZA0BD6 | 143113028L | 10 | 250 | 2014 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA I | RTU-1 | STERLING | M1P-PV80A6G03M53S5QB5L4 | E1301224870001001 | - | 800 | 2013 | R-410A
| CONDENSING UNIT | ROOF - SOUTH | CU-1 | HEATCRAFT | NA | NA | NA | - | NA | NA | LABEL NOT VISIBLE
| CONDENSING UNIT | ROOF - SOUTH | CU-2 | HEATCRAFT | LHT030X6CFM | T16D08845 | 3 HP | - | 2016 | R-404A
| BOILER | 22A | B-1 | AERCO | BENCHMARK 2.0LN | G-13-0903 | - | 1500 | 2013 | -
| BOILER | 22A | B-2 | AERCO | BENCHMARK 2.0LN | G-13-0903 | - | 1500 | 2013 | -
| CABINET WALL HEATER | NE STAIRS | HT-1 | NA | NA | NA | - | NA | NA | NA | LABEL NOT VISIBLE
| FURNACE | 44B | F-2 | JACKSON & CHURCH | SDF25-GMSH-MB-RH | B92-479 | - | 313 | NA | NA | LABEL PARTIALLY HIDDEN
| KITCHEN HOOD | 44C | KH-1 | NA | NA | NA | - | - | NA | - | LABEL NOT VISIBLE
MIDDLE
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS6 | CARRIER | 48TCSA06A2M6A2B4C0 | 2316C89903 | 5 | 72 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS7 | CARRIER | 48TCSA06A2M6A2B4C0 | 2316C89902 | 5 | 72 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS1 | CARRIER | 48TCRD12A2M6A2A4J0 | 2316P96897 | 10 | 224 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS8 | CARRIER | 48LCSB14A7M6A1B4C0 | 2416P15930 | 12.5 | 176 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS5 | CARRIER | 48TCSA05A2M6A2A4C0 | 2316C89894 | 4 | 72 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS2 | CARRIER | 48TCRD12A2M6A2A4J0 | 2316P96896 | 10 | 224 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS3 | CARRIER | 48TCRD12A2M6A2A4J0 | 2316P96895 | 10 | 224 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-MS4 | CARRIER | 48TCRD08A2M62A4J0 | 2316P96847 | 7.5 | NA | 2016 | NA | LABEL PARTIALLY HIDDEN
| EXHAUST FAN | ROOF - AREA B | EF-1 | TWIN CITY | DCRD130BE1 | E16-000000183573 | - | - | NA | -
| CHILLER | GRADE - EAST B | CH-1 | TRANE | RTAA3004XT0IA3D0BFGKM | U00006706 | 300 | - | 2006 | R-22
| UNIT VENTILATOR | CLASSROOMS | UV-1 TO UV- | NA | MAUVF411AFB223X0M1AAALAXA1A | W160789057 | NA | NA | 2016 | R-410A | LABEL PARTIALLY HIDDEN
| KITCHEN HOOD | KITCHEN 127 | KH-1 | NA | NA | NA | - | - | NA | - | LABEL NOT VISIBLE
| UNIT HEATER | CORRIDOR 130 | HT-1 | NA | NA | NA | - | NA | NA | - | LABEL NOT VISIBLE
| CABINET WALL HEATER | CORRIDOR 300C | HT-2 | NA | NA | NA | - | NA | NA | - | LABEL NOT VISIBLE
| AIR HANDLING UNIT | MECHANICAL 401 | AHU-6 | TRANE | MCCA014BBJ0B0CA | K99H50329N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 401 | AHU-5B | TRANE | MCCA014GAW0ABA | K99H50318N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 400 | AHU-5A | TRANE | MCCA014GAW0ABA | K99H50303N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 400 | AHU-4 | TRANE | MCCA008ABH0B0A | K99H50368N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 402 | AHU-1 | TRANE | MCCA030GAW0AAA | K99H50258N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 402 | AHU-2A | TRANE | MCCA025GAW0ABA | K99H50266N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 402 | AHU-2B | TRANE | MCCA025GAW0ABA | K99H50279N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 402 | AHU-3 | TRANE | MCCA021UB000A | K99H50284N | - | - | 1999 | R-22
| AIR HANDLING UNIT | MECHANICAL 402 | AHU-8 | TRANE | MCCA006GAW0AAA | K99H50377N | - | - | 1999 | R-22
| BOILER | MECHANICAL 402 | B-1 | LOCHINVAR | FBN2500 | 1608102642359 | - | 2500 | 2016 | -
| BOILER | MECHANICAL 402 | B-2 | LOCHINVAR | FBN2500 | 1608102642361 | - | 2500 | 2016 | -
| BOILER | MECHANICAL 402 | B-3 | LOCHINVAR | CHN1802 | H14H00267368 | - | 1800 | 2014 | -
| UNIT HEATER | MECHANICAL 402 | HT-3 | NA | NA | NA | - | NA | NA | - | LABEL NOT RECORDED
ELEMENTARY
| CONDENSING UNIT | ROOF - AREA J | CU-1 | LENNOX | TSA048S4N43Y | 5813E18197 | 4 | - | 2013 | R-410A
| CONDENSING UNIT | ROOF - AREA J | CU-7 | LENNOX | TSA048S4N43Y | 5813D19857 | 4 | - | 2013 | R-410A
| CONDENSING UNIT | ROOF - AREA J | CU-2 | LENNOX | TSA048S4N43Y | 5812K06335 | 4 | - | 2012 | R-410A
| CONDENSING UNIT | ROOF - AREA J | CU-6 | LENNOX | TSA048S4N43Y | 5812H07822 | 4 | - | 2012 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA J | RTU-702 | CARRIER | 48SS-018040311 | 0395G10185 | 1.5 | 40 | 1995 | R-22
| CONDENSING UNIT | ROOF - AREA J | CU-4 | LENNOX | TSA048S4N43Y | 5813D19870 | 4 | - | 2013 | R-410A
| CONDENSING UNIT | ROOF - AREA J | CU-5 | LENNOX | TSA048S4N43Y | 5812M00701 | 4 | - | 2012 | R-410A
| EXHAUST FAN | ROOF | EF-1 TO EF-6 | NA | NA | NA | - | - | NA | - | LABEL NOT VISIBLE
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-707 | CARRIER | 48PDMC05-M-50-B3 | 3409G50005 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-723 | CARRIER | 48PDMC05-M-50-B3 | 3409G40010 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-720 | CARRIER | 48PDMC05-M-50-B3 | 3409G50001 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-768 | CARRIER | 48PDMC05-M-50-B3 | 3409G40011 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-1 | STERLING | E1G-RT15C6C01K42J2AB3ABE3H | H0230526_ | - | 150 | 2002 | R-22 | LABEL PARTIALLY HIDDEN
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-718 | CARRIER | 48PDMC05-M-50-B3 | 3409G50004 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-719 | CARRIER | 48PDMC05-M-50-B3 | 3409G40014 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-716 | CARRIER | 48PDMC05-M-50-B3 | 3409G50003 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA H | RTU-717 | CARRIER | 48PDMC05-M-50-B3 | 3409G40012 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA I | RTU-767 | CARRIER | 48TCRD08A2M5A0B5F0 | 2815P82332 | 7.5 | 180 | 2015 | R-410A
| SPLIT SYSTEM HEAT PUMP | ROOF - AREA I | HP-1 | MITSUBISHI | MXZ-3C30NAHZ | 4ZP01296 | 2.5 | - | 2014 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-721 | CARRIER | 48ES-018040301TP | 0509G50711 | 1.5 | 40 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-7 | CARRIER | 48PDMC05-M-50-B3 | 3409G50006 | 4 | 75 | 2009 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-715 | CARRIER | 48TCTD25A6M5A2B4J0 | 2416P15955 | 20 | 400 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-714 | CARRIER | 48TCSA06A2A5A2F0C0 | 2313C86152 | 5 | 72 | 2013 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-2 | STERLING | E1G-RT15C6C01K42J2AB3ABE3H | H02305261 | - | 150 | 2002 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-713 | CARRIER | 48TCSA06A2A5A2F0C0 | 2313C86156 | 5 | 72 | 2013 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-712 | CARRIER | 48TCSA06A2A5A2F0C0 | 2313C86154 | 5 | 72 | 2013 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-711 | CARRIER | 48TCSA06A2A5A2F0C0 | 2313C86153 | 5 | 72 | 2013 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-710 | CARRIER | 48TCSA06A2A5A2F0C0 | 2313C86151 | 5 | 72 | 2013 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-708 | CARRIER | 48TCSA06A2A5A2F0C0 | 2313C86157 | 5 | 72 | 2013 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA G | RTU-709 | CARRIER | 48TCSA06A2A5A2F0C0 | 2313C86155 | 5 | 72 | 2013 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA D | RTU-769 | TRANE | YCD090C3HABE | N31104515D | 7.5 | 205 | 1998 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA D | RTU-770 | TRANE | YCD090C3HABE | N31101570D | 7.5 | 205 | 1998 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-685 | CARRIER | 48TCSA04A1M5A2B4C0 | 2316C89875 | 3 | 72 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-686 | CARRIER | 48TCSA04A1M5A2B4C0 | 2316C89872 | 3 | 72 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-6 | CARRIER | 48TCSA04A1M5A2B4C0 | 2316C89874 | 3 | 72 | 2016 | R-410A
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-696 | CARRIER | 48TCSA04A1M5A2B4C0 | 2316C89873 | 3 | 72 | 2016 | R-410A
| CONDENSING UNIT | ROOF - AREA F | CU-8 | HEATCRAFT | LHT015X68 | T09H02993 | 1.5 HP | - | 2009 | R-404A
| CONDENSING UNIT | ROOF - AREA F | CU-9 | HEATCRAFT | LZT030L6C | T09H02994 | 3 HP | - | 2009 | R-404A
| UNIT VENTILATOR | CLASSROOMS | UV-1 TO UV-18 | UL | U.AVS.6.S15.A.G.66.A.17.AL.22.GBB1 | AUBU132901612 | - | - | 2013 | R-410A
| SPLIT SYSTEM AC UNIT | A-120 | AC-1 | SANYO | K1812W | 0168304 | 1 | - | 1990 | R-22
| SPLIT SYSTEM AC UNIT | A-119 | AC-2 | SANYO | K1812W | 0168204 | 1 | - | 1990 | R-22
| SPLIT SYSTEM AC UNIT | A-118 | AC-3 | SANYO | K1812W | 0168104 | 1 | - | 1990 | R-22
| BOILER | A-157 | B-1 | LOCHINVAR | FBN1251 | 1619102945534 | - | 1250 | 2015 | -
| BOILER | A-157 | B-2 | LOCHINVAR | FBN1251 | 1619102945535 | - | 1250 | 2015 | -
EARLY CHILDHOOD
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-1 | MCQUAY | RPS030CLY | FBOU071200365 | 32 | - | 2007 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA A | RTU-2 | MCQUAY | RPS060CSY | FBOU071200013 | 66 | - | 2007 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA C | RTU-3 | MCQUAY | RPS060CSY | FBOU071200363 | 66 | - | 2007 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-4 | MCQUAY | MPS003AYCK | 7368F140705639 | 3 | - | 2007 | R-22
| PACKAGED ROOFTOP UNIT | ROOF - AREA B | RTU-5 | MCQUAY | RPS045CSY | FBOU071200364 | 46 | - | 2007 | R-22
| EXHAUST FAN | ROOF | EF-1 TO EF-5 | GREENHECK | CUBE-131-5-X | 111649120801 | - | - | NA | - | LABEL PARTIALLY HIDDEN
| RADON FAN | ROOF | RF-1 TO RF-3 | FANTECH | FR250 | 2374724 | - | - | 2016 | -
| BOILER | B-118 | B-1 | AERCO | BMK2.0 | G-08-0022 | - | 1500 | 2008 | -
| BOILER | B-118 | B-2 | AERCO | BMK2.0 | G-08-0023 | - | 1500 | 2008 | -
| UNIT HEATER | B-118 | HT-1 | NA | NA | NA | - | NA | NA | - | LABEL NOT VISIBLE
| KITCHEN HOOD | B-133 | KH-1 | GREENHECK | NA | NA | - | - | NA | - | LABEL NOT VISIBLE
| WALL CABINET HEATER | VESTIBULES | HT-2 | NA | NA | NA | - | - | NA | - | LABEL NOT VISIBLE