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	DISTRICT PROGRAM FOR DEVELOPMENT AND IMPLIMENTATION OF PROCESSES TO BE USED IN SAINT PAUL PUBLIC SCHOOLS OPERATIONS
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Eye Wash Stations and Safety Showers
The Occupational Safety and Health Administration (OSHA) regulates emergency eyewash station and safety shower equipment designed to promote eye and body safety under certain work conditions. OSHA's general regulation is applicable to all facilities that require the installation of an emergency shower or eyewash station equipment as a form of first aid. Subpart K 29 CFR 1910.151 (c). It states that:
"Where the eyes or body of any person may be exposed to injurious corrosive materials, suitable facilities for quick drenching or flushing of the eyes and body shall be provided within the work area for immediate emergency use." 

[bookmark: _Toc510159405][bookmark: _Toc510159870]The Eyewash Station and Safety Shower written plan is designed to comply to Subpart K 29 CFR 1910.151(c). 































OBJECTIVE

Example: The objective of the Saint Paul School District Eyewash Station and Safety Shower Standard Operating Procedure (SOP) is to ensure the working operation of eyewash stations and safety showers.  A copy of this SOP will be maintained by all affected departments. 
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Environmental Services Group (ESG)

· Develop and carry out the provisions of the Eyewash Station and Safety Shower written plan.
· Keep records of eyewash station testing and update annually.  
· Keep records of safety shower testing and update annually.  
· Ensure all eyewash stations and safety showers are audited annually by an SPPS licensed plumber.
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Employees

· It is recommended that anyone who is required to use caustic or corrosive chemicals is familiar with how to operate the eyewash station and or safety shower.
· It is recommended that eyewash stations/safety showers are checked on a weekly basis to ensure their functionality throughout the year.  In leu of weekly checks by staff, ESG staff and Custodial staff will conduct spot checks
· Communicate with your Head Engineer any fixes needed to the eyewash station/safety shower.  They will submit a TMA work order for repair.
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Eye Wash Station Design

Heads
· Positioned 33"—45" from floor
· Positioned 6" from wall or nearest obstruction
· 0.4 gallons per minute (GPM) for 15 minutes for plumbed units shall provide flushing fluid at 30 PSI
· 0.4 gallons per minute (GPM) for 15 minutes for gravity-feed units
Valves
· Activate in 1 second or less
· Stay-open valve (leaving hands free)
Installation
· Eye wash station shall be located in an area that requires no more than 10 seconds to reach when caustic/corrosive materials are being used. The location of the eye wash station shall be in a well-lit area and identified with a sign
· Eye wash stations shall be on the same level as the hazard
Maintenance, Training, and Testing
It is recommended that an eyewash station and safety shower be activated once a week to verify proper operation.  In leu of weekly checks by staff, ESG staff and Custodial staff will conduct spot checks 
· When testing an eyewash station and safety shower:
· Equipment should be installed within 10 second from the hazard and on the same plane as the hazard
· Pathway is clear of obstructions
· Water is fully turned on – water is clear and free of sediment
· Water is room temperature
· Water Pressure is adequate
· Equipment is free of broken or missing parts
· Equipment is protected against freezing
· User is protected from scalding water
· Gravity-feed units shall be maintained according to the manufacturer's instructions
· All employees who might be exposed to a chemical splash shall be trained in the use of the equipment, this training is covered in Employee Right to Know (ERTK)
· All eye/face wash stations shall be inspected annually a licensed plumber.  These records are kept in a digital database and managed by Facilities.
· For those stations without a plumbed drain, a five-gallon bucket can be used to collect the wash water.
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Recordkeeping requirements outlined in Eyewash Station and Safety Shower written plan shall be maintained by ESG and available upon request or on the District Facilities Department web site.
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Any questions, concerns, comments, or other information regarding the District Eyewash Station and Safety Shower Program can be directed to:

· The Environmental Services Group
· Phone: 651.744.1800
· Email: ESG@spps.org
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· 29 CFR 1910 OSHA General Industry Regulations & Standards: January 2018.  Mancomm, Inc.  Davenport, IA.
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