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	DISTRICT PROGRAM FOR DEVELOPMENT AND IMPLIMENTATION OF PROCESSES TO BE USED IN SAINT PAUL PUBLIC SCHOOLS OPERATIONS
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PURPOSE

AHERA Management Plan
40 CFR 763


The following program name is provided as a guide to assist administration and staff employees of Saint Paul Public Schools in complying with the requirements of EPA’s Asbestos Hazard Emergency Response Act (AHERA) Standard, 40 CFR 763, Subparts 763.80 through 763.179, and OSHA 29 CFR 1910.1001 Asbestos Standard. It also provides other helpful information. The Management Plan is not intended to supersede the requirements of the standard.  

The District Environmental Services Group (ESG) will review the standard annually for particular requirements that are applicable to the District, and adjust this program accordingly.  

This written plan is designed to be specific to the needs of users of Saint Paul Public Schools and is intended to comply with the following Asbestos Standards: EPA 40 CFR 763, Subparts 763.80 through 763.179, with the main focus given to 40 CFR Subpart E—Asbestos-Containing Materials in Schools. Reference is also made to OSHA’s Asbestos Standard, 29 CFR 1910.1001*. 

If there are conflicts or discrepancies between this plan and the standard, the standard shall take precedence.





*Note: This written plan incorporates some exposure to asbestos in construction work. The complete construction standard is covered by 29 CFR 1926.1101.
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ACBM	Asbestos Containing Building Materials.

ACM	Asbestos containing material when referring to school buildings means any material or product which contains more than 1% asbestos.

Accessible	When referring to ACM means that the material is subject to disturbance by school building occupants or custodial or maintenance personnel in the course of their normal activities.

AHERA	Asbestos Hazardous Emergency Response Act.

Debris	Asbestos debris means pieces of ACBM that can be identified by color, texture or composition, or means dust, if the dust is determined by an accredited inspector to be ACM.

Encapsulation	Means the treatment of ACBM with a material that surrounds or embeds asbestos fibers in an adhesive matrix to prevent the release of fibers, as the encapsulant creates a membrane over the surface (bridging encapsulant) or penetrates the material and binds its components together (penetrating encapsulant). 

Enclosure	Means an air tight, impermeable, permanent barrier around ACBM to prevent the release of asbestos fibers into the air.

EPA	Environmental Protection Agency.

Fiber Release	Means any uncontrolled or unintentional disturbance of ACBM resulting in visible emission.

Friable	When referring to materials in a school building means that the material, when dry, may be crumbled, pulverized, or reduced to powder by hand pressure.

Functional Space	Means a room, group of rooms or homogenous area (including crawl spaces, spaces above ceilings), such as classroom(s), a cafeteria, gymnasium, hallway(s), designated by a person accredited to prepare management plans, design abatement projects, or conduct response actions.

LEA Designated Person	The individual designated by the local education agency to ensure that requirements under specific sections of plan are properly implemented.

Mastic	A glue or tar that is used to adhere items to a surface.
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OBJECTIVE

The purpose of the Saint Paul School District AHERA Management Plan is to comply with 40 CFR 763 Asbestos Hazard Emergency Response Act (AHERA) with specific focus given to 40 CFR Subpart E—Asbestos-Containing Materials in Schools. The intent is to reduce asbestos exposures in schools by identifying asbestos containing building materials (ACBM), assessing the hazards of these materials, and implementing policies and procedures to eliminate and/or minimize these hazards.

The key elements of this plan are identification, management, notification, and training.  What follows is a compliance document to ensure the implementation and compliance with the AHERA regulations and the intent to reduce/eliminate asbestos exposures.


CONTENTS OF THE MANAGEMENT PLAN

· General Information
· List of names and addresses of all school buildings
· Whether buildings contain ACBM and if the ACBM is friable

· Designated person Information
· Name, address and telephone number of the LEA Designated Person
· Documentation of training of Designated Person
· Truth Statement

· Inspection Information
· Third Year Reinspection requirements
· A plan for Periodic Surveillance Activities under 763.92

· Management Plan Information
· Response Action Information
· Remaining Asbestos Locations

· A Plan for operations and maintenance activities (O&M) under 763.91.

· Short Term Worker Notifications

· Annual Staff and Student or Parental Guardian Notification

· Recordkeeping Requirements
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[bookmark: _Toc510159407][bookmark: _Toc510159872]Management
District Administration
· Provide overall support and involvement in the program.
· Review the specification outlined in this written program that cover the employee/worker notification requirements under 763.84, and insert them in all employment contract documents for workers, including short-term workers, with potential exposure to ACBM.

Environmental Services Group (ESG)
· Use engineering and administrative controls to limit employee exposure.
· Monitor and ensure that required inspections and reinspections are performed per the schedule outlined in this written program.
· Once every 3 years conduct a reinspection in each building that it leases, owns, or otherwise uses as a school building that contains ACBM or is assumed to contain ACBM.
· At least once every 6 months conduct periodic surveillance in each building that it leases, owns, or otherwise uses as a school building that contains ACBM or is assumed to contain ACBM. 
· Review and make appropriate asbestos related response decisions in collaboration with the district’s environmental consultant and the LEA Designated Person.
· Ensure that the required building inspection reports are available on the district’s web site and available to the public and contractors.
· Provide required training for any employee, including short-term workers, with potential exposure to ACBM and maintain documentation of such training. 
· Provide employees with appropriate Personal Protective Equipment (PPE) and other controls.
· Annually inform employees, parents/guardians of students, and school visitors about inspections, reinspections, response actions, and post-response activities.
· Annually review OSHA, EPA, and industry data; update this program as needed.

[bookmark: _Toc510159408][bookmark: _Toc510159873]Staff
Employees
· Follow the work practices described in this document, including the use of appropriate PPE and controls.
· Attend all training required relative to this program.
· Assist, as needed, the LEA Designated Person, accredited inspector, or others with inspections, reinspections, or response actions and activities.
· Report hazardous conditions or other health and safety concerns immediately to their supervisors/foremen/project managers.
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[bookmark: _Toc353525401]Listing of School Buildings
	Building Name
	Address
	Friable
	Nonfriable
	Friable
	Nonfriable

	 
	 
	ACBM
	ACBM
	Assume
	Assumed

	271 Belvidere St
	271 Belvidere St
	X
	X
	X
	X

	Adams Spanish Immersion Magnet
	615 S Chatsworth
	X
	X
	
	X

	Administration Building
	360 Colborne
	X
	X
	X
	X

	AGAPE High School
	1037 University Ave
	
	X
	
	X

	American Indian Magnet School
	1075 E Third St
	
	X
	
	X

	Community Education
	1780 W Seventh St
	
	
	
	

	Barack & Michelle Obama Elementary
	707 Holly Ave
	X
	X
	
	X

	Battle Creek Elementary School
	60 S Ruth St
	
	X
	
	X

	Battle Creek Middle School
	 2121 N Park Dr
	X
	X
	
	X

	Benjamin E Mays Int’l Magnet
	560 Concordia Ave
	
	
	
	

	Bridge View School
	350 Colborne
	X
	X
	X
	X

	Bruce F. Vento Elementary
	409 E Case Ave
	X
	X
	
	X

	Capitol Hill Magnet
	560 Concordia Ave
	
	
	
	

	Chester St Bus Garage
	261 Chester
	
	
	
	

	Central Senior High School
	275 N Lexington Pkwy
	X
	X
	
	X

	Central Service Station
	1157 Selby Avenue
	
	X
	
	X

	Chelsea Heights Elementary
	1557 Huron St
	
	X
	
	X

	Cherokee Heights Elementary School
	694 Charlton St
	X
	X
	
	X

	Como Park Elementary
	780 W Wheelock Pkwy
	X
	X
	X
	X

	Como Park Senior High School
	740 W Rose Ave
	X
	X
	
	X

	Creative Arts High School
	65 E Kellogg Blvd
	X
	X
	
	X

	Crossroads Montessori School
	543 Front Ave
	
	
	
	

	ESTEM Middle School
	600 Weir Dr
	
	
	
	

	Dayton's Bluff Achievement Plus Elementary
	262 Bates Ave
	X
	X
	
	X

	District Service Facility
	1930 Como Ave
	X
	X
	X
	X

	Eastern Heights Elementary
	2001 Margaret St
	X
	X
	X
	X

	EXPO for Excellence Elementary
	540 Warwick St
	X
	X
	
	X

	Farnsworth Aerospace (Lower K-4)
	1290 Arcade St
	
	X
	
	X

	Farnsworth Aerospace (Upper 5-8)
	1000 Walsh  St
	
	X
	
	X

	Focus Beyond
	340 Colborne
	X
	X
	X
	X

	Four Seasons A+ Elementary
	318 Moore St
	
	X
	
	X

	Frost Lake Elementary School
	1505 E Hoyt Ave
	X
	X
	
	X

	Early Childhood Hub West
	1317 Charles Ave
	
	X
	X
	X

	Global Arts Plus - Lower (Linwood PK-5)
	1023 Osceloa Ave
	X
	X
	X
	X

	Global Arts Plus - Upper (Monroe 6-8)
	810 Palace Ave
	X
	X
	X
	X

	Gordon Parks High School
	1212 University Ave
	
	
	
	

	Groveland Park Elementary
	2045 St Clair Ave
	
	X
	X
	X

	Hamline Elementary
	1599 Englewood Ave
	
	X
	
	X

	Harding Senior High School
	1540 E Sixth St
	X
	X
	X
	X

	Hazel Park Preparatory Academy
	1140 White Bear Ave
	X
	X
	
	X

	Hidden River Middle School
	1700 Summit Ave
	X
	X
	X
	X

	Highland Park Elementary
	1700 Saunders Ave
	X
	X
	
	X

	Highland Park Middle School
	975 Snelling Ave S
	
	
	
	

	Highland Park High School (Complex)
	1015 S Snelling Ave
	X
	X
	
	X

	Highwood Hills Elementary
	2188 Londin Ln
	
	X
	X
	X

	Horace Mann Elementary
	2001 Eleanor Ave
	X
	X
	
	X

	Hubbs Center for Lifelong Learning
	1030 University Ave
	
	
	
	

	Humboldt High School
	30 E Baker St
	X
	X
	X
	X

	JJ Hill Montessori
	998 Selby Ave
	
	X
	
	X

	Jackson Elementary
	437 Edmund Ave
	
	X
	
	X

	Jie Ming Mandarin Immersion Academy
	1845 Sheridan Ave
	
	
	
	

	John A Johnson Achievement Plus Elementary
	740 York Avenue
	
	X
	X
	X

	Johnson Aerospace & Engineering High School
	1349 Arcade St
	X
	X
	X
	X

	Journeys Secondary
	90 Western Ave S
	
	X
	
	X

	Wilson
	631 N Albert St
	X
	X
	X
	X

	L'Etoile Du Nord French Immersion Lower Campus
	1305 Prosperity Ave
	X
	X
	
	X

	L'Etoile Du Nord French Immersion Upper Campus
	1760 Ames Pl
	X
	X
	
	X

	Maxfield Elementary
	380 N Victoria St
	
	X
	
	X

	Mississippi Creative Arts School
	1575 L' Orient St
	X
	X
	X
	X

	Murray Middle School
	2200 Buford Ave
	X
	X
	X
	X

	Nokomis Montessori School North
	985 Ruth St
	X
	X
	
	X

	Nokomis Montessori School South
	525 White Bear Ave N
	
	X
	
	X

	Open World Learning
	30 E Baker St
	X
	X
	X
	X

	Txuj Ci Upper HMong Language and Culture
	1363 Bush Ave
	X
	X
	X
	X

	Txuj Ci Lower HMong Language and Culture
	1089 Cypress St
	
	X
	
	X

	Randolph Heights Elementary
	348 S Hamline Ave
	
	X
	
	X

	RiverEast School
	1055 Mackubin St
	X
	X
	
	X

	Riverview West Side School of Excellence
	160 E Isabel St
	
	X
	
	X

	Rondo Education Center
	560 Concordia Ave
	
	
	
	

	Saint Paul Music Academy
	27 E Geranium Ave
	
	X
	X
	X

	St Anthony Park Elementary
	2180 Knapp St
	X
	X
	X
	X

	Student Placement Center
	2102 University Ave
	X
	
	
	X

	The Heights Community School
	1863 Clear Ave
	
	X
	
	X

	Washington Technology Secondary
	1495 Rice St
	
	
	
	

	(Paul & Sheila) Wellstone Elementary
	1041 Marion St  
	X
	X
	
	X

	Wheelock Early Education
	1521 Edgerton St
	X
	X
	X
	X






[bookmark: _Toc353525402]Inspection Reports
· All inspection and reinspection reports can be found in a separate document. Each report shall contain the date of the inspection and the inspector’s name, signature, State of accreditation, and accreditation number.

· The inspection reports must contain written descriptions of:
· Location;
· Approximate square or linear footage of homogenous areas;
· Locations of all samples taken and date taken;
· A description of the manner used to determine sample locations;
· Name and accreditation state and number of each inspector collecting samples;
· Homogenous areas where friable suspected ACBM is assumed to be ACM;
· Homogenous areas where nonfriable suspected ACBM is assumed to be ACM;
· A copy of the analysis of any bulk samples collected and analyzed, including name and address of laboratory, statement that the laboratory meets the applicable requirements of 763.87(a), the date of analysis and the name and signature of the person performing the analysis;
· A description of the assessments required to be made under 763.88 of all ACBM and assumed  ACBM; and
· Name and accreditation state and number of each inspector making the assessments.

· Reinspections will be completed every three years or sooner.  Current schedule has St. Paul Public Schools doing reinspections in 2012, 2015, 2018, 2021, etc.

[bookmark: _Toc353525403]LEA Designated Person
· St. Paul Public Schools LEA Designated Person is:
John Elling, Environmental Services Manager
1930 Como Ave.
St. Paul, MN 55108
Cell: 612.394.5510

· The LEA Designated Person shall certify that the following responsibilities have been met or will be met:
1. Ensure that the activities of any persons who perform inspections, re-inspections, and periodic surveillance, develop and update management plans, and develop and implement response actions, including operations and maintenance, are carried out in accordance with subpart E of this part.
2. Ensure that all custodial and maintenance employees are properly trained as required by the subpart E and other applicable Federal and/or State regulations (e.g. the Occupational Safety and Health Administration, asbestos standard for construction, the ECP worker protection rule, or applicable State regulations). 
3. Ensure that workers and building occupants, or their legal guardians, are informed at least once each school year about inspections, responses actions, and post-response action activities, including periodic reinspection and surveillance activities that are planned or in progress.
4. Ensure that short-term workers (e.g. Telephone repair workers, utility workers, or exterminators) who may come in contact with asbestos in a school are provided information regarding the location of ACBM and suspected ACBM assumed to be ACM.
5. Ensure that warning labels are posted in accordance with 763.95.
6. Ensure that management plans are available for inspection and notification of each has been provided as specified in the management plan under 763.93(g).
7. Consider whether any conflict of interest may arise from the interrelationship among accredited personnel and whether that should influence the selection of accredited personnel to perform the activities under this subpart.

Notification Requirements
Annual Parent and Staff Notification
· At the beginning of each school year the district’s communications department publishes in a district wide news publication intended to reach all parent/legal guardians of all students as well as all staff members of the district.
· The content of this publication is as follows:
· The asbestos Emergency Response Act (AHERA) in 1987 required school districts to developed and implement an Asbestos Management Plan by July 1989.  AHERA also requires that schools annually inform workers, student’s parents/guardians and school visitors about inspections, reinspections, six month periodic, response actions and post-response action activities.
· The Institute for Environmental Assessment has inspected and developed a management plan for each Saint Paul Public School building.  Each management plan contains a health risk assessment and building recommendations concerning the maintenance or removal of asbestos containing building materials.
· Individual Building Management Plans are available in the Administrative Office of each school building. The AHERA law requires that the plans, which include inspection, reinspections, six-month periodic surveillance, response actions and post response actions, be available during normal business for inspection by interested individuals.

Short-Term Worker Notification
· All workers, including short-term workers, with potential exposure to ACBM are under contract with the district. The building inspection reports are available on the district’s web site at https://www.spps.org/Page/3495 and are available to the public and contractors. 
· The district has placed the following specification section in the contract documents providing for the notification requirements under 763.84:
[bookmark: _Toc510159411][bookmark: _Toc510159876]

XI	ENVIRONMENTAL AND HAZARDOUS MATERIALS REQUIREMENTS

1.00	Occupational Health and Safety Administration (OSHA)

The General Contractor and any of their Subcontractors and/or suppliers shall perform the training as mandated by Federal, State, and Local regulations that is required for completion of this contract.  Occupational Health and Safety Administration (OSHA) requires training for construction workers in several areas including, but not limited to, asbestos, employee right to know (ERTK) and personal protective equipment (PPE).

1.01	ASBESTOS GENERAL:

A. The Owner has surveyed the site(s) to determine the existence of Asbestos Containing Building Materials (ACBM), and all bidders are hereby notified that the existence of ACBM may affect work procedures and processes.
1. Section 1.05 ASBESTOS INSPECTION contains the most recent survey performed by the Owner showing the material type(s) and location(s) of all asbestos and non-asbestos containing materials for the site(s).  (Clarification of information contained in this report is available by contacting the Environmental Services Group @ 651.744.1800.)
2. The General Contractor must notify all of their Subcontractors and/or suppliers of all known locations of ACBM at the site(s).
3. Asbestos containing materials not listed in the inspection report may still exist in the facility in inaccessible chases and shafts.  Federal requirement for these inspections did not require accessing these areas.  If work is required in these types of areas notify the Environmental Safety Department.
B. Work required under this section includes identification of potentially or actual hazardous substances encountered during construction operations under this contract or contracts.  This section establishes procedures for notifying Owner of said substances.
1. Upon encountering any suspect ACBM, the Contractor shall immediately notify the Architect and/or the Owner's representative, and concurrently cease operations in the vicinity if it appears that normal construction operations will possibly disturb the materials or cause release of hazardous substances into the atmosphere.
2. The General Contractor and any of their Subcontractors and/or suppliers shall not be required to perform nor bear any responsibility for the performance of asbestos abatement work, supervision of the asbestos abatement contractor, or assurance of the proper execution of asbestos abatement procedures or any work related to asbestos.

1.02	ASBESTOS ABATEMENT:

A. The Owner shall, under separate contract, remove ACBM at any and all locations where construction work under this contract will interface with execution of that work.


1.03	NOTIFICATION PROCEDURES: (Other Hazards)

A. Upon encountering any suspect materials, the Contractor shall immediately notify the Architect and/or the Owner's representative, and concurrently cease operations in the vicinity if it appears that normal construction operations will possibly disturb the materials or cause release of hazardous substances into the atmosphere.
B. Upon suspension of operations, the Architect and/or the Owner's representative is to be notified of the situation and the following information provided:
1. Location of the substance in question;
2. Condition of the substance; (include notification of possible release of material into the atmosphere if material is disturbed)
3. Description of substance for which analysis is requested; and
4. Extent of substance.

A. The Architect and/or the Owner's representative upon being notified will in turn notify Saint Paul Public School's Environmental Services Group (651.744.1800) for further direction and clarification.
B. This notification procedure will be followed in its entirety.  It applies to contractors, subcontractors, suppliers, and their respective agents or representatives.  Failure to follow these procedures shall render the party responsible for any subsequent contamination of the premises.

1.04	The contractor will be required to final clean all work areas (including those they failed to protect) as follows:

A. Damp wipe all horizontal surfaces with water and an all-purpose non-ammonia based cleaner or detergent;
B. Vacuum all floors in occupied spaces.  Vacuums should be capable of removing 90% or better of contaminants down to one micron in size;
C. Broom clean floors in all other areas; and
D. Ducts, coils, diffusers/vent covers shall be dust and dirt free.

1.05	ASBESTOS INSPECTIONS (can be found at https://www.spps.org/Page/3495)



Employee Training
· Ensure that all maintenance and custodial personnel who may work in buildings that contain ACBM receive asbestos training of at least two hours, whether or not they are required to work with ACBM.  
· Training should occur within 60 days of employment and should include:
· Information regarding asbestos and its various uses and forms;
· Information on the health effects associated with asbestos exposure;
· Locations of ACBM identified throughout each school building in which they work;
· Recognition of damaged, deterioration and delimitation of ACBM;
· Name and telephone number of the of the person designated to carry out the general local education agency responsibilities under 763.84 and the availability and the location of the management plan;
· Training of maintenance and custodial staff who conduct any activities that will result in the disturbance of ACBM shall receive the above-described 2-hour asbestos awareness training and 14 hours of additional.  
· Additional training shall include, but not be limited to:
· Descriptions of the proper methods of handling ACBM:
· Information on the use and availability of respirators as outlined in the district’s respiratory protection program;
· Provisions of 763.93; and
· Hands-on training in the use of respiratory protection, other personal protection measures and good work practices.
· Maintenance and custodial staff who have attended EPA-approved asbestos training or received equivalent training for O&M and periodic surveillance activities involving asbestos shall be considered trained.
· Training records will be maintained by ESG.		


OPERATION AND MAINTENANCE ACTIVITIES

[bookmark: _Toc353525409]Response Action General Requirements 
· All response action recommendations shall be a collaborative decision made by the environmental consultant and the LEA Designated Person. 
· For the purpose of 763.93(5) requirements, the LEA Designated Person makes the response action recommendations.
· The general guidelines to response actions are as follows:
· All accessible damaged TSI will be repaired or removed as soon as it is identified as such.
· Inaccessible damaged TSI will be left as is, unless it is determined that the material is a danger to human health or the environment, until such time that it can be accessed and repaired or removed.
· Millboard Pipe Insulation (with asbestos in the tar paper layer only) unsealed ends are not considered damaged if the end is as manufactured and contains non-mudded fitting residue and do not require a response action.
· Millboard Pipe Insulation (with asbestos in the tar paper layer only) is not considered damaged unless the tar paper layer is found to be damaged.
· Response actions cover friable asbestos only, or those nonfriable materials about to become friable as a result of activities performed in the school building.

[bookmark: _Toc353525410]Response Action Requirements 
· Response actions shall contain a detailed description of preventative measures to be taken, methods to be used, locations where the measures and actions will be taken and a schedule for beginning and completing each preventative measure and response action.
· All contractors performing response actions must be accredited contractors under Minnesota Department of Health Rules.
· A detailed description in writing of any ACBM which remains in the schools once response actions are undertaken pursuant to 763.90 shall be completed in the following periodic surveillance or third year inspection, whichever comes first.
· Restrict entry by persons other than those necessary to perform the maintenance project, either by physically isolating the area or by scheduling.
· Post signs to prevent entry by unauthorized persons. Shut off or temporally modify air-handling system and restrict other sources of air movement.
· Use work practices or other controls, such as wet methods, protective clothing, HEPA vacuums, mini enclosures, glovebags, as necessary to inhibit the spread of any released asbestos fibers.
· Clean all fixtures or other components in the immediate work area.
· Place all asbestos debris and other cleaning materials in a sealed leak-tight container.
 

[bookmark: _Toc353525411]Maintenance Activities / Minor and Major Fiber Releases
· All maintenance activities, minor fiber releases and major fiber releases shall be defined, performed and conducted by persons accredited to design and conduct response actions.  Methods used for these responses shall be sufficient to protect human health and the environment from asbestos fibers. 

[bookmark: _Toc353525412]Reinspection Requirements
· Reinspections required at least every three years per 763.85 shall be performed with, at a minimum, the requirements outlined under the Inspection Requirements section of this document.  Due to the many changes in facilities including access to new areas, materials introduced in renovations, changes in suspected materials covered, the district may choose to perform full facility inspections during the third-year inspection periods.

[bookmark: _Toc353525413]Periodic Surveillance 
· In the years when third year reinspections are not performed, two periodic inspections will be performed on all asbestos containing materials noting any change in condition of the material.  

[bookmark: _Toc353525414]Additional Cleaning
· No additional cleaning is required above and beyond a minor or major fiber release episode or in conjunction with an O&M response action.


[bookmark: _Toc353525415][bookmark: _Toc510159414][bookmark: _Toc510159879]RECORDKEEPING REQUIREMENTS

[bookmark: _Toc353525416][bookmark: _Toc510159415][bookmark: _Toc510159880]Management
Recordkeeping requirements outlined in 40 CFR 763.94 shall be maintained by ESG and available upon request.

[bookmark: _Toc510159881]Contact Information
Questions, concerns, comments or other information regarding the District’s AHERA Management Plan can be directed to:

· The Environmental Services Group
· Phone: 651.744.1800
· Program Manager: Brian Bergstrom, (651.802.2309)
· Web Site: https://www.spps.org/Page/3470
· Email: ESG@spps.org


[bookmark: _Toc510159417][bookmark: _Toc510159882]RESOURCES & APPENDIX

Resource 1: 
· AHERA – Asbestos Hazardous Emergency Response Act (AHERA) records can be found in the administrative office of all district facilities.  The district asbestos records are kept in the Facility Planning Department.  Regulatory sources of information are the Asbestos Abatement Section of the Minnesota Department of Health, Division of Air Quality of the Minnesota Pollution Control Agency, the Occupational Safety and Health Division of the Minnesota Department of Labor and Industry at 651.296.2116 and the U.S. Environmental Protection Agency at 312.353.5590.

Resource 2: 
· ASHRAE 62-1989 – American Society of Heating, Refrigerating and Air-Conditioning Engineers Standard “Ventilation for Acceptable Indoor Air Quality”.  A copy can be obtained from ASHRAW Publications Sales Department, 1791 Tullie Circle, NE, Atlanta, GA 30329, 404.636.8400.

Resource 3: 
· ASHRAE 52.1-1992 – American Society of Heating, Refrigerating and Air-Conditioning Engineers Standard “Method of Testing Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter”.  A copy can be obtained from ASHRAW Publications Sales Department, 1791 Tullie Circle, NE, Atlanta, GA 30329, 404.636.8400.

Resource 4: 
· ASHRAE 55-1992 – American Society of Heating, Refrigerating and Air-Conditioning Engineers Standard “Thermal Environmental Conditions for Human Occupancy”.  A copy can be obtained from ASHRAW Publications Sales Department, 1791 Tullie Circle, NE, Atlanta, GA 30329, 404.636.8400.

Resource 5: 
· Building Air Quality.  A Guide for Building Owners, Facility Managers, and Agency Contacts – Minnesota Department of Administration Facilities Management Bureau, May 24, 1995.

Resource 6: 
· EPA Tools for Schools

Resource 7: 
· EPA Building Air Quality Manual – EPA/400/1-91/033 – “Building Air Quality, A Guide for Building Owners and Facility Managers” published December, 1991.  To obtain a copy call 800.438.4318.

Resource 8: 
· EPA Introduction to Air Quality – EPA/400/3-91/003 - /3-91/003 – “Introduction to Indoor Air Quality, a Reference Manual”, published July, 1991. To obtain a copy call 800.438.4318.

Resource 9: 
· Integrated Pest Management

Resource 10: 
· IICUC Carpet Cleaning Standard S001-1991 -  International Institute of Carpet and Upholstery Certification, 2715 East Mill Plain Blvd., Vancouver, Washington 98661, 206.693.5675.

Resource 11: 
· Occupational Safety and Health Association (OSHA) Standard CFR 1910 Subpart Z – Toxic and Hazardous Substances – Title 29 Code of Federal Regulations General Industry Standards.  Enforced by the Minnesota Department of Labor and Industry Occupational Safety and Health Administration.

Resource 12: 
· OSHA Standard 29 CFR 1910.1033 - To obtain a copy call Minnesota OSHA at 612.296.2116.

Resource 13: 
· Uniform Building Codes, Uniform Mechanical Codes, Uniform Fire Code, and other related documents adopted and amended by the State Building Codes and Standards Division.
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