ADVERTISEMENT OF BID NOTICE

Princeton Public Schools

Mercer County, New Jersey

NOTICE IS HEREBY GIVEN that the Princeton Board of Education (“Owner”) will receive bids for a Power Purchase Agreement, in accordance with the requirements of the Bid Documents prepared by Fraytak Veisz Hopkins Duthie, P.C. (FVHD), Architects-Planners, www.fvhdpc.com, FVHD Project No. 5698.

Bids will be received for: Power Purchase Agreement – FVHD-5698.

Proposal Documents are available for no fee from the Architect’s website.  Requests for electronic project documentation must be made through a registered account via the FVHD Contractor Portal at https://www.fvhdpc.com/contractors. There is no cost to create an account at the FVHD Contractor Portal. Hard copies are available for $50 per set.  A check or money order should be made payable to Fraytak Veisz Hopkins Duthie, P.C.  A direct shipping account number (FedEx or UPS) and preferred shipping speed must also be provided.

A Pre-Proposal Meeting is scheduled for Marh 5, 2026, 10:00 AM, at the Princeton Board of Education, 25 Valley Road, Princeton, NJ 08540. A facilities site walk will immediately follow the conclusion of the meeting. It is mandatory that someone from the Proposal Team conduct a facility inspection at each project site. There will not be scheduled facility inspections other than the site walk immediately following the Pre-Proposal Meeting.

Sealed Bids are due by March 31, 2026, 2:00 PM to the Princeton Board of Education, Attn: Andrew Harris, 25 Valley Road, Princeton, NJ 08540, and will be publicly opened and read immediately thereafter.  No Proposals shall be received by the Princeton Board of Education after the time and manner specified within the RFP.  The Owner reserves the right to reject and all proposals if deemed by the District to be in its best interests, to the extent permitted by the law pursuant to N.J.S.A. 18A:18A-22, and to waive minor informalities or non-material exceptions, that may be in the best interest of the Owner.

Proposals shall be submitted in duplicate (one original and one copy) in a sealed envelope, addressed to the Owner, bearing the name and address of the bidder, and clearly marked “PROPOSAL” with the contract title and/or project number on the outside of the envelope and must be accompanied by a Certified Check, Cashier's Check or Bid Bond drawn to the order of the Owner in the amount of ten percent (10%) of the amount of the bid, but in no case in excess of $20,000; and must be delivered to the Princeton Board of Education, Attn: Andrew Harris, 25 Valley Road, Princeton, NJ 08540 to the above place on or before the hour named.  The Board of Education and the Architect assume no responsibility for bids mailed or misdirected in delivery.

Proposers are required to comply with the requirements of N.J.S.A. 10:5-31, et seq. and N.J.A.C. 17:27-1, et seq., concerning affirmative action and equal employment pursuant to the “Public Works Contractor Registration Act” (P.L. 1999, C238). Proposers and their subcontractors are required to be registered with the New Jersey Department of Labor and to possess a current certificate by said Department including compliance with the Act.

All Proposals shall be in accordance with the RFP requirements and fully comply with the requirements of the Department of Education (“DOE”), Division of Consumer Affairs (“DCA”), Public School Contracts Law, Office of Clean Energy requirements for renewable energy systems (www.njcleanenergy.com) and the New Jersey Board of Public Utilities (“BPU”).

Proposers are required to submit a Statement of Ownership Disclosure with the Proposal, in compliance with N.J.S.A. 52:25-24.2 (P.L. 1977, c. 33), and complete all other forms provided with the RFP.

The issuance of this RFP is not intended to, and shall not be construed to, commit the Owner to execute any agreement. Neither the Owner, nor any of its consultants, shall be liable for any claims or damages resulting from the solicitation or receipt of Proposals in response to this RFP, nor will there be any reimbursement to Proposers for the cost of preparing the Proposal or for participating in the RFP process. By submitting a Proposal in response to this RFP, the Proposers accept and consent to the procurement process selected by the Owner, and the Proposer waives any and all claims to same.

All Proposals will become the property of the Owner and will not be returned. Reasonable efforts will be taken by the Owner to keep confidential, as permitted by law, such information that is properly identified by the Proposer as being confidential or proprietary in nature.

The submission of a Proposal will constitute a conclusive and binding representation by the Proposer that it has agreed to, and complied with, every requirement of this RFP, that the procurement process has been conducted and implemented in a legally permissible manner and that the Proposal documents are sufficient in scope and detail to indicate and convey the understanding of the parties as to all terms and conditions for performance hereunder.

Princeton Public Schools

Andrew Harris, Business Administrator/Board Secretary

TABLE OF CONTENTS

Section 1: RFP Introduction and General Information…………………………………………

Section 2: Terms and Conditions……………………………………………………………….

Section 3: Scope of Services…………………………………………………………………..

Section 4: Instructions & Evaluation Criteria…………………………………………………..

Appendices…………………………………………………………………………………….

Appendix A – Proposal Form…………………………………………………………..

Appendix B – Expected and Guaranteed Annual kWh Production…………..………..

Appendix C – Acknowledgement of Addenda ……………………………….……….

Appendix D – Roofing Areas & Preferred Array Locations …………………………..

Other Appendices – Other Required Forms, Disclosures, Certificates, Statements, etc……….

Section 1: RFP Introduction and General Information

The Princeton Board of Education (“Owner”), in keeping with the goals and mission elements of the Princeton Public Schools community, is requesting bids from qualified Bidders to specifically provide substantial savings to the ongoing operations of the Owner educational facilities, enhance community partnerships, and to demonstrate a commitment to responsible environmental stewardship. In partnership with the New Jersey Energy Savings Improvement Program (“ESIP”), the ESIP contractor and the Awarded Bidder, the BOE shall demonstrate the Owner’s commitment to:

- Maximize savings through a lower electric rate provided by a Solar Power Purchase Agreement (PPA);

- Offset as much of the District’s electric usage as possible;

- Improve the environmental sustainability of the Owner;

- Strengthen the Owner’s reputation within the community and state-wide; and

- Provide the potential for energy storage to the Princeton Public Schools, either immediately or in the future.

Bidders shall submit proposed PPA rates based upon the information contained within this RFP. The final RFP rate, terms, and conditions will be determined between the Owner and the Selected Proposer. Proposers shall submit, with their proposal, the template PPA version they intend on using for this Project, subject to the Owner’s review. Proposers submitting proposals must have the ability to obtain PPA financing. Given the multiple facets that constitute a solar development project, multiple parties may jointly submit Proposals in partnership, joint venture,

or other legal structure. Proposals will be evaluated based on the qualifications of the Proposer, scope of services to be provided, and proposal price offered pursuant to N.J.S.A. 18A:18A: -4.6 and N.J.A.C. 5:34-4.1, et seq.

  - List of Facilities Included in this RFP

Princeton High School, 151 Moore Street, Princeton, NJ 08540

Princeton Middle School, 217 Walnut Lane, Princeton, NJ 08540

Community Park School, 372 Witherspoon Street Princeton, NJ 0854

Johnson Park School, 285 Rosedale Road, Princeton, NJ 08540

Littlebrook School, 39 Magnolia Lane, Princeton, NJ 08540

Riverside School, 58 Riverside Drive Princeton, NJ 08540

  - Preliminary Utility Interconnection Information

If the electric distribution company interconnection review concludes that interconnection approval can be granted with electrical upgrades to the facilities; then the Awarded Bidder shall bear the cost up to $50,000 for Utility required safety and monitoring equipment. If the Utility required upgrades are in excess of $50,000 per site to gain interconnection approval for any one Solar Energy System (SES), then the Awarded Bidder shall have the option to remove that SES from the PPA contract without penalty and without any further obligation to proceed with the SES. The Owner may also consider an adjustment to the PPA pricing, if the actual interconnection costs are higher than the $50,000 per site estimate in order to proceed with the SES’s. This adjustment will be at the option of the BOE based on the evaluation of total additional cost and a fair assessment to the PPA rate increase requested by the Awarded Bidder to cover those additional costs.

Section 2: Terms and Conditions

The Selected Proposer shall be required to provide a turnkey Solar PV system at each of the sites included in this RFP. The Solar PV systems shall be developed and owned by the Selected Proposer through a Power Purchase Agreement (PPA) in which the engineering, design, materials, installation, operation, and maintenance of these Solar PV system shall be at the responsibility of the Selected Proposer through the life of the term of the PPA. The selected proposer will also be responsible for the complete technical design and engineering of the solar energy system, as well as for obtaining and/or arranging all permits, inspections, reviews, and approvals, satisfying all utility interconnection and net metering requirements and arranging and/or preparing all necessary governmental and utility inspections and applications related thereto; geotechnical and structural analyses and wind load calculations; procuring all materials and components; and the successful completion and commissioning of the Project.

2.1 Renewable Energy Certificates

The Selected Proposer shall own the rights to the Renewable Energy Certificates (REC’s) during the term of the PPA. If at any point the Owner purchases the Solar PV Systems, the rights to the REC’s and any other environmental benefit shall be transferred to the Owner.

2.2 Purchase Options

It shall be part of the Power Purchase Agreement that the Owner shall have the option to purchase the system at the end of the 15-year term at fair market value. There shall also be early buyout options in the PPA that allows the Owner to purchase the systems after 10 years at fair market value.

2.3 End of Term Removal of System

If the Owner elects not to purchase the systems at the end of the PPA term or extend the life of the PPA, the PPA Proposer shall be required to remove all equipment installed and return the sites to their original condition, with exception of normal wear and tear. The proposer shall remove the solar project within ninety (90) days of the end of the service term.

2.4 End of Term PPA Extension

Within the PPA, the Owner shall have the option to extend the life of the Agreement for a five-year term at the end of the PPA, or as permitted by law.

2.5 Approval/Compliance with Laws

The Selected Proposer shall be required to obtain all necessary Federal, State, and Local approvals prior to construction commencement. The proposal shall be in accordance with the RFP requirements and fully comply with the requirements of the Department of Education (DOE), Department of Community Affairs (DCA), Local Public School Contracts Law, New Jersey Department of Labor and Workforce Development, Office of Clean Energy requirements for renewable energy systems, and the New Jersey District of Public Utilities (BPU) requirements.

2.6 Cost of Proposal

All Proposers shall incur the cost of their submittal. The Owner shall not be responsible for any proposal costs.

2.7 Required Qualifications

All contractors and subcontractors that take part in these installations must be properly licensed in the State of New Jersey and shall comply with the Public Works Contractor Registration Act (N.J.S.A. 34:11-56.48) and laws applicable to public works contracts, such as the Prevailing Wage Act (N.J.S.A. 34:11-56.25 et seq.). The General Contractor named in the Selected Proposal must be registered with the New Jersey Department of Labor and Workforce Development Pursuant to the Public Works Contractor Registration Act and pre-qualified by the Division of Property Management and Construction (DPMC).

2.8 Hazardous Material

If at any point during the installation the Selected Proposer encounters hazardous material, they are to notify the Owner and cease work at that site. If any delays are incurred by the discovery and removal of this hazardous material the Selected Proposer’s completion date shall be adjusted accordingly.

2.9 Insurance Requirements

The Selected Proposer shall be required to obtain and maintain always during the term of the PPA as a direct cost of operation, insurance coverage as directed by the District, which shall include the below listed types of insurance with limits of liability in at least the amounts listed below. Such coverage shall be obtained from an insurance company authorized and licensed to do business in the State of New Jersey, with a rating of not less than “A-” in the current AM Best Manual and must be approved by the Owner.

- Commercial General Liability Coverage in the amount of $2,000,000. Each Occurrence; $2,000,000 Personal Injury Limit: $2,000,000 General Aggregate; and $2,000,000 Products-Completed Operations Aggregate.

- Casualty and Property Damage in the amount equal to the replacement of value of all Renewable Energy Projects.

- Workers’ Compensation Coverage as statutorily required by the State of New Jersey for all employees of Successful Proposer. Employers’ Liability coverage on the Workers Compensation Polity shall be written in the minimal amount of $1,000,000.

- Excess Liability Coverage, in the amount of $5,000,000 per occurrence and $5,000,000 aggregate, shall be in the form of an Umbrella policy.

- Comprehensive Automobile Liability Coverage, in an amount not less than $1,000,000 per accident.

- Professional Liability Insurance (errors and omissions) in the amount of $1,000,000 per claim.

All the required insurance policies, except Worker’s Compensation, shall include the Owner as an additional insured. Evidence of such coverage being in place shall be promptly delivered to the Owner’s offices, Attn: Business Administrator prior to the commencement of the term of the PPA.

2.10 Taxes

The Selected Proposer shall be responsible for the payment of all taxes that that may be imposed upon any aspect of the Solar PV or energy storage components or installation. The Proposer’s PPA rate must be inclusive of applicable sales & use taxes.

2.11 Qualifications of Sureties

The Surety must be licensed in accordance with the laws of the State of New Jersey to transact business as a surety company in the state of New Jersey. The Surety providing the relevant bond(s) shall satisfy the requirements of N.J.S.A. 40A:11-4.1 as amended.

2.12 Consent of Surety

Each Proposer shall submit a Consent of Surety with their proposal substantially similar to the form provided in Appendix E - Form of Consent of Surety for Construction Performance Bond, executed by a surety company qualified to do business in New Jersey, who shall, at the time of submission, agree that in the event of an award, the surety shall furnish a construction performance bond in the amount of 100% of the costs of designing, constructing, and installing the Renewable Energy Projects.

2.13 Proposal Bond

Each Proposer shall submit a certified check, cashier’s check, or proposal bond in the amount of $20,000, payable to the Princeton Public Schools. The Proposal Bond shall be accompanied by Power of Attorney for the full amount of the Proposal Bond from a surety company authorized to do business in the State of New Jersey. The check or bond of the Selected Proposer to whom the PPA is awarded shall be retained until a PPA and other required documents are executed, and the required Construction Performance Bond is submitted to the Owner.

The Selected Proposer who is awarded the contract shall give a Construction Performance Bond in the amount of 100% of the costs of designing, constructing, and installing the Renewable Energy Projects, which shall be cancelled and returned upon installation and commencement of commercial operation of the projects. The Construction Performance Bond may be provided by the Selected Proposer’s subcontractor.

2.15 Affirmative Action Requirements

The Selected Proposer shall comply with the requirements of N.J.S.A. 10:5-31 and N.J.A.C. 17:27-1, et seq. (Affirmative Action/Equal Employment Opportunity), refer to Appendix K - Affirmative Action Compliance/Mandatory EEO Language.

2.16 Business Registration Certificate

All Proposers must be registered to work in the State of New Jersey and submit with their proposal a copy of their Business Registration Certificate.

2.17 Americans with Disabilities Act of 1990

The Selected Proposer agrees to abide by the Americans with Disabilities Act of 1990 (42 U.S.C. 12101, et seq.) which prohibits discrimination based on disability by public entities in all services, programs and activities provided or made available by public entities.

2.18 Responsibility for Tax Advice

By submitting a response to this RFP, all Proposers acknowledge that the Owner nor its attorneys or other advisors are rendering any advice or opinion in connection with any federal and state tax matters set in this RFP.

2.19 Prevailing Wages

The Selected Proposer and/or its subcontractors shall pay no less than the prevailing wage rate to workers employed in the performance of any contract for the project, in accordance with the rate determined by the commissioner of the New Jersey Department of Labor and Workforce Development pursuant to N.J.S.A. 34:11-56.25, et seq.

2.20 Disclosure of Contributions to New Jersey ELEC

Respondents are advised that, pursuant to N.J.S.A. 44A:20.27, all business entities who have received contracts valued more than $50,000 from public entities in any calendar year must file an annual disclosure statement of political contributions with New Jersey Election Law Enforcement Commission (ELEC). Respondents are responsible for determining if filling is necessary.

2.21 Letter of Financing Guarantee

A letter from the entity that will be providing the financing to install the renewable energy project at Princeton Public Schools is required. The letter is to be signed by the financing party guaranteeing that the funds are available for these projects.

2.22 Criminal History Background Checks

When applicable, the Proposer, shall provide to the District prior to commencement of contract, evidence, or proof that each employee assigned to provide services and that comes in regular contact with students, has had a criminal history background check, and furthermore, that said background check indicates that no criminal history record information exists on file for that worker. Failure to provide a proof of criminal history background check for any employee coming in regular contact with students, prior to commencement of contact, may be cause for breach of contract.

2.23 Debarment, Suspension, or Disqualification

Princeton Public Schools will not enter a contract for work with any person, company or firm that is on the State Department of Labor and Workforce Development; Prevailing Wage Debarment List, or the State of New Jersey Consolidated Debarment Report (www.state.nj.us/treasury/debarred). Pursuant to N.J.S.A. 52:32-44.1 (a), any person that is debarred at the federal level from contracting with a federal government agency shall be debarred from contracting for any public work in this State.

All Proposers are required to submit a sworn statement indicating whether the entity listed on the proposal form, or any person employed by this entity, or the person’s affiliates are debarred from contracting with a federal government agency, nor debarred from contracting with the State of New Jersey. The District shall verify the certification by consulting:

- New Jersey Department of Treasury – Consolidated Debarment Report

- NJ Department of Labor and Workforce Development – Prevailing Wage Debarment List

- Federal Debarred Vendor List—System for Award Management (SAM.gov)

2.25 Form of Agreement: Template PPA

All Proposers shall submit, with their Proposal, the template PPA version they intend to use if selected, subject to review and approval by the Owner.

2.26 Incentives

The Owner makes no representations to the availability of incentives. The Selected Proposer is responsible for identifying, designing the project to meet the requirements, and attaining all incentives available. The Owner shall not accept contingent Proposals, including Proposals or proposed PPA prices that are contingent on specific incentive programs and amounts.

2.27 Temporary Shutdown of the Solar Facility

The Owner shall not cause the Solar Project to shut down temporarily, unless in the case of emergency or in a Force Majeure Event for more than a total of ten (10) days in any two (2) consecutive contract years, whether scheduled or as a result of an emergency, negligent act or omission caused by the Owner (a “Temporary Shutdown”). Further, the Owner shall make its best efforts not to schedule a Temporary Shutdown during the Solar Project’s peak production months of April through August. The Owner shall communicate to the Selected Proposer the commencement date and expected duration of any such Temporary Shutdown as far in advance of the commencement of the Temporary Shutdown as practicable. In the event the duration of the Temporary Shutdown is in excess of ten (10) days in any two (2) consecutive contract years, the Owner shall pay to the Selected Proposer an amount equal to the following: (i) the reasonable cost to remove and re-install or shutdown and reinitiate the Solar Project or portion of the Solar Project; (ii) the cost, if any, of lost solar energy production during the period of Temporary Shutdown in excess of the ten (10) days in any two (2) consecutive contract years at the PPA Price then in effect; and (iii) an amount attributable to any lost solar renewable energy credits, if any, calculated at the Selected Proposer’s actual out-or-pocket loss in excess of the ten (10) days in any two (2) consecutive contract years.

2.28 Commercial Operation Date – Guaranteed Completion Date & Liquidated Damages

Proposer shall provide a Commercial Operation Date and Guaranteed Completion Date for each site receiving a solar PV system. In the event the Commercial Operation Date has not been achieved by the Guaranteed Completion Date for any school, the Selected Proposer shall be liable for delay liquidated damages of $1,000 per day for each day of unexcused delay until the Commercial Operation Date is achieved. The Commercial Operation Date shall commence after: (i) no less than eighty percent (80%) of the nameplate capacity has been installed; and (ii) the Selected Proposer has acquired all permits necessary to authorize the production, sale and delivery of energy in the intended amounts hereunder; and (iii) the Selected Proposer gives the Owner written notice that the Solar Project is mechanically complete and has been approved for interconnected operation by the applicable utility and capable of providing energy to the Selected Proposers meter at each respective school.

2.29 Electrical Interconnections

The Selected Proposer shall supply and install all equipment required to interconnect the Solar Projects to the utility electric distribution system as net-metered solar energy systems. The Selected Proposer shall complete all applications, studies, and testing procedures to complete the interconnection process. All costs associated with utility interconnections shall be borne by the Selected Proposer, except those costs already incurred to date.

  - Mandatory Provisions to Include in Form of Power Purchase Agreement

- A requirement that the Proposer, upon expiration of the contract term or upon earlier termination of the PPA for any reason, remove the entire solar energy system from the Owner’s property and restore the Owner’s property to its condition prior to installation of the solar energy system, reasonable wear and tear excepted. The removal of the solar energy system and the restoration of the Owner’s property must be done at the Proposer’s sole cost and expense; no costs, fees, or charges for removal or restoration shall be assessed against or incurred by the Owner under any circumstances.

- A provision which the Proposer to reimburse the Owner in the amount of $85,000.00 for the professional services expenses it incurred in relation to the preparation for and procurement of the PPA. This payment must be paid immediately upon execution of the PPA.

- The Proposer accepts all of the Owner’s property in as-is, where-is condition with all faults, known and unknown. The Owner makes no warranties regarding property condition, structural capacity, roof condition, electrical systems, soil conditions, solar access, or suitability for solar installation. The Owner will not be required to make any modifications, improvements, or repairs to accommodate installation. If any modifications to the Owner’s property are necessary, the Proposer will perform the required modifications at its cost or adjust the system design accordingly (subject to the guaranteed minimum production set forth in the proposal).

- Provide the following documentation as to the Proposer (if the Proposer is performing work) and all subcontractors: Notice of Classification from DPMC, as issued by the State of New Jersey, Department of Treasury, Division of Property Management and Construction (DPMC) for C035 Solar Energy Systems and C047 Electrical.

Section 3: Scope of Services

Princeton Public Schools is seeking proposals for onsite solar systems at the locations identified in Section 1.1 List of Facilities Included in this RFP. Use the areas designated in Appendix D – Roofing Areas & Preferred Array Locations.

The Selected Proposer shall provide fully managed PV development services that include, but are not limited to:

- Site assessment;

- System design, engineering, and construction for the PV system, including, timeline/project schedule, equipment and description, layout of equipment and specification for equipment permanent installation;

- Financing;

- Securing the necessary labor, services, equipment, funding, permits and approvals to develop fully operational PV systems at each project site;

- Satisfying all local, state, federal and utility requirements for the solar system;

- Commission, monitor, own, operate, and maintain the systems after installation for the projects sites; and

- Establish and maintain construction standards, safety, and quality control throughout the work.

3.1 Site Assessment and Final Proposal

The Selected Proposer shall assess each site within the Owner, including an analysis of the impact of shading, tilt, and orientation on annual electricity production, and note any electrical, mechanical, or structural considerations that may incur costs above and beyond the PPA rate being offered.

The Selected Proposer shall submit a Final Proposal for each project site including:

- kW DC generating capacity, project layout, configuration, azimuth, tilt angle, de-rate factor, and projected degradation rate of proposed system;

- Projected annual energy generation in kWh for the full period of the PPA and projected monthly energy generation in kWh for year 1 of the PPA;

- Provide hourly production reports for each site in Microsoft Excel format;

- Projected annual PPA costs for the full period of the PPA;

- Proposed PPA rate along with annual escalation, if any, and term of PPA;

- Adder rates to the base PPA rate, per the Price Proposal Sheet; and

- Net present value of PV system.

3.2 PPA Financing

The Owner is seeking third-party ownership, financing, and maintenance agreement with the Selected Proposer. Proposers shall indicate whether guaranteed financing is available, who will be funding the project, and who will own the system for the life of the PPA. Any language required by the proposed financing entity MUST BE SUBMITTED WITH THE PROPOSAL.

3.3 Utility Interconnection

- The awarded Proposer shall supply and install all equipment required to interconnect the Solar Energy Systems to the utility electric distribution system as net-metered solar energy systems. The Proposer shall complete all applications, studies, and testing procedures to complete the interconnection process. All costs associated with utility interconnection shall be borne by the Proposer.

- Electric Service Interruptions: The Awarded Proposer must coordinate all interruptions of the BOE’s electric service required for the installation, interconnection, commissioning, startup, and maintenance of the SES’s. This interruption shall not be performed during the BOE’s normal working days/hours. Proposers are required to disclose in this proposal, the physical and operational limitations including the minimum number of hours to be allocated to system shutdown to afford the BOE access to the facilities.

3.4 Environmental Permitting

The Selected Proposer shall be responsible for securing all environmental permits.

3.5 Ground Mount Arrays

There are no ground mount arrays in this RFP.

3.6 Roofs

The roof sections approved for solar by Princeton Public Schools are identified in Appendix D – Roof Areas & Preferred Array Locations. The Selected Proposer shall include the following requirements for their rooftop solar designs:

- All rooftop systems shall provide sufficient spacing to access roof hatches and service rooftop equipment.

- The Selected Proposer shall ensure that any roof and/or solar installation meets or exceeds the roofing manufacturer/warrantor requirements for roof work and solar array installations on their roofing product.

Final system layouts are subject to approval by the Owner.

  - Setbacks and Installation

Flat roof installation areas shall require 6’ setbacks from roof edges. For pitched roof areas, refer to the International Building Code 2018 (IBC2018) for setbacks, unless superseded by a local Authority Having Jurisdiction (AHJ). The installations shall be conducted by the Selected Proposer in conformance with all applicable laws and codes, interconnection requirements, and established industry practices. Site evaluations, installations, and all other onsite work shall be conducted in coordination with all Contractors and shall be completed as quickly and with as little disruption as reasonably possible.

The awarded Proposer shall supply all equipment, materials, and labor necessary to install the Solar Energy Systems (SES) and integrate each SES into the site and with the existing electrical system at the BOE Site, including emergency generation equipment.

The Solar Energy Systems shall be installed at the location shown in Appendix C. The site information is representational; but should be independently confirmed through on-site inspection. Bidders should confirm that PV arrays as proposed can be installed properly, in accordance with all applicable manufacturer’s recommendations (including overburden requirements), within the available space as shown on the site areas depicted in Appendix C and in accordance with Proposer’s on-site inspections.

3.8 Operation, Maintenance and Monitoring

The Selected Proposer shall be responsible for the operation, maintenance, and monitoring of the PV system at each site under the PPA. The Selected Proposer shall make an online interface showing instantaneous and cumulative energy production of each installed PV system accessible to the Owner, which can be used for monitoring purposes.

The Selected Proposer shall be responsible for installing a real-time Data Acquisition System for each site which shows renewable energy production data in kWh, historical production data, and emission offset information.

3.9 Communication

The Selected Proposer shall be required to designate a specific staff member who shall serve as the primary point of contact during the Project Period (Development and Construction). The Selected Proposer shall interface directly with the Owner and its consultants. The Selected Proposer shall provide regular progress updates during the Project Period. The Selected Proposer shall be expected to be responsive and prompt in communications.

3.10 Workdays

  - Construction activities shall adhere to all of the following requirements, as well as any additional requirements directed by the BOE or its representatives to ensure safety and normal operations of the facilities:

- All work to be performed on this project during summer recess and other breaks shall be done at the following hours: 7:00 AM – 3:30 PM Monday thru Friday, or other such times as may be designated by the BOE and local ordinances.

- All work to be performed on this project during the school year shall be done at the following hours: Second Shift 2:30 PM – 11:00 PM, Monday thru Friday and First Shift 6:00 AM – 2:30 PM on Saturdays, or other such times as may be designated by the BOE and local ordinances.

- The contractor is responsible for paying for custodial time if they need to work outside the designated work hours to meet the project schedule. See district calendar for additional information.

- The contractor cannot work within the school buildings at any time without prior approval from the BOE.

- All demolition and construction noise and dust to be limited inside the building during hours of operation. The district will decide the limitations on excessive noise and dust.

- The awarded Proposer shall be responsible for submitting a critical path method schedule to the BOE and their designated representative within one week after notice to proceed.

- No construction activities will be allowed until an acceptable schedule has been submitted and the BOE has approved the schedule.

- Notice to proceed shall serve as the commencement date for work on this project.

- All debris shall be removed on a daily basis.

3.11 Quality Assurance

- UL Compliance (or equivalent third-party safety consulting and certification organization) Materials manufactured within the scope of Underwriters Laboratories shall conform to UL Standards and have an applied UL listing mark (or equivalent). If no UL compliance (or equivalent certification) is available, provide all work in accordance with NFPA 70, National Electrical Code (NEC). Where required by the Authority Having Jurisdiction (AHJ), material and equipment shall be labeled or listed by a nationally recognized testing laboratory or other organization acceptable to the AHJ to provide a basis for approval under the NEC.

- Ensure that all work under the awarded Proposer’s control is conducted in accordance with all applicable safety codes, requirements and practices; including but not limited to, OSHA requirements, local and State safety codes, and specific project requirements as mandated by the BOE.  A safety plan must be submitted to and approved by the BOE or its designated representative.

- The Awarded Proposer shall be responsible for initiating, maintaining and supervising all safety precautions and programs in connection with the work.  The Awarded Proposer shall properly ensure individuals working onsite pursuant to the insurance requirements noted herein.

- The Awarded Proposer Awarded Proposer shall submit to the BOE a site-specific, safety plan detailing procedures for all safety aspects of all trades involved in the work. The safety plan shall be reviewed by the Owner prior to the start of construction.

- Responsibility to protect and prevent damage to property during removal, relocation or replacement actions rests solely with the Awarded Proposer.

- The Awarded Proposer shall restore to its original condition without extra costs to the BOE.  Property that is damaged due to the acts or omissions of any employees, agents, or subcontractors of the Awarded Proposer.  Acceptance of such repairs is subject to the requirements of and approval by the BOE.

- The Awarded Proposer must take proper care to protect all finished work by substantial covering until accepted by the BOE. To ensure public safety, the Awarded Proposer shall provide the required barricading, cones, safety tape, etc., for all areas which have work in progress.

3.12 Safety

The Selected Proposer shall be responsible for maintaining all safety precautions and programs connected to the work being performed. The Selected Proposer shall ensure that all Occupational Safety and Health Administration (OSHA) guidelines are being practiced by all contractors, subcontractors, and any agents on site at any given time.

3.13 Material Delivery

All major system components shall be delivered to their final location in protective containers. When loading to the roof, the Selected Proposer shall ensure proper placement of point loads. If material is stored on the ground, the Selected Proposer shall use areas approved by the Owner. The Selected Proposer shall work with the Owner to confirm all staging areas are adequate and safe. No roofs are to be loaded by crane while school is in session and students are present in the school.

3.14 Product Considerations

The Selected Proposer shall provide new, high quality, tier 1 (if applicable), UL-listed products and components for the PV system that is being proposed.

3.15 Commissioning

The Selected Proposer shall be responsible for putting together and submitting a written commissioning report to the Owner. The Selected Proposer is required to provide an operation and maintenance manual for each location.

3.16 Warranties

Each Proposer shall clearly describe warranties offered in the Proposal. Proposers should provide requirements that meet or exceed the minimum standards:

- Photovoltaic parcels – 25-year performance warranty with a minimum production of 90% at 10 years and 80% at 25 years; a material and workmanship warranty of 10 years.

- Inverter – 15-year product warranty.

- Racking/Monitoring System – 10-year product warranty.

3.17 Rapid Shutdown Compliance

All solar arrays on the roof of any school shall abide by all applicable codes within the National Electrical Code (N.E.C.) 2017 “Rapid Shutdown for PV Systems on Buildings” requirements.

3.18  License

During the term of the PPA and during construction, the Owner shall grant a license for the limited purpose of installation, operation, and maintenance of the solar system at the sites.

3.19 Technical Requirements

Each Proposer shall provide a technical proposal with design documents that include the following information:

- System description;

- Equipment details and description;

- Estimated layout of installation;

- Installation plan and staging requirements;

- Electrical work;

- Warranties on equipment;

- Integration of solar system with the existing electrical system at the site;

- Planned roof work scope;

- Site preparation, tree removal requirements, asphalt and concrete repairs, and final landscaping;

- Fencing and security measures;

- Electrical grid interconnection requirements;

  - Plan for reverse power relay and minimum import relay requirements, configurations, and settings;

- Controls, monitors, and instrumentation; and

- Operations and maintenance manuals (sample).

3.20 Tree Trimming/Removal

The Selected Proposer shall be responsible for tree trimming and tree removal at its cost once the Owner’s representatives have given approval on any request by the Selected Proposer to trim or remove any trees.

3.21 Estimated Production

  - Estimated Combined System Size (all sites): 1,513 kW

  - Solar PV system may only be installed on roof areas indicated in Appendix D – Roofing Areas & Preferred Array Locations.

  - Each Proposer shall provide a calculation based on PV Watts software that outputs the estimated hourly production of each solar energy system, using the assumptions from the actual system design in the proposal. The PV Watts Calculator available at http://pvwatts.nrel.gov/pvwatts.php that depicts the estimated production of each Solar Energy Systems, using the assumptions consistent with the actual system design in the Proposal or as required below. A separate PV Watts analysis should be performed for each separate array at each site. Proposers must use the following PV Watts assumptions:

- Electric Price as specified in the Proposal Form for Historical Electric Price year one (1)

- Solar Panel Type (in accordance with specification in Proposed design); Proposers must use the Standard assumption for modules with less than 19% efficiency.

- Array Type (in accordance with specification in Proposed design)

- DC System Size (in accordance with specification in Proposed design)

- System Losses % assume 15% for all systems

- Clearview Regional High, State of New Jersey location

- Azimuth (in accordance with specification in Proposed design)

- Tilt Angle (in accordance with specification in Proposed design)

The submission of solar energy production calculations using software other than PVWATTS SHALL NOT BE ACCEPTED.

3.22 Annual Electricity Output Reports and Minimum Electricity Output Requirement

The Selected Proposer shall provide an annual report to the Owner based on calculated versus actual electricity output, reduction in carbon footprint, and savings. This report should show monthly integrals. Such report shall be made available to the Owner within thirty (30) days of the end of the electricity output year.

It is preferred that the Selected Proposer shall guarantee a minimum energy output each year of 90% of the projected annual output based on the final design. Because of the non-export requirements, the Owner is open to negotiating this based on the scenario that the solar systems’ energy production may have to be throttled down to avoid exporting power. Each Proposal shall explain what amount of production shall be guaranteed to the Owner, and how that shall be calculated and reconciled.

3.23 Design, Engineering and Permitting

- The Proposer shall design/engineer the Solar Energy Systems to maximize the solar energy resources at the OWNER sites - taking into consideration the site's electrical demand and load patterns, proposed installation site, available solar resources, applicable permitting and zoning ordinances, installation costs, potential incentives and other relevant factors.

- For its proposed Solar Energy Systems, each Proposer shall provide a Technical Proposal that shall include design documents that communicate the following information:

  - System description

  - Equipment details & description

  - Estimated layout of installation

  - Installation plan and staging requirements

  - Electrical work

  - Warranties on equipment

  - Integration of Solar Energy System with the existing Building Electrical System at the Site

  - Site preparation, tree removal requirements and final landscaping

  - Fencing and security measures (as applicable)

  - Electrical grid interconnection requirements

  - Controls, monitors and instrumentation

  - Operation and maintenance manuals (sample)

  - Web-based performance monitoring system and communication platform that can be accessed by a link on the OWNER and/or school websites

- The Awarded Proposer will be responsible for submission of the final system layout to the Owner’s technical representatives for review.  The Awarded Proposer will be responsible for providing their own independent structural analysis for each roof to be considered.

- The awarded Proposer shall secure from governing agencies and the appropriate utility company or companies all required rights, permits, approvals, and interconnection agreements at no additional cost to the OWNER. The OWNER or its designated representative will become the signatory on applications, permits, and utility agreements where necessary.

- The Awarded Proposer shall complete and submit in a timely manner all documentation required to operate the Solar Energy Systems.

- The OWNER shall assign the rights for each system for available rebates, incentives, sale of Renewable Energy Credits and tax benefits as appropriate and requested by the Proposer.

- The awarded Proposer shall construct the Solar Energy Systems in accordance with OWNER approved plans, specifications and submittals prepared by the Proposer to meet or exceed all requirements of the OWNER. The Proposer shall install PV panels, inverters and other components that meet all of the New Jersey Board of Public Utilities rules and regulations, as well as ensure compliance with the requirements for generation and reporting of the New Jersey Board of Public Utilities for the applicable incentive programs including, but not limited to: Solar Renewable Energy Certificate Program (referred to as “Legacy SREC Program”) and/or New Jersey Solar Transition Program (also referred to as Transition Renewable Energy Certificates or TRECs), and the program which is referred to as the “Successor Solar Program” in the State of New Jersey.

- The electrical design and installation of all Solar Energy Systems shall conform to the most recent version of the National Electric Code (NEC, NFPA 70). Article 690 of the NEC applies specifically to photovoltaic system safety, protection, control and interface with other sources. Other articles of the NEC also apply. The Solar Energy Systems electrical design shall also comply with the most recent version of Institute of Electrical and Electronic Engineers (IEEE) Std. 1374- 1998 (Guide for Terrestrial Photovoltaic Power System Safety) as well as other applicable standards regarding photovoltaic power systems published by the IEEE.

- The Awarded Proposer and all its subcontractors shall be liable to the OWNER, its employees, officers, and agents for injury including bodily injury, death, damages to or destruction of property resulting, in whole or part, from any acts, errors or omission of Awarded Proposer or subcontractors in the performance of their services. The Awarded Proposer shall procure, and shall require all subcontractors to procure, prior to the commencement of services, and maintain, at its expense until final acceptance by the OWNER of all services required under the RFP and throughout the term of the PPA, insurance for liability for damages assumed under the terms to the Power Purchase Agreement, of the kinds and in the amounts provided below, with insurance companies authorized to do business in the State of New Jersey.

- All of the required insurance policies, except Worker’s Compensation, shall be endorsed to name the OWNER as an “additional insured.” The Awarded Proposer shall provide full copies of such required insurance policies and all endorsements of the same to the OWNER upon request.

3.24 PV Panels, Inverters and Other Plant Component Specifications

## Only roof-mounted ballasted PV Panels will be considered for this contract.

## The Proposer shall install Solar Energy Systems that meet all the New Jersey Board of Public Utilities rules and regulations, as well as ensure compliance with the requirements  for generation and reporting of Solar Renewable Energy Certificates or other NJCEP incentive programs as may be most advantageous to the BOE.

- It is understood that system sizing will only be confirmed after vendor site assessments including roof conditions, shading, electrical equipment size, configuration and panel locations. It is the BOEs intention that proposers have the flexibility and creativity to customize a project that maximizes system output, as well as optimizes the cost-effectiveness of the overall project; achieving the lowest possible PPA price and greatest overall cost savings. Roofing areas available for PV Panels are limited to those indicated in Appendix D.

- The Proposer shall include a detailed description of specifications and show a layout of all the PV panels, inverter(s) and all other System components, including utility required disconnect switches proposed for each facility included in the Project.  Include the total size in kW (dc) for the SES at each site as well as the physical dimensions of the panels and the physical dimensions of the space needed to mount the panels for each location included in this RFP.

- Proposers shall include a detailed description of, and drawings of, the structural attachment details for all arrays or the SES’s.  The BOE and the District Representatives must review the layout and location of all SES components.

- The electrical design and installation of all Solar Energy Systems shall conform to the most recent version of the National Electric Code (NEC, NFPA 70). Article 690 of the NEC applies specifically to photovoltaic system safety, protection, control and interface with other sources. Other articles of the NEC also apply. The Solar Energy Systems electrical design shall also comply with the most recent version of Institute of Electrical and Electronics Engineers (IEEE) Std. 1374-1998 (Guide for Terrestrial Photovoltaic Power System Safety) as well as other applicable standards regarding photovoltaic power systems published by the IEEE.

- The Photovoltaic (“PV”) panels shall meet or exceed the New Jersey Clean Energy Program requirements and shall meet or exceed the following requirements and standards:

- Qualification test standards for PV panel safety of International Electrochemical Commission (“IEC”) IEC 61215 for Crystalline Silicon panels or IEC 61646 for Thin Film panels - most recent version

- UL Standard 1703 - most recent version

- A minimum efficiency rating of 16%

- 25 - year warranty

- The inverter shall meet or exceed the most recent version of UL Standard 1741 and shall meet or exceed the New Jersey Clean Energy Program requirements.

- The inverter shall have all of the following minimum protective functions:

- AC over/under voltage

- AC under/over frequency

- Over temperature

- AC and DC over current

- DC over voltage

- Enclosure Type: NEMA 4 or NEMA 3R (steel)

- The inverter shall have all of the following minimum features:

- Maximum peak power tracking

- Overload on temperature permit

- DC and AC disconnect switch

- DC and AC voltage surge protection

- Adjustable DC ground fault

- Event log-in non-volatile memory

- NC contact for AC line breaker trip

- Wake up/sleep sequencing

- Grid synchronization

- Minimum Efficiency Rating of 95%

- The inverter shall have an enclosure type rated as NEMA 4 or NEMA 3R (steel)

- The inverter(s) shall carry a minimum warranty of 15 years

- The total connected PV capacity in KW DC shall not exceed 120% of the Continuous AC rating of the inverter capacity for any inverter.

- Metering shall be an independent revenue grade meter that meets the ANSI C12.1-2014 (accuracy requirements are required for each of the Solar Energy Systems.)

  - Design and Construction Requirements

- The Awarded Proposer inspects the solar areas listed in Appendix D and shall promptly provide information to the BOE of any potential issues with the roof areas.

- For roof areas; if it is discovered that the installation of the solar equipment does not meet the manufacturer/warrantors’ requirements, and/or voids the roof warranty, the Awarded Proposer shall be responsible to cover any and all costs associated with damage to the roof resulting from the installation of the solar equipment, and/or damage that would have been covered under the roof warranty.

- Roof Mounted Ballasted System Components: All structural members and all mounting components of the panels shall be made of aluminum, stainless steel, durable aluminum alloys as accepted by the BOE or its designated representative. Structural and mounting components of galvanized or painted steel shall not be accepted.

- The Awarded Proposer shall work cooperatively with the BOE and the District Representative’s to resolve expeditiously any water damage or leaking from the roofs once the SES are installed and throughout the Term of the PPA.  If it is determined that the roof issues and water infiltration was caused by the SES installation then the Awarded Proposer shall be responsible to pay for the repairs as performed by the BOE’s designated contractor.

- The Awarded Proposer will be responsible for confirming to the Owner's Representatives structural engineering reports that certify that the existing conditions are adequate to accommodate the weight of the system components both individually and collectively.   The Awarded Proposer will be responsible for providing their own independent structural analysis by an appropriately licensed third-party structural engineer.

- All wiring for the Solar Energy Systems shall be installed to protect against direct ground contact

- All wiring shall be protected by conduit of the appropriate type and size, no PVC conduit shall be allowed.

- All junction boxes that are not part of the solar panels or the inverter shall be a minimum of NEMA 4X rated.

- Where penetrations may be necessary shall minimize the number of penetrations. All roof penetrations shall be sealed with an acceptable sealing method that does not adversely impact the roofing system.

- All personnel and subcontractors of the awarded Proposer shall be security screened prior to being on site and the reports provided to the BOE prior to working at the schools.

- All cables, conduit, exposed conductors, and electrical boxes should be secured and supported according to code requirements.

- All exposed cables or conduits shall be sunlight resistant. All cables shall be installed in the raceway unless noted otherwise. Raceway installed below finished grade and, on the roof, shall be PVC and sunlight resistant PVC schedule 40; provide expansion fittings for all roof raceways, as required. All raceways exposed on the exterior of the buildings shall be IMC or RGS.

- Awarded Proposer shall furnish and execute a detailed commissioning/quality assurance plan for the project to the BOE for approval. The commissioning plan shall include the following steps:

  - Design-assist measures to be provided during the design of the SES.

  - SES installation checks.

  - SES functional checks including all operational and safety checks.

  - Comprehensive performance testing to verify system capacity has been achieved.

  - Maintain a written log of issues identified and corrected during the commissioning process.

- The awarded Proposer shall maintain a written log of issues identified and corrected during the commissioning process. System shall maintain roof integrity and warranties in effect at the time of installations.

- Any and all exceptions to ANY of the requirements of this RFP that are conditions of that Proposal must be specifically included as an attachment to the Proposal Form on company letterhead and signed by an authorized agent of the company. Please be aware that non- compliance with the minimum requirements of the RFP and any changes to the PPA contract MAY be disqualifying. Inclusion in the evaluation of bids process shall not be considered an acceptance of such exceptions and conditions by the BOE or its representatives.

- Restoration: The Vendor will remove the Solar Energy System from the Premises at the end of the Contract Term or upon any earlier termination of the Power Purchase Agreement. Vendor shall pay all costs and expenses of removal. Subject to any limitations arising from inclement weather, labor shortages or force majeure events, Vendor shall remove the Solar Energy System within sixty (60) days of termination or expiration of the PPA. The vendor shall restore the Board’s property (roofing, etc.) to its original condition, except for any Solar Energy System underground cabling and ordinary wear and tear.

  - Monitoring

- The awarded Proposer shall provide a turn-key data acquisition and monitoring system accessible from the internet that allows the BOE to monitor, analyze and display historical and real-time solar electricity generation data for the Solar Energy Systems. The regularly collected data should reflect, but not be limited, to the following:

- SES performance factors

- Output of the Solar Energy Systems in real time and historical

- Savings day/month/year

- CO2 lbs./day; NOx lbs./day; SOx lbs./day.

- Min & Max temperature

- Average Global Radiation (Averaged Insolation Incident on a Horizontal Surface)

- Interval Energy; Aggregate meter name; Aggregate Interval Energy (KWh); Aggregate Average

- Power (KW); Aggregate Cumulative Energy (KWh).

- The data acquisition system shall be designed for turnkey, remote operation and accessible via an internet-based website.

## Operation and Maintenance Manuals, and As – Built  Drawings

- The awarded Proposer shall provide two (2) printed sets of site-specific operation, maintenance, and parts manuals for the Solar Energy Systems, as well as an electronic version of the manual in PDF format. The awarded Proposer shall also provide two (2) printed sets of site-specific as-built wiring drawings and conduit layout of the Solar Energy Systems, as well as an electronic version in PDF format.

Section 4: Instructions & Evaluation Criteria

All proposals shall include the documents and information described in the Proposal Format section of this RFP. Please submit proposal as one PDF document including all pages. Submit proposals in 8.5” x 11” document size using a minimum 10- point font size and a standard font.

Neither Princeton Public Schools nor its consultants is liable for any costs incurred by Proposer in the preparation and/or submission of a Proposal. Any material submitted by a Proposer shall become the property of the Owner.

4.1 Questions and Communications

Questions regarding any aspect of the RFP and the proposed projects that Proposers may have must be directed to Andrew Harris and shall be answered as expeditiously and completely as possible. Applicable questions shall be responded to in a single addendum that will be distributed to all recipients of the RFP on the date noted in the Advertisement of Bid Notice.

4.2 Modifications and Clarifications

The Owner may modify the RFP at any time prior to the RFP due date, by issuance of a written addendum to all Proposers who are participating in the process. The Owner may also cancel, delay, or suspend this solicitation at its sole discretion.

4.3 Proposal Evaluation

All complete Proposals submitted by the proposal due date shall be reviewed and evaluated by the Project Team consisting of the Owner and its chosen representatives. Proposals shall be evaluated on a scale of 100 points based on the criteria indicated in the Proposal Format section of this RFP. Evaluation and selection of a Proposer is at the sole discretion of the Owner.

During the evaluation process, the Owner may request clarification or additional information from any Proposer. Interviews may be scheduled with one or more Proposers at the sole discretion of the Owner.

4.4 Proposal Format

All proposals must include the documents listed in the Proposal Checklist and described below.

| Proposal Checklist |  |
| --- | --- |
|  | Cover Letter |
|  | I. Company Profile and Qualifications |
|  | II. Scope of Services and Schedules |
|  | III. PPA Financing Terms |
|  | IV. Required Documentation |
|  | V. Official Statements by Proposers |
|  | Appendix. Supporting Information. |

4.5 Cover Letter

Provide a signed cover letter for the Proposal. Include the name and address of the Proposer, the name, address, email address, and telephone number(s) of the contact person who shall be authorized to make representations for the Proposer, and the firm’s federal tax identification. The Proposer may include any other relevant information that highlights their unique qualifications.

4.6 Proposer Profile and Qualifications (35 points)

This section shall include a brief description of the Proposer’s firm size and local organizational structure. Include a discussion of the firm’s financial stability, capacity, and resources.

Describe the demonstrated experience of the firm in developing solar PV systems, particularly on the scale described in this RFP, and describe how experience on previous projects relates to this Program. Describe experience working within school districts and other public entities in New Jersey. Describe your experience with and capacity to provide PPA financing for PV systems hosted on a variety of roof top, ground mounted, and carport systems.

As part of this section, please include the following:

- The total number and capacity of commercial and industrial PV systems completed and brought online by the Proposer in 2022, 2023, 2024, and 2025. Present this information in a table.

  - Specify how many of these systems are located in New Jersey.

  - Specify how many of these systems are located at K-12 schools.

  - Specify how many total systems the Proposer currently operates under PPAs, and the size of the smallest and largest PV systems the Proposer currently operates under a PPA.

- An organization chart for the Proposer listing executive and management positions and indicating part-time and full-time positions.

- At least three (3) references, preferably from New Jersey school districts or public entities. The Proposer may include as many as three (3) additional references that demonstrate the Proposer’s ability to complete this Project. Customers with similar site characteristics and PV system sizes as potential solar project sites are preferred. For each reference, please include:

  - Customer name

  - Number of sites and the kW capacity of each site

  - A description of the Proposer’s role in the project

  - Date the PPA contract was signed

  - Date of commercial operation

  - A contact name, email address, and telephone number

- A description of the Proposer’s experience with environmental permitting at a local and state (NJDEP) level.

- A description of the key factors required for successful solar projects.

- A description of the key points of failure for solar PPA projects.

- List of key program team members by name and position, qualifications, and experience. Specify which team member(s) will be the main contact person(s) for the Program. Include resumes for those individuals who will be involved in this Project.

- A list of all subcontractors who will work on the Solar Project, their profession (i.e., electrical) and experience.

- Insurance coverage documentation complying with this RFP.

- List of any PPAs within the last five (5) years that have been executed by the Proposer and not completed. If not complete, state the reason why and the other party to PPA.

4.7 Scope of Services and Schedule (30 points)

In this section the Proposer shall describe in detail how they will implement the Scope of Services described in this RFP. Provide a narrative and schedule addressing all work required to fulfill this scope, including the following elements:

- Project Schedule

Provide a solar project schedule showing the expected timeline for completion of the work. Include milestones for major work tasks including site evaluation, system design, permitting and approvals, construction commencement, shutdown dates, construction completion, final inspections/approvals, commercial operation.

- Equipment and Warranties

Provide information about the manufacturer and/or models of PV modules, inverters, racking equipment and batteries. Indicate where the PV modules and other major equipment is manufactured. Provide details about the equipment and labor provided by the Proposer and/or manufacturer. Please indicate what the warranty claim procedure will be for the Owner.

- Services by Other

Identify which elements of the Scope of Services (finance, design, construction, maintenance, or other services) will be managed by a partner, subcontractor, or third party other than the Proposer. Describe how the Proposer will maintain accountability for the quality and timeliness of the completion of the full Scope of Services.

- Permitting and Interconnection Expediting Plan

Provide a description of the Proposer’s method of and capacity to expedite all incentive filing, permitting and interconnection requirements with relevant state and local agencies.

- Operations and Maintenance Plan: Billing

Provide details about the operations and maintenance plan and services provided under the PPA. Describe who will be providing the operations and maintenance support for the life of the agreement. Describe billing process under the PPA.

- Fire Safety

Provide “Firefighters Safety Procedure” manual in case of the event of a fire occurring within the rooftop solar panels. It is the responsibility of the Proposer to receive approval(s) from the single and/or multiple Jurisdiction Holding Authority (“JHA”) for an acceptable “Firefighters Safety Procedure.”

- Additional Services

The Proposer may choose to describe any additional services that can be offered to the Project Sites on an optional basis. Briefly describe how these services would be evaluated, priced, and implemented. Indicate whether services could be included in the PPA financing.

- Roofing, electrical, and/or structural repairs necessary for the installation of a PV system.

- Emergency back-up energy storage and off-grid capability.

- Solar thermal (hot water) systems.

- Any other relevant optional services that align with the goals described in this RFP.

4.8 Proposal Price and Total Savings (35 points)

This section shall include the pricing to be provided to the Owner.

Please summarize the key characteristics and benefits of the proposed PPA, and provide the following:

- Power Purchase Agreement Offer

Provide a PPA Offer using the Price Proposal Sheet provided in the Appendices of this RFP. Please indicate if the Proposer intends to sell or transfer ownership of the PPA within three (3) years of the Commercial Operation Date. Proposers MUST provide with their Proposal a template PPA version that the Proposer intends to use, subject to the Owner’s review and approval.

The Proposer may also provide additional PPA Offers that it believes are beneficial to the Owner. Clearly specify the contingencies to which this Offer is subject, and how these contingencies shall be evaluated.

- PPA Escalator not to Exceed 2.2%

If the PPA rate is to include an escalator, it is not to exceed 2.2% annually.

- Additional Costs

The Proposal must indicate any potential or likely additional costs or actions that may be required on the part of the Owner for project realization that would add to project costs above and beyond the PPA Rate offered. The Owner shall have no financial responsibilities other than the proposed rate with escalation.

- Hourly Production Reports

Provide hourly production reports for each site in Microsoft Excel format.

4.9 Required Documentation

All Proposers must include with their submission:

- The two most recent fiscal years of Financial Statements for the Respondent(s), including at a minimum balance sheet and operating statements

- Proposal Form

- A valid State of New Jersey Business Registration Certificate

- Public Works Contractor Certificate

- Notice Disclosure of Contributions to New Jersey Election Law Enforcement

- Total Amount of Uncompleted Contracts form DPMC 701

- Consent of Surety Form

- Proposal Bond or Agreement for Proposal Security in lieu of Proposal Bond

- Statement of Ownership Disclosure

- Non-Collusion Affidavit

- Statement of Respondent’s Qualifications

- Acknowledgement of Receipt of Addenda

- Affirmative Action Compliance Notice/EEO Mandatory Language

- American with Disabilities Act of 1990 Compliance

- No Debarment/Suspension/Disqualification Affidavit

- Federal Debarment/ Suspension/Disqualification Affidavit

- No Material Change of Circumstances Affidavit

- Notice of Classification from DPMC, as issued by the State of New Jersey, Department of Treasury, Division of Property Management and Construction (DPMC) for C035 Solar Energy Systems and C047 Electrical

- Disclosure of Investment Activities in Iran

- Certification of Non-Involvement in Prohibited Activities in Russia or Belarus

- Letter of Financing Guarantee

- Proposer procedure for criminal history records checks

- Template PPA version to be used, pending the Owner review

4.10 Official Statement by Proposers

Proposals must contain the following certified statements with attestation by a person authorized to bind the Proposer to this RFP response:

- Proposer has read and agrees to the terms and conditions set forth in the RFP.

- The terms and conditions set forth in the proposal shall remain in effect for at least sixty (60) days from date of proposal submission.

- Any comments the Proposer would like to make to this RFP.

- Who the financier and/or owner will be for the life of the Power Purchase Agreement.

Appendices

Appendix A – Proposal Form

# PROPOSAL DATE:		_______________

# PROJECT:	Princeton Public Schools Solar Energy Power Purchase Agreement

# Proposal Submitted By:			____________________________________							(Name)												____________________________________

# ____________________________________							(Address)

# _____________________________________                   	(Telephone)

# _____________________________________ (Facsimile)

# _____________________________________		(E-Mail)

# List all entities if a joint venture

# and identify lead entity:			__________________________________

# __________________________________

# __________________________________

BASE PROPOSAL

Year One (1) Price

(4 decimal points)				___________________   $/kWh

# Escalation Factor

# (2 decimal points)				___________________  %

# Appendix B – EXPECTED AND GUARANTEED ANNUAL kWh PRODUCTION

# Provide annual calculations, using PV watts or similar industry accepted software to determine annual expected and guaranteed kWh (ac) production for each year of the proposed PPA by location. Provide all assumptions in calculations, including system size, KWdc, tilt, azimuth and de-rate factor. Proposals for PPA are based on a 15-year term consistent with RFP.

# Annual kWh production (AC) for each year of the proposed 15-year PPA. Provide all assumptions in calculation including system size, KWdc, tilt, azimuth and de-rate factor.

|  | # Expected | # Guaranteed |
| --- | --- | --- |
| # Year 1 | # ___________ kWh | # ___________ kWh |
| # Year 2 | # ___________ kWh | # ___________ kWh |
| # Year 3 | # ___________ kWh | # ___________ kWh |
| # Year 4 | # ___________ kWh | # ___________ kWh |
| # Year 5 | # ___________ kWh | # ___________ kWh |
| # Year 6 | # ___________ kWh | # ___________ kWh |
| # Year 7 | # ___________ kWh | # ___________ kWh |
| # Year 8 | # ___________ kWh | # ___________ kWh |
| # Year 9 | # ___________ kWh | # ___________ kWh |
| # Year 10 | # ___________ kWh | # ___________ kWh |
| # Year 11 | # ___________ kWh | # ___________ kWh |
| # Year 12 | # ___________ kWh | # ___________ kWh |
| # Year 13 | # ___________ kWh | # ___________ kWh |
| # Year 14 | # ___________ kWh | # ___________ kWh |
| # Year 15 | # ___________ kWh | # ___________ kWh |

I certify that I, _____________, am the 					 of the Proposer submitting this proposal and that I am authorized to submit this bid on behalf of the proposer and that the information contained on all of the proposal documents is true and accurate. I am aware that if any of the foregoing statements made by me are willfully false, I am subject to punishment.

Witness:

(Affix corporate seal)							Authorized Representative

Title:

Appendix C – Roofing Areas & Preferred Array Locations

Appendix D – Acknowledgement of Addenda

RFP [insert] 				   Proposal Date: [insert]

The Respondent acknowledges receipt of the hereinafter enumerated Addenda which has been

issued during the period of bidding and agrees that said Addenda shall become a part of this

contract. The respondent shall list below the numbers and issuing dates of the Addenda.

ADDENDA NO. 				ISSUING DATES

_________________________		__________________________

_________________________		__________________________

_________________________		__________________________

_________________________		__________________________

- NO ADDENDA RECEIVED

Name of Company ___________________________________________________________

Address___________________________________________ P.O. Box _________________

City, State, Zip Code _________________________________________________________

Name of Authorized Representative _____________________________________________

Signature ___________________________________ Title __________________________

Other Appendices – Other Required Forms, Disclosures, Certificates, Statements, etc.

The appendices on the following pages contain required information and documents that are to be included with proposals.

Appendix E – Form of Consent of Surety for Construction Performance Bond

FORM OF CONSENT OF SURETY

PERFORMANCE BOND, PAYMENT BOND and MAINTENANCE BOND

For and in consideration of the sum of one dollar ($1.00) lawful money of the United States, the receipt is hereby acknowledged, paid to the undersigned surety, and for other valuable consideration, the undersigned surety, authorized to transact business in the State of _________________, certifies and agrees that if the Contract entitled: _____________________ ______________________________________________________________________________

CONTRACT: __________     _____________________________________________________

(NUMBER)	(TITLE)

is awarded to: _________________________________________________________________

(BIDDER’S NAME)

the undersigned hereby warrants that it is in all respects qualified to provide the required Bonds as set forth in the Contract Documents, and that it will provide and execute the Performance Bond in the full amount of awarded contract in the event that said contractor is awarded a contract for the above project, the Payment Bond, and the Maintenance Bond in the form and as otherwise required by the Contract Documents.

_______________________________

(Print Name of Surety)

_________________________________		____________________________________

(Print Name of Attorney-in-Fact)			(Signature of Attorney-in-Fact)

CERTIFICATE (to be completed by an authorized certifying agent for each surety)

I, ______________________, as ___________________ for ___________________, a corporation/mutual insurance company/other (circle one) domiciled in _____________________, DO HEREBY CERTIFY that, to the best of my knowledge, the foregoing statements made by me are true, and ACKNOWLEDGE that, if any of those statements are false, this bond is VOIDABLE.

_________________________________

(Signature of certifying agent)

_________________________________

(Printed name of certifying agent)

_________________________________

(Title of certifying agent)

ATTACH AND SUBMIT WITH THE BID: A POWER OF ATTORNEY FOR THE ATTORNEY -IN- FACT WHICH IS CURRENTLY DATED AND VALID FOR THE TOTAL AMOUNT OF ALL BONDS.

NOTE: IF SUBCONTRACTORS ARE LISTED ON BID FORM, N.J.S.A. 18A:18A-18 REQUIRES THAT EVIDENCE OF PERFORMANCE SECURITY AS TO SUBCONTRACTORS BE SUBMITTED WITH THE BID, EITHER BE THE BIDDER ON ITS OWN BEHALF AND ON BEHALF OF ALL LISTED SUBCONTRACTORS, OR BY EACH SUBCONTRACTOR, OR ANY COMBINATION THEREOF, PROVIDED THAT THE PERFORMANCE SECURITY IN TOTAL EQUALS, BUT DOES NOT EXCEED, THE TOTAL AMOUNT OF THE BID.

CONSENT OF SURETY

Appendix F – Form of Construction Performance Bond

FORM OF CONSTRUCTION PERFORMANCE BOND

Date: ______________________

___________________________________________________, PRINCIPAL

___________________________________________________, SURETY

___________________________________________________, SURETY

___________________________________________________, SURETY

THE [SPECIFIC NAME TO BE ADDED BASED ON EACH PPA], NEW JERSEY, OBLIGEE

KNOW ALL MEN BY THESE PRESENTS, that we, the PRINCIPAL and SURETY(IES) above named, are held and firmly bound unto the above named OBLIGEE, in the just and full sum of _________________________________________($____________________) for the payment of which sum well and truly to be made, the said PRINCIPAL and SURETY(IES) bind themselves, their respective heirs, administrators, executors, successors and assigns, jointly and severally, firmly by these presents. Provided, that, we, the Sureties, bind ourselves in such sum “jointly and severally” as well as “severally” only for the purpose of allowing a joint action or actions against any or all of us, and for all other purposes each Surety binds itself, jointly and severally with the PRINCIPAL, for the payment of such sum only as is set forth opposite the name of such Surety at the end of this Bond.

WHEREAS, the PRINCIPAL has entered into a certain written agreement with the OBLIGEE, dated ____________________, known as the Solar Power Purchase Agreement (the “Agreement”), whereby the PRINCIPAL shall provide construction related services to OBLIGEE, which Agreement is by reference made a part hereof, as if set forth in full herein.

NOW THEREFORE, the condition of this obligation is such that, if the PRINCIPAL shall faithfully perform its obligations under the Agreement as they relate to the engineering, procurement of materials, construction and installation of the Renewable Energy Projects at various Obligee-owned property and interconnecting with an Obligee-owned facility (the “Construction Obligations”), then this obligation shall be null and void, otherwise it shall remain in full force and effect.

PROVIDED, HOWEVER:

Whenever the PRINCIPAL shall be, and is, declared to be in default of its Construction Obligations by the OBLIGEE, the OBLIGEE having performed its obligations under the Agreement, the SURETIES may promptly remedy the default or shall promptly as follows:

- Perform the Construction Obligations in accordance with the terms and conditions of the Agreement and the RFP, or

- Obtain a proposal or proposals for performance of the Construction Obligations, and upon a determination by SURETIES and the OBLIGEE of the lowest responsible respondent, arrange for a contract between such respondent and the OBLIGEE, and make available as services continue (even though there should be a default or a succession of defaults under the contract or contracts arranged under this paragraph) sufficient funds to pay the cost of performance of such Construction Obligations; but not exceeding, including other costs and damages for which the SURETIES may be liable hereunder, the amount set forth in the first paragraph hereof.

- After investigation, determine the amount for which it may be liable to the OBLIGEE and, as soon as practicable after the amount is determined, tender payment therefore to the OBLIGEE.

- Without waiver of any rights of the OBLIGEE, notify the OBLIGEE of the denial of liability in whole or in part citing reasons, therefore.

Notwithstanding any term or condition contained in the Agreement to the contrary, it is understood and agreed that the PRINCIPAL’s and SURETIES’ obligation under this bond shall not be assigned without the written consent of the PRINCIPAL and the SURETIES, which consent shall not unreasonably be withheld.

No right or action shall accrue on this bond to or for the use of any person or corporation other than the OBLIGEE named herein or their heirs, executors, administrators, or successors of the OBLIGEE.

The PRINCIPAL and the SURETIES shall not be liable to the OBLIGEE in the aggregate in excess of the penal sum above stated. Any payment made by the SURETIES in good faith under this bond shall reduce the bond amount stated by a like amount.

The SURETIES hereby stipulate and agree that no modifications, omissions, or additions in or to the terms of the Agreement or in or to the RFP and specifications therefore should in any way affect the obligation of the SURETIES on this Bond.

IN WITNESS WHEREOF, the above-bounded parties have executed this instrument under their several seals on the date indicated above.

PRINCIPAL

Limit: $_______________________________ Title

SURETY

Limit: $_______________________________ Attorney-in-fact

SURETY

Limit: $_______________________________ Attorney-in-fact

Countersigned:

______________________________________

IN WITNESS WHEREOF, the undersigned has caused these presents to be signed and attested by a duly authorized officer, and its corporate seal to be hereto affixed this ________ day of ______________________, 2026.

ATTEST:

[Name of Surety]

By: _________________________________          By: _________________________________

Name: ______________________________	           Name: ______________________________

Title: _______________________________           Title: ________________________________

Date: _______________________________	           Date: _______________________________

Appendix G – Agreement for Proposal Security in Lieu of Proposal Bond

(This form is to be completed if the Proposer does not provide a proposal bond

with its Proposal.)

This Proposal is accompanied by proposal security in the form of a Certified Check or Cashier's Check drawn on the

__________________________________________________________________

(name of banking institution)

__________________________________________________________________

(address of banking institution)

__________________________________________________________________

in the amount of Twenty Thousand ($20,000) Dollars.

The undersigned Respondent hereby agrees that if its Proposal shall be accepted by Princeton Public Schools, and the undersigned shall fail to execute and deliver the Services to be performed pursuant to the Power Purchase Agreements and the Request for Proposals, and provide the Construction Performance Bond within ten (10) days of the issuance of a Notice to Proceed by the Owner in accordance with the terms and requirements of the Request for Proposals, the Power Purchase Agreements, and other Contract Documents, then the undersigned shall be deemed to have abandoned the Power Purchase Agreements, and thereupon the Proposal and its acceptance shall be null and void. In such event, the certified or cashier's check herewith submitted as the Proposal security shall be due and payable thereunder to Princeton Public Schools as liquidated damages; otherwise said check or the amount thereof, shall be returned to the undersigned concurrently upon the issuance of a Notice to Proceed, if any, by the Owner, and the receipt by the Owner of the Successful Respondent’s Construction Performance Bond.

The undersigned Respondent hereby understands and agrees that the Successful Respondent’s Construction Performance Bond shall be submitted to the Owner upon the issuance of a Notice to Proceed, which may be issued by the Owner at any time during the Power Purchase Agreements. The undersigned Respondent hereby understands and agrees that the Owner shall retain the Successful Respondent’s certified check or cashier’s check submitted as the proposal security until the issuance of a Notice to Proceed by the Owner, and the receipt by the Owner of the Successful Respondent’s Construction Performance Bond.

[Signature on Next Page]

[NAME OF RESPONDENT]

By: __________________________________________

Attach Cashier’s Check or Certified Check

Payable to the order

Print Name: ___________________________________

Princeton Public Schools, Title

Appendix H – Form of Proposal Bond

(This form is to be completed if the respondent provides a proposal bond with its proposal instead of a certified check or cashier’s check.)

KNOW ALL MEN BY THESE PRESENTS, that, [NAME OF RESPONDENT], as Principal (hereinafter, the “Principal”) and [NAME OF SURETY], a [Corporation] [Partnership] duly organized under the laws of the State of __________________ as Surety (hereinafter, the “Surety”), are held and firmly bound unto Princeton Public Schools, as Obligee (hereinafter, the “Obligee”), in the sum of TWENTY THOUSAND ($20,000) DOLLARS lawful money of the United States of America, for which payment well and truly to be made, the said Principal and Surety bind ourselves, our successors, and assigns, jointly and severally, firmly by these presents.

WHEREAS, the Principal has submitted or is about to submit to the Obligee a Proposal for the provision of certain Services, which Proposal is made a part hereof;

NOW THEREFORE, the Surety hereby understands that if the said Proposal is accepted and the Power Purchase Agreements (the “Agreements”) be awarded to the Respondent, said Principal will execute the Agreement and give the Construction Performance Bond with Surety acceptable to the Obligee for the faithful performance of Obligee’s Construction Obligations, or if the Principal shall fail to enter such agreement and give such Construction Performance Bond, then the Principal shall be deemed to have abandoned the Services and the Agreements, and thereupon the Proposal and its acceptance shall be null and void. In such event, Surety hereby agrees that it will pay to the Obligee the Penal amount of this Proposal Bond as liquidated damages; otherwise the said Bond shall be returned to the undersigned concurrently upon the issuance of a Notice to Proceed, if any, by the Obligee, and the receipt by the Obligee of the Successful Respondent’s Construction Performance Bond.

It is agreed that this Proposal Bond shall be effective on the date the Proposal is submitted and will continue in full force until the issuance of a Notice to Proceed by the Obligee, and the receipt by the Obligee of the Successful Respondent’s Construction Performance Bond.

[Signature on Next Page]

SIGNED AND SEALED this _____ day of _________________2026.

In the presence of:

___________________________________ (Seal) PRINCIPAL

___________________________________

WITNESS

___________________________________

TITLE

___________________________________

WITNESS

___________________________________

TITLE

____________________________________ (Seal) SURETY

Appendix I – Statement of Ownership Disclosure

STATEMENT OF OWNERSHIP DISCLOSURE

N.J.S.A. 52:25-24.2 (P.L. 1977, c.33, as amended by P.L. 2016, c.43)

This statement shall be completed, certified to, and included with all Proposal Submissions.

Failure to submit the required information is cause for automatic rejection of the Proposal.

Name of Organization: ___________________________________________________

Organization Address: ___________________________________________________

Part I Check the box that represents the type of business organization:

Sole Proprietorship (skip Parts II and III, execute certification in Part IV)

Non-Profit Corporation (skip Parts II and III, execute certification in Part IV)

For-Profit Corporation (any type)

Limited Liability Company (LLC)

Partnership

Limited Partnership

Limited Liability Partnership (LLP)

Other (be specific): ________________________________________

Part II The list below contains the names and addresses of all stockholders in the corporation

who own 10 percent or more of its stock, of any class, or of all individual partners in the

partnership who own a 10 percent or greater interest therein, or of all members in the limited

liability company who own a 10 percent or greater interest therein, as the case may be.

(COMPLETE THE LIST BELOW IN THIS SECTION)

OR

No one stockholder in the corporation owns 10 percent or more of its stock, of any class, or no

individual partner in the partnership owns a 10 percent or greater interest therein, or no

member in the limited liability company owns a 10 percent or greater interest therein, as the

case may be. (SKIP TO PART IV)

(Please attach additional sheets if more space is needed):

| Name of Individual or Business Entity | Home Address (for Individuals) or Business Address |
| --- | --- |

Part III DISCLOSURE OF 10% OR GREATER OWNERSHIP IN THE STOCKHOLDERS, PARTNERS OR LLC MEMBERS LISTED IN PART II

If a Bidder has a direct or indirect parent entity which is publicly traded, and any person holds a 10 percent or greater beneficial interest in the publicly traded parent entity as of the last annual federal Security and Exchange Commission (SEC) or foreign equivalent filing, ownership disclosure can be met by providing links to the website(s) containing the last annual filing(s) with the federal Securities and Exchange Commission (or foreign equivalent) that contain the name and address of each person holding a 10% or greater beneficial interest in the publicly traded parent entity, along with the relevant page numbers of the filing(s) that contain the information on each such person. Attach additional sheets if more space is needed.

| Website (URL) containing the last annual SEC (or foreign equivalent) filing | Page #’s |
| --- | --- |

Please list the names and addresses of each stockholder, partner or member owning a 10

percent or greater interest in any corresponding corporation, partnership and/or limited liability

company (LLC) listed in Part II other than for any publicly traded parent entities referenced

above. The disclosure shall be continued until names and addresses of every non-corporate

stockholder, and individual partner, and member exceeding the 10 percent ownership criteria

established pursuant to N.J.S.A. 52:25-24.2 has been listed. Attach additional sheets if more

space is needed.

| Stockholder/Partner/Member and Corresponding Entity Listed in Part II | Home Address (for Individuals) or Business Address |
| --- | --- |

Part IV  Certification

I, being duly sworn upon my oath, hereby represent that the foregoing information and any

attachments thereto to the best of my knowledge are true and complete. I acknowledge: that I

am authorized to execute this certification on behalf of the bidder/Bidder; that Princeton Public Schools is relying on the information contained herein and that I am under a continuing obligation from the date of this certification through the completion of any

contracts with Princeton Public Schools to notify the Owner in writing of any changes to the information contained herein; that I am aware that it is a criminal offense to make a false statement or misrepresentation in this certification, and if I do so, I am subject to criminal prosecution under the law and that it will constitute a material breach of my agreement(s) with Princeton Public Schools, permitting Princeton Public Schools to declare any contract(s) resulting from this certification void and unenforceable.

| Full Name (Print): |  | Title: |  |
| --- | --- | --- | --- |
| Signature: |  | Date: |  |

SIGN AND NOTARIZE THIS FORM AND PROVIDE ALL THE DOCUMENTATION REQUESTED

Appendix J – Non-Collusion Affidavit

State of _____________________________  	)

)

County of____________________________	)

I, _____________________________________of the City of ___________________________ in the County of ____________________ and State of _____________________ of full age, being duly sworn according to law on my oath depose and say that:

I am ____________________________ of the firm of ______________________________,

(Title or position)					(Name of firm)

the Respondent making this Proposal for Princeton Public Schools Renewable Energy Program, and that I executed the said Proposal with full authority so to do; that said Respondent has not directly or indirectly entered into any agreement, participated in any collusion, or otherwise taken any action in restraint of free, competitive contracting in connection with the above named Program; and that all statements contained in said Proposal and in this affidavit are true and correct, and made with full knowledge that the Owner relies upon the truth of the statements contained in said Proposal and in the statements contained in this affidavit in awarding the contract for the said Program.

I further warrant that no person or selling agency has been employed or retained to solicit or secure such contract upon an agreement or understanding for a commission, percentage, brokerage, or contingent fee, except bona fide employees or bona fide employees or bona fide established commercial or selling agencies maintained by ______________________________.

SUBSCRIBED AND SWORN to before me this ______ day of____________________ , 2026.

__________________________________		____________________________________

Notary Public of 					Signature

(Type or print name of affiant under Signature)

Commission Expires: _____________________

(Seal)

A NOTARIZED NON-COLLUSION AFFIDAVIT SHALL BE INCLUDED WITH PROPOSAL SUBMISSION

Appendix K – Affirmative Action Compliance/Mandatory EEO Language

This form is a summary of the Successful Respondent’s requirement to comply with the requirements of N.J.S.A. 10:5-31 and N.J.A.C. 17:27-1, et seq.

The Successful Respondent shall submit to the West Windsor-Plainsboro Regional School District after notification of award but prior to execution of the contract, one of the following three documents as forms of evidence.

- A photocopy of a valid letter that the contractor is operating under an existing Federally approved or sanctioned affirmative action program (good for one year from the date of the letter);

OR

- A photocopy of a Certificate of Employee Information Report approval, issued in accordance with N.J.A.C. 17:27-4;

OR

- A photocopy of an Employee Information Report (Form AA302) provided by the Division and distributed to the public agency to be completed by the contractor in accordance with N.J.A.C. 17:27-4.

The Successful Respondent may obtain the Affirmative Action Employee Information Report (AA302) from the contracting unit during normal business hours. The Successful Respondent must submit the copies of the AA302 Report to the Division of Contract Compliance and Equal Employment Opportunity in Public Contracts (Division). The public agency copy is submitted to the District and the vendor copy is retained by the Successful Respondent.

The undersigned Respondent certifies that he/she is aware of the commitment to comply with the requirements of N.J.S.A. 10:5-31 and N.J.A.C. 17:27.1, et seq. and agrees to furnish the required forms of evidence. The undersigned Respondent further understands that its Proposal shall be rejected as non-responsive if Respondent fails to comply with the requirements of N.J.S.A. 10:5- 31 and N.J.A.C. 17:27-1, et seq.

Respondent:_____________________________________________

Signature:_______________________________________________

Print Name:______________________________________________

Title:____________________________________________________

Date:____________________________________________________

NOTICE: The successful Bidder shall comply with the following upon award of contract for services:

MANDATORY EQUAL EMPLOYMENT OPPORTUNITY LANGUAGE

N.J.S.A. 10:5-31 et seq. (P.L. 1975, C. 127)

N.J.A.C. 17:27

CONSTRUCTION CONTRACTS

During the performance of this contract, the contractor agrees as follows:

contractor or subcontractor, where applicable, will not discriminate against any employee or applicant for employment because of age, race, creed, color, national origin, ancestry, marital status, affectional or sexual orientation, gender identity or expression, disability, nationality or sex. Except with respect to affectional or sexual orientation and gender identity or expression, the contractor will ensure that equal employment opportunity is afforded to such applicants in

recruitment and employment, and that employees are treated during employment, without

regard to their age, race, creed, color, national origin, ancestry, marital status, affectional or sexual orientation, gender identity or expression, disability, nationality or sex. Such equal employment opportunity shall include, but not be limited to the following: employment, upgrading, demotion, or transfer; recruitment or recruitment advertising; layoff or termination; rates of pay or other forms of compensation; and selection for training, including apprenticeship. The contractor agrees to post in conspicuous places, available to employees and applicants for employment, notices to be provided by the Public Agency Compliance Officer setting forth provisions of this nondiscrimination clause.

The contractor or subcontractor, where applicable will, in all solicitations or advertisements for employees placed by or on behalf of the contractor, state that all qualified applicants will receive consideration for employment without regard to age, race, creed, color, national origin, ancestry, marital status, affectional or sexual orientation, gender identity or expression, disability, nationality or sex.

The contractor or subcontractor will send to each labor union, with which it has a

collective bargaining agreement, a notice, to be provided by the agency contracting officer,

advising the labor union or workers' representative of the contractor's commitments under this

act and shall post copies of the notice in conspicuous places available to employees and

applicants for employment.

The contractor or subcontractor, where applicable, agrees to comply with any regulations promulgated by the Treasurer, pursuant to N.J.S.A. 10:5-31 et seq., as amended and supplemented from time to time and the Americans with Disabilities Act.

When hiring or scheduling workers in each construction trade, the contractor or

subcontractor agrees to make good faith efforts to employ minority and women workers in each

construction trade consistent with the targeted employment goal prescribed by N.J.A.C. l7:27-

7.2; provided, however, that the Dept. of LWD, Construction EEO Monitoring Program may, in

its discretion, exempt a contractor or subcontractor from compliance with the good faith

procedures prescribed by the following provisions, A, B and C, as long as the Dept. of LWD,

Construction EEO Monitoring Program is satisfied that the contractor or subcontractor is

employing workers provided by a union which provides evidence, in accordance with standards

prescribed by the Dept. of LWD, Construction EEO Monitoring Program, that its percentage of

active "card carrying" members who are minority and women workers is equal to or greater than

the targeted employment goal established in accordance with N.J.A.C. l7:27-7.2.

The contractor or subcontractor agrees that a good faith effort shall include compliance

with the following procedures:

- If the contractor or subcontractor has a referral agreement or arrangement with a union for a construction trade, the contractor or subcontractor shall, within three business days of the contract award, seek assurances from the union that it will cooperate with the contractor or subcontractor as it fulfills its affirmative action obligations under this contract and in accordance with the rules promulgated by the Treasurer pursuant to N.J.S.A. 10:5- 31 et. seq., as supplemented and amended from time to time and the Americans with Disabilities Act. If the contractor or subcontractor is unable to obtain said assurances from the construction trade union at least five business days prior to the commencement of construction work, the contractor or subcontractor agrees to afford equal employment opportunities minority and women workers directly, consistent with this chapter. If the contractor's or subcontractor's prior experience with a construction trade union, regardless of whether the union has provided said assurances, indicates a significant possibility that the trade union will not refer sufficient minority and women workers consistent with affording equal employment opportunities as specified in this chapter, the contractor or subcontractor agrees to be prepared to provide such opportunities to minority and women workers directly, consistent with this chapter, by complying with the hiring or scheduling procedures prescribed under (B) below; and the contractor or subcontractor further agrees to take said action immediately if it determines that the union is not referring minority and women workers consistent with the equal employment opportunity goals set forth in this chapter.

- If good faith efforts to meet targeted employment goals have not or cannot be met for each construction trade by adhering to the procedures of (A) above, or if the contractor does not have a referral agreement or arrangement with a union for a construction trade, the contractor or subcontractor agrees to take the following actions:

(l) To notify the public agency compliance officer, the Dept. of LWD, Construction EEO Monitoring Program, and minority and women referral organizations listed by the Dept. of LWD, Construction EEO Monitoring Program pursuant to N.J.A.C. 17:27-5.3, of its workforce needs, and request referral of minority and women workers;

(2) To notify any minority and women workers who have been listed with it as awaiting available vacancies;

(3) Prior to commencement of work, to request that the local construction trade union refer minority and women workers to fill job openings, provided the contractor or subcontractor has a referral agreement or arrangement with a union for the construction trade;

(4) To leave standing requests for additional referral to minority and women workers with the local construction trade union, provided the contractor or subcontractor has a referral agreement or arrangement with a union for the construction trade, the State Training and Employment Service and other approved referral sources in the area;

(5) If it is necessary to lay off some of the workers in a given trade on the construction site, layoffs shall be conducted in compliance with the equal employment opportunity and non-discrimination standards set forth in this regulation, as well as with applicable Federal and State court decisions;

(6) To adhere to the following procedure when minority and women workers apply or are referred to the contractor or subcontractor:

- The contractor or subcontractor shall interview the referred minority or women worker.

- If said individuals have never previously received any document or certification signifying a level of qualification lower than that required in order to perform the work of the construction trade, the contractor or subcontractor shall in good faith determine the qualifications of such individuals. The contractor or subcontractor shall hire or schedule those individuals who satisfy appropriate qualification standards in conformity with the equal employment opportunity and non-discrimination principles set forth in this chapter. However, a contractor or subcontractor shall determine that the individual at least possesses the requisite skills, and experience recognized by a union, apprentice program or a referral agency, provided the referral agency is acceptable to the Dept. of LWD, Construction EEO Monitoring Program. If necessary, the contractor or subcontractor shall hire or schedule minority and women workers who qualify as trainees pursuant to these rules. All of the requirements, however, are limited by the provisions of (C) below.

- The name of any interested women or minority individual shall be maintained on a waiting list and shall be considered for employment as described in (i) above, whenever vacancies occur. At the request of the Dept. of LWD, Construction EEO Monitoring Program, the contractor or subcontractor shall provide evidence of its good faith efforts to employ women and minorities from the list to fill vacancies.

- If, for any reason, said contractor or subcontractor determines that a minority individual or a woman is not qualified or if the individual qualifies as an advanced trainee or apprentice, the contractor or subcontractor shall inform the individual in writing of the reasons for the determination, maintain a copy of the determination in its files, and send a copy to the public agency compliance officer and to the Dept. of LWD, Construction EEO Monitoring Program.

(7) To keep a complete and accurate record of all requests made for the referral of workers in any trade covered by the contract, on forms made available by the Dept. of LWD, Construction EEO Monitoring Program and submitted promptly to the Dept. of LWD, Construction EEO Monitoring Program upon request.

- The contractor or subcontractor agrees that nothing contained in (B) above shall

preclude the contractor or subcontractor from complying with the union hiring hall or

apprenticeship policies in any applicable collective bargaining agreement or union hiring hall

arrangement, and, where required by custom or agreement, it shall send journeymen and

trainees to the union for referral, or to the apprenticeship program for admission, pursuant to

such agreement or arrangement. However, where the practices of a union or apprenticeship

program will result in the exclusion of minorities and women or the failure to refer minorities

and women consistent with the targeted county employment goal, the contractor or

subcontractor shall consider for employment persons referred pursuant to (B) above without

regard to such agreement or arrangement; provided further, however, that the contractor or

subcontractor shall not be required to employ women and minority advanced trainees and

trainees in numbers which result in the employment of advanced trainees and trainees as a

percentage of the total workforce for the construction trade, which percentage significantly

exceeds the apprentice to journey worker ratio specified in the applicable collective bargaining

agreement, or in the absence of a collective bargaining agreement, exceeds the ratio established

by practice in the area for said construction trade. Also, the contractor or subcontractor agrees

that, in implementing the procedures of (B) above, it shall, where applicable, employ minority

and women workers residing within the geographical jurisdiction of the union.

After notification of award, but prior to signing a construction contract, the contractor shall

submit to the public agency compliance officer and the Dept. of LWD, Construction EEO

Monitoring Program an initial project workforce report (Form AA 201) electronically provided to

the public agency by the Dept. of LWD, Construction EEO Monitoring Program, through its

website, for distribution to and completion by the contractor, in accordance with N.J.A.C. 17:27-

7. The contractor also agrees to submit a copy of the Monthly Project Workforce Report once a

month thereafter for the duration of this contract to the Department of LWD, Construction EEO

Monitoring Program, and to the public agency compliance officer.

The contractor agrees to cooperate with the public agency in the payment of budgeted funds,

as is necessary, for on-the-job and/or off-the-job programs for outreach and training of

minorities and women.

- The contractor and its subcontractors shall furnish such reports or other documents to the Dept. of LWD, Construction EEO Monitoring Program as may be requested by the Dept. of LWD, Construction EEO Monitoring Program from time to time in order to carry out the purposes of these regulations, and public agencies shall furnish such information as may be requested by the Dept. of LWD, Construction EEO Monitoring Program for conducting a compliance investigation pursuant to N.J.A.C. 17:27-1.1, et seq.

Appendix L – Disclosure of Investment Activities in Iran

Disclosure of Investment Activities in Iran

| Person or Entity: |  |
| --- | --- |

Part 1: Certification

BIDDERS ARE TO COMPLETE PART 1 BY CHECKING EITHER BOX.

Pursuant to Public Law 2012, c. 25, any person or entity that submits a bid or proposal or otherwise proposes to enter into or renew a contract must complete the certification below to attest, under penalty of perjury, that neither the person or entity, nor any of its parents, subsidiaries, or affiliates, is identified on the Department of Treasury's Chapter 25 list as a person or entity engaging in investment activities in Iran. The Chapter 25 list is found on the N.J. Division of Purchase and Property website at www.state.nj.us/treasury/purchase/pdf/Chapter25List.pdf. Bidders must review this list prior to completing the below certification. Failure to complete the certification may render a bidder's proposal non-responsive. If a person or entity is found to be in potential violation of law, the matter shall be referred to the State Attorney General who shall take action as may be appropriate and provided by law, rule or contract, including but not limited to, imposing sanctions, seeking compliance, recovering damages, declaring the party in default and seeking debarment or suspension of the party.

CHECK THE APPROPRIATE BOX:

|  | I certify, pursuant to Public Law 2012, c. 25, that neither the bidder listed above nor any of the bidder's parents, subsidiaries, or affiliates is listed on the N.J. Department of the Treasury’s list of entities determined to be engaged in prohibited activities in Iran pursuant to P.L. 2012, c. 25 ("Chapter 25 List"). I further certify that I am the person listed above, or I am an officer or representative of the entity listed above and am authorized to make this certification on its behalf. I will skip Part 2 and sign and complete the Certification below. |
| --- | --- |
|  | OR |
|  | I am unable to certify as above because the bidder and/or one or more of its parents, subsidiaries, or affiliates is listed on the Department's Chapter 25 list. I will provide a detailed, accurate and precise description of the activities in Part 2 below sign and complete the Certification below. Failure to provide such will result in the proposal being rendered as nonresponsive and appropriate penalties, fines and/or sanctions will be assessed as provided by law. |

Part 2: Additional Information

PLEASE PROVIDE FURTHER INFORMATION RELATED TO INVESTMENT ACTIVITIES IN IRAN. You must provide a detailed, accurate and precise description of the activities of the bidding person/entity, or one of its parents, subsidiaries or affiliates, engaging in the investment activates in Iran on additional sheets provided by you.

Part 3: Certification

I, being duly sworn upon my oath, hereby represent and state that the foregoing information and any attachments there to the best of my knowledge are true and complete. I attest that I am authorized to execute this certification on behalf of the above-referenced person or entity. I acknowledge that the Contracting Unit is relying on the information contained herein and thereby acknowledge that I am under a continuing obligation from the date of this certification through the completion of any contracts with the Contracting Unit to notify the Contracting Unit in writing of any changes to the answers of information contained herein. I acknowledge that I am aware that it is a criminal offense to make a false statement or misrepresentation in this certification, and if I do so, I recognize that I am subject to criminal prosecution under the law and that it will also constitute a material breach of my agreement(s) with the Contracting Unit and that the Contracting Unit at its option may declare any contract(s) resulting from this certification void and unenforceable.

| Full Name (Print): |  | Title: |  |
| --- | --- | --- | --- |
| Signature: |  | Date: |  |

Appendix M – Certification of Non-Involvement in Prohibited Activities in Russia or Belarus

CERTIFICATION OF NON‐INVOLVEMENT IN PROHIBITED ACTIVITIES IN RUSSIA OR BELARUS

N.J.S.A. 18A:18A-49.5

Pursuant to N.J.S.A. 52:32-60.1, et seq. (L. 2022, c. 3) any person or entity (hereinafter “Vendor”) that seeks to enter into or renew a contract with a State agency for the provision of goods or services, or the purchase of bonds or other obligations, must complete the certification below indicating whether or not the Vendor is identified on the Office of Foreign Assets Control (OFAC) Specially Designated Nationals and Blocked Persons list, available here: https://sanctionssearch.ofac.treas.gov/. If the Department of the Treasury finds that a Vendor has made a certification in violation of the law, it shall take any action as may be appropriate and provided by law, rule, or contract, including but not limited to, imposing sanctions, seeking compliance, recovering damages, declaring the party in default and seeking debarment or suspension of the party.

I, the undersigned, certify that I have read the definition of “Vendor” below, and have reviewed the Office of Foreign Assets Control (OFAC) Specially Designated Nationals and Blocked Persons list, and having done so certify:

|  | (Check the Appropriate Box) |
| --- | --- |
| A. | That the Vendor is not identified on the OFAC Specially Designated Nationals and Blocked Persons list on account of activity related to Russia and/or Belarus. |
|  | OR |
| B. | That I am unable to certify as to “A” above, because the Vendor is identified on the OFAC Specially Designated Nationals and Blocked Persons list on account of activity related to Russia and/or Belarus. |
|  | OR |
| C. | That I am unable to certify as to “A” above, because the Vendor is identified on the OFAC Specially Designated Nationals and Blocked Persons list. However, the Vendor is engaged in activity related to Russia and/or Belarus consistent with federal law, regulation, license or exemption. A detailed description of how the Vendor’s activity related to Russia and/or Belarus is consistent with federal law is set forth below. |
|  | (Attach Additional Sheets If Necessary.) |

_______________________________________________		______________________

Signature of Vendor’s Authorized Representative			Date

________________________________________________	_______________________

Print Name and Title of Vendor’s Authorized Representative	Vendor’s FEIN

_______________________________________________		_______________________

Vendor’s Name							Vendor’s Phone Number

_______________________________________________		_______________________

Vendor’s Address (Street Address)					Vendor’s Fax Number

_______________________________________________		_______________________

Vendor’s Address (City/State/Zip Code)				Vendor’s Email Address

Appendix N – Political Contribution Disclosure Form

# C. 271 POLITICAL CONTRIBUTION DISCLOSURE FORM

Contractor Instructions

Business entities (contractors) receiving contracts from a public agency that are NOT awarded pursuant to a “fair and open” process (defined at N.J.S.A. 19:44A-20.7) are subject to the provisions of N.J.S.A. 19:44A-20.26.  This law provides that 10 days prior to the award of such a contract, the contractor shall disclose contributions to:

- any continuing political committee (a.k.a., political action committee)

- any candidate committee of a candidate for, or holder of, an elective office:

  - of the public entity awarding the contract

  - of that county in which that public entity is located

  - of another public entity within that county

  - or of a legislative district in which that public entity is located or, when the public entity is a county, of any legislative district which includes all or part of the county

The disclosure must list reportable contributions to any of the committees that exceed $200 per election cycle that were made during the 12 months prior to award of the contract.  See N.J.S.A. 19:44A-8 and 19:44A-16 for more details on reportable contributions.

N.J.S.A. 19:44A-20.26 itemizes the parties from whom contributions must be disclosed when a business entity is not a natural person.  This includes the following:

- individuals with an “interest” ownership or control of more than 10% of the profits or assets of a business entity or 10% of the stock in the case of a business entity that is a corporation for profit

- all principals, partners, officers, or directors of the business entity or their spouses

- any subsidiaries directly or indirectly controlled by the business entity

- IRS Code Section 527 New Jersey based organizations, directly or indirectly controlled by the business entity and filing as continuing political committees, (PACs).

When the business entity is a natural person, “a contribution by that person’s spouse or child, residing therewith, shall be deemed to be a contribution by the business entity.” [N.J.S.A. 19:44A-20.26(b)]  The contributor must be listed on the disclosure.

Any business entity that fails to comply with the disclosure provisions shall be subject to a fine imposed by ELEC in an amount to be determined by the Commission which may be based upon the amount that the business entity failed to report.

The enclosed list of agencies is provided to assist the contractor in identifying those public agencies whose elected official and/or candidate campaign committees are affected by the disclosure requirement.  It is the contractor’s responsibility to identify the specific committees to which contributions may have been made and need to be disclosed.  The disclosed information may exceed the minimum requirement.

The enclosed form, a content-consistent facsimile, or an electronic data file containing the required details (along with a signed cover sheet) may be used as the contractor’s submission and is disclosable to the public under the Open Public Records Act.

The contractor must also complete the attached Ownership Disclosure Certification.  This will assist the agency in meeting its obligations under the law. NOTE: This section does not apply to Board of Education contracts.

# C. 271 POLITICAL CONTRIBUTION DISCLOSURE FORM

Required Pursuant To N.J.S.A. 19:44A-20.26

This form or its permitted facsimile must be submitted to the local unit

no later than 10 days prior to the award of the contract.

Part I – Vendor Information

| Vendor Name: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Address: |  |  |  |  |  |
| City: |  |  |  | State: | Zip: |

The undersigned being authorized to certify, hereby certifies that the submission provided herein represents compliance with the provisions of N.J.S.A. 19:44A-20.26 and as represented by the Instructions accompanying this form.

________________________    	___________________________	__________________________

Signature			Printed Name				Title

## Part II – Contribution Disclosure

Disclosure requirement: Pursuant to N.J.S.A. 19:44A-20.26 this disclosure must include all reportable political contributions (more than $200 per election cycle) over the 12 months prior to submission to the committees of the government entities listed on the form provided by the local unit.

- Check here if disclosure is provided in electronic form.

| Contributor Name | Recipient Name | Date | Dollar Amount |
| --- | --- | --- | --- |
|  |  |  | $ |

- Check here if the information is continued on subsequent page(s)

# Continuation Page

# C. 271 POLITICAL CONTRIBUTION DISCLOSURE FORM

Required Pursuant To N.J.S.A. 19:44A-20.26

Page ___ of ______

Vendor Name:

| Contributor Name | Recipient Name | Date | Dollar Amount |
| --- | --- | --- | --- |
|  |  |  | $ |

- Check here if the information is continued on subsequent page(s)

Appendix O – No Adverse Material Change of Qualifications

NO ADVERSE MATERIAL CHANGE OF QUALIFICATION INFORMATION

AFFIDAVIT

I, _______________________________, being of full age under oath depose and say:

- I am a(n) owner, partner, shareholder, or officer of the company set forth below and am duly authorized to execute this affidavit on its behalf.

- A statement as to the financial ability, adequacy of plant and equipment, organization, and prior experience of [Proposer], as required by N.J.S.A. 18A:18A-28 has been submitted to the Department of Treasury within one (1) year preceding the date of opening of proposals for this contract.

- I certify, as required by N.J.S.A. 18A:18A-32 that there has been no material adverse change in the qualification information of [Proposer] since such statement was submitted to the Department of Treasury except: ______________________________________________.

SEAL

__________________________________

TITLE

__________________________________

COMPANY

Sworn to and subscribed

before me this ______ day of _______________________, 2026.

________________________

Notary Public

Commission Expires: ______________________

Appendix P – Guarantee for Correction of Work

GUARANTEE FOR CORRECTION OF WORK AFTER FINAL PAYMENT

STATE OF NEW JERSEY 		)

) SS:

COUNTY OF Burlington 		)

_____________________________________________________ being duly sworn according to law upon his oath deposes and says:

(1) That he is the ____________________ of _________________________

(Officer) 			(Contractor)

for _______________________________ Proposal Dated: _________________________

(Description of Project)

belonging to Princeton Public Schools in the County of Mercer, State of New Jersey (“Owner”) and as such has full authority to sign this Affidavit.

NOW, THEREFORE,

- This contractor shall remedy any defects due to faulty materials or workmanship and pay for any damages to other work resulting there from, which shall appear within a period of one year from the date of completion and acceptance by West Windsor-Plainsboro Regional School District. Where guarantee or warranties for longer terms are written in any part of the Specifications such longer terms shall apply.

- The date of completion and acceptance shall be interpreted as the date West Windsor-Plainsboro Regional School District accepted the Solar Project and began paying for the provided energy.

- This Contractor shall, in case work performed by his subcontractor and material suppliers, also guarantee said work and does not release this obligation.

- Neither the foregoing nor any provisions in the Contract Documents, nor any special guaranteed time limit, shall be held to the limit of this Contractor’s liability in accordance with the law of the place of building. The Owner shall give notice of observed difficulties with reasonable promptness. All questions arising with regard to this guarantee shall be decided by the Owner.

Signature: ____________________________

(SEAL)

Sworn and subscribed before me

This _______ day of __________________, 2026.

Appendix Q – Addenda Acknowledgement Form

ACKNOWLEDGMENT OF RECEIPT OF ADDENDA

The undersigned Bidder hereby acknowledges receipt of the following Addenda:

Addendum Number						Dated

________________________				_____________________

________________________				_____________________

________________________				_____________________

________________________				_____________________

Acknowledged for: _________________________________________

(Name of Bidder Company)

By: _________________________________________ (Signature of Authorized Representative)

Name: _______________________________	Title: _______________________________

COMPLETE THIS FORM AND SIGN AS ACKNOWLEDGMENT OF RECEIPT OF ALL RFP MATERIALS (VERIFY ALL ADDENDA AND DATES)

Appendix R – American with Disabilities Act of 1990

AMERICANS WITH DISABILITIES ACT OF 1990

Equal Opportunity for Individuals with Disability

The CONTRACTOR and the OWNER do hereby agree that the provisions of Title II of the Americans With Disabilities Act of 1990 (the "ACT") (42 U.S.C. S12101 et seq.), which prohibits discrimination on the basis of disability by public entities in all services, programs, and activities provided or made available by public entities, and the rules and regulations promulgated pursuant thereunto, are made a part of this contract. In providing any aid, benefit, or service on behalf of the OWNER pursuant to this contract, the CONTRACTOR agrees that the performance shall be in strict compliance with the Act. In the event that, its agents, servants, employees, or subcontractors violate or are alleged to have violated the Act during the performance of this contract, the CONTRACTOR shall defend the OWNER in any action or administrative proceeding commenced pursuant to this Act. They shall indemnify, protect, and save harmless the OWNER, its agents, servants, and employees from and against any and all suits, claims, losses, demands, or damages, of whatever kind or nature arising out of or claimed to arise out of the alleged violation. The CONTRACTOR shall, at its own expense, appear, defend, and pay any and all charges for legal services and any and all costs and other expenses arising from such action or administrative proceeding or incurred in connection therewith. In any and all complaints brought pursuant to the OWNER grievance procedure, the CONTRACTOR agrees to abide by any decision of the OWNER which is rendered pursuant to said grievance procedure. If any action or administrative proceeding results in an award of damages against the OWNER or if the OWNER incurs any expense to cure a violation of the ADA which has been brought pursuant to its grievance procedure, the CONTRACTOR shall satisfy and discharge the same at its own expense.

The OWNER shall, as soon as practicable after a claim has been made against it, give written notice thereof to the CONTRACTOR along with full and complete particulars of the claim. If any action or administrative proceedings is brought against the OWNER or any of its agents, servants, and employees, the OWNER shall expeditiously forward or have forwarded to the CONTRACTOR every demand, complaint, notice, summons, pleading, or other process received by the OWNER or its representatives.

It is expressly agreed and understood that any approval by the OWNER of the services provided by the CONTRACTOR pursuant to this contract will not relieve the CONTRACTOR of the obligation to comply with the Act and to defend, indemnify, protect, and save harmless the OWNER pursuant to this paragraph.

It is further agreed and understood that the OWNER assumes no obligation to indemnify or save harmless the CONTRACTOR, its agents, servants, employees, and subcontractors for any claim which may arise out of their performance of this Agreement. Furthermore, the CONTRACTOR expressly understands and agrees that the provisions of this indemnification clause shall in no way limit the CONTRACTOR'S obligations assumed in this Agreement, nor shall they be construed to relieve the CONTRACTOR from any liability, nor preclude the OWNER from taking any other actions available to it under any other provisions of the Agreement or otherwise at law.

DATE: ____________________

COMPANY NAME: ________________________________

AUTHORIZED COMPANY REPRESENTATIVE NAME: ____________________________

SIGNATURE: ________________________________

COMPLETE FORM AND INCLUDE WITH PROPOSAL SUBMISSION TO ACKNOWLEDGE REQUIREMENT

Appendix S – Business Registration Certificate Requirement

BUSINESS REGISTRATION CERTIFICATE REQUIREMENT

All Proposers must provide a State Division of Revenue issued Business Registration Certificate with the Proposal.

Detailed information on this requirement is found in the Division of Local Government Services Local Finance Notices 2004-17 (8/6/04), 2004-24 (8/1/04), 2005-12 (4/27/05) and on the Division web site at www.nj.govidca/Igs/Ipcl.

THE REQUIRED BUSINESS REGISTRATION CERTIFICATE(S) SHALL BE INCLUDED WITH PROPOSAL SUBMISSION

Appendix T – Public Works Contractor Registration Act Requirement

PUBLIC WORKS CONTRACTOR REGISTRATION ACT REQUIREMENT

All named contractors and sub-contractors MUST be registered with the Department of Labor pursuant to the PWCRA at the time the Proposal is received, or the Proposal will be determined to be non-responsive. Any non-listed (un-named, TBD) sub-contractor must be registered with the Department of Labor prior to physically starting work.

A contractor's certification can be confirmed by contacting the Department of Labor's Division of Wage and Hour Compliance website (www.nj.gov/labor/Isse/Ispubcon.html). This site only shows approved contractors; there is no "pending" approval or a "grace" period.

Additional information on the PWCRA can be obtained from the:

Contractor Registration Unit 				Telephone: 609-292-9464

Division of Wage and Hour Compliance 		Fax: 609-633-8591

New Jersey Department of Labor 			E-mail: contregPdol.state.nj.us

PO Box 389 						Website:

Trenton, New Jersey 08625-0389 			www.nj.gov/labor/Isse/Ispubcon.html

A VALID PUBLIC WORKS CONTRACTOR REGISTRATION SHALL BE INCLUDED FOR ALL NAMED CONTRACTORS AND SUBCONTRACTORS WITH PROPOSAL SUBMISSION

Appendix U – Non-Debarment/Suspension/Disqualification Affidavit

NO DEBARMENT/SUSPENSION/DISQUALIFICATION AFFIDAVIT

STATE OF NEW JERSEY			)

)

COUNTY OF ________________________	)

Name of Project ________________________________________________________________

I, _______________________________________ , of the City of _______________________in

the County of _________________________ and the State of ___________________________,

of full age, being duly sworn according to law on my oath, depose and say that:

I am the owner, an officer, or a partner of the firm of ___________________________________ (the "Proposer"), which is proposing on the above-referenced project. Neither the Proposer nor its principals:

A. 	are currently debarred, suspended, proposed for debarment, declared ineligible, or voluntarily excluded from proposing or contracting by any agency of government including but not limited to federal, state, regional, county, or local government agency in this or any other state including any department, division, commission, authority, office, branch, section, and political subdivision or other governmental or quasi-governmental entity, including the New Jersey Economic Development Authority and Schools Development Authority;

B. 	have, within a three-year period preceding this proposal, been convicted or had a civil judgment rendered against them for commission of fraud or a criminal offense in connection with obtaining, attempting to obtain or performing a public federal, state or local contract; violation of federal or state antitrust statutes or commission of embezzlement, theft, forgery, bribery, falsification or destruction of records, making false statements, or receiving stolen property;

C. 	are currently indicted for or otherwise criminally or civilly charged by a governmental entity (federal, state, or local) with commission of any of the offenses enumerated in paragraph (B) of this certification; and

D. 	have, within a 3-year period preceding this proposal, had one or more public contracts (federal, state, or local) terminated for cause or default.

[Certification on Next Page]

By: ______________________________________

Signature

Print or Type Name: _________________________

Title: _____________________________________

Sworn and subscribed to before me this _____ day of__________________, 2026.

Notary Public of ___________________________

Commission Expires: _______________________

Appendix V – No Material Change of Circumstances

NOTICE: SIGN AND NOTARIZE THIS FORM AND PROVIDE ALL THE DOCUMENTATION REQUESTED

NO MATERIAL CHANGE OF CIRCUMSTANCES AFFIDAVIT

I, ______________________________________________, being of full age, under oath depose and say:

1. 	I am the owner, partner, shareholder, or officer of the proposer named below and am duly authorized to execute this affidavit on its behalf.

2. 	A statement as to the financial ability, adequacy of plant and equipment,

organization and prior experience of the proposer, as required by N.J.S.A. 18A:18A-28, has been submitted to the Department of Treasury within the last twelve (12) months preceding the date of opening of proposals for this contract.

3. 	I certify, as required by N.J. S.A. 18A:18A-32, that there has been no material adverse change in the qualification except as set forth herein as follows:

4. 	I hereby certify under penalty as provided by law, that there is not now pending any litigation or other action that may jeopardize my rating, status, or contract limits from their current limits.

SEAL

Firm

By: ___________________________________

(Signature)

______________________________________

(Print or Type Name)

______________________________________

(Title)

Sworn and subscribed to before me this _____ day of ________________, 2026.

Notary Public of ____________________________

Commission Expires: ________________________

Appendix W – Disclosure of DPMC Contractor Classification

DISCLOSURE OF DPMC CONTRACTOR CLASSIFICATION

The Proposer must be registered by the Department of Labor and Workforce Development, and the Department of the Treasury, Division of Revenue; and classified by the Department of the Treasury - Division of Property Management and Construction.

The Proposers shall submit copies of their current Classification Notice from the Department of Treasury, Division of Property Management and Construction for all named contractors and sub-contractors.

All contractors shall have completed the form DPMC-27 Request for Classification. Additional information for this requirement can be found at: https://www.state.nj.us/treasury/dpmc/forms.html.

This contractor classification application form is used in accordance with N.J.S.A. 52:35-1 et. seq. to allow a firm to propose various state and local school District public works construction projects.

Proposers and subcontractors shall have a valid Classification effective as of the date of the proposal opening.

PROPOSERS MUST SUBMIT A COPY OF THEIR DPMC CONTRACTOR CLASSIFICATION NOTICE

Appendix X – Total Amount of Uncompleted Contracts

I Certify that the amount of uncompleted work on contracts is $________________________.

The amount claimed includes uncompleted portions of all currently held contracts from all sources (public and private) in accordance with N.J.A.C. 1 7:19-2.13.

I further certify that the amount of this proposal, including all outstanding incomplete contracts, does not exceed my prequalification dollar limit.

______________________________________

Name of Firm

______________________________________	____________________________________

Signature 						Printed Name

______________________________________

Title

______________________________________

______________________________________

______________________________________

Business Address

Sworn to and subscribed before me

This _________ day of ______________________, 2026.

Notary Public: ___________________________________

Commission Expires: _____________________________

Seal

COMPLETE, SIGN, AND NOTARIZE THIS FORM