Pete Palmer, Director of Facilities • 760 Magnolia Avenue, Piedmont CA 94611• 510.594.2877

February 27th, 2026

Wildwood Elementary & PMS 400 + 500 Bld Elevator Modernization Project RFP

Bid Due date: Monday, March 23rd at 2pm at District Office-760 Magnolia Ave, Piedmont

(mandatory bid walk to occur on Wed, March 18th at 2pm at 760 Magnolia Ave, Piedmont)

Refer to the following PUSD link for all plans, specs and contract documents:

https://www.piedmont.k12.ca.us/ref/facilities

Wildwood Elementary School Modernize existing 2 stop elevator

(DOSH State# 108823, original install 1995-31yrs old) PUSD Proposed Budget = $155,000

Piedmont Middle School Modernize existing 2 stop elevator in the 400 Bld

(DOSH State# 108745, original install 1996-30yrs old)  PUSD Proposed Budget = $160,000

Piedmont Middle School Modernize existing 3 stop elevator in the 500 Bld

(DOSH State# 124727, original install 2001-25yrs old)  PUSD Proposed Budget = $155,000

Total proposed PUSD budget to modernize all three elevators = $470,000

Scope of work

Furnish the labor and materials required to install new micro-processor driven elevator controls, fixtures, hoistway and machine room wiring, and other work described on the Passenger Elevators located at Wildwood Elementary School, 301 Wildwood Ave, Piedmont 94611 and Piedmont Middle School, 740 Magnolia Ave, Piedmont 94611.  Work will be done in accordance with the specifications and scope of work described hereunder.

1.	General:

A)	Permits and Certificates - All necessary elevator State permits and/or certificates to

perform the scope of work under this proposal will obtained.

B)	Wiring Diagrams - Two (2) complete sets of “as built” wiring diagrams will be provided

upon completion.

- Painting - All exposed metal work furnished under this proposal, except pre-finished

metal such as stainless steel, or factory finished work, but including metal work exposed

in the hoistway shall be painted after installation.

D)	Codes and Ordinances - All designs, clearances, construction, workmanship, and materials provided will be in accordance with California Elevator Safety Orders as well as local codes and ordinances in force as of the above proposal date, including ASME A17.1 Group 4, 2004.

E)	Wiring - All new wiring will be in accordance with NEC and CAC requirements.

- Removal of Old Equipment - All existing material and equipment that has been removed by Paramount Elevator and not reused will be carefully taken out of the building and properly disposed of.

2.	Elevator Controller Equipment:

Install one (1) new non-proprietary micro-processor driven hydraulic elevator controller with new state of the art diagnostics.  The new controller will include:

A)	Computer controlled motion of the elevator including acceleration, top speed,

deceleration, and leveling.

B)	Serial Microprocessor car-top controller.

C)	Fire Fighter’s Service Phase I & II.

- Hall Board Serial Link.

- Door operating circuitry for new door operator.

F)	Emergency battery lowering device to bring the elevator to the bottom floor when

there is a power outage.

G) All hall stations will be set up to accommodate card reader provided by the District

3.	Operation of Elevator:

The elevator will have its own selective collective computerized dispatching system.  The operation of one or more car or hall call push buttons shall cause the car to start and run automatically provided the hoistway door interlocks and car door contacts are closed.  The elevator car shall stop at the first call or hall call set for the direction of travel.  Stops shall be made in order in which the car or hall calls set for the direction of travel are reached, regardless of the order in which they were registered.  If only hall calls set for the opposite direction of travel of the elevator exist ahead of the car, the car shall proceed to the most distant hall call, reverse direction and start collecting calls.

4.	Power Unit:

Install new submersible type oil pump unit.  The new unit will have:

- 3-phase elevator duty motor with built in thermal protection.

- Direct coupled pump.

- Silencer.

- Ball type shutoff valve.

- Maxton unit-type control valve.

- New hydraulic oil will be added.

5.	Elevator Cylinder and Piston:

The existing hydraulic cylinder and piston will be retained.

6.	Landing System:

The elevator will be equipped with a new tape selector landing system.

7.	Automatic Self Releveling:

Automatic self leveling will be provided which will bring the elevator car to each landing

level within 1/8” of the landing floor irrespective of load or direction of travel.  The self

releveling system will correct for car over-travel, under-travel and any leak down between runs.

8.	Wiring:

- New wiring will be installed in the elevator machine room, hoistway and elevator car.  All new wiring will be run in conduit, tubing, or electrical wire-ways.

- A new AC main line feed, disconnect and independent lighting circuits will be installed by others. (See “Work By Others”)

9.	Traveling Cable:

The existing traveling cable will be removed, and a new fire-retardant traveling cable will be

installed with additional spare wires and shielded pair communication cables for any future 	security system or camera upgrades.

10.	Car Rail Fastenings and Brackets:

The existing car rail fastenings and brackets will be retained.

11.	Hoistway Switches:

The terminal, directional and access hoistway switches will be replaced, as necessary

12.	Elevator Guides:

The existing elevator car (top and bottom) guides will be replaced.

13.	Elevator Pit Equipment:

- A new code compliant rupture valve will be installed.

- A new code compliant ball type shutoff valve will be installed.

- The existing car buffers will be retained.

- All other equipment in the pit will be retained.

14.	Top of Car Inspection Systems:

New car top inspection station will be provided and connected to the new controls.

15.	Car Enclosure:

- The existing car enclosure will be retained or refurbished by the District.

16.	Car Fixtures:

The existing car fixtures will be replaced with the following:

A)	Car Operating Panel (C.O.P.) - a new C.O.P. will be installed with the following features:

- Pushbuttons, key switches and Braille plates (all ADA/Title 24 compliant).

2)	Firefighter’s Service Phase II – key switch and indicator light installed per Code

requirements.  This will allow emergency personnel to “commandeer” the elevator

during emergencies.

- Car Position Indicator with digital display showing the landing the elevator car is at.

4)	ADA compliant Emergency Hands-Free Telephone.

B)	Emergency Light Unit - equipped with alarm bell and rechargeable battery.  During

loss of power the emergency light unit will provide illumination to a portion of the

elevator cab and the alarm bell will be functional.

C)	Floor Passing Chime - a floor passing chime will be installed so that as the elevator

passes a landing an audible chime will sound once.

D)  All fixture finishes will have #4 stainless steel finish.

17.	Car Door Equipment:

- Door Operator

- A new Solid State Car Door Operator will be installed.

- Door Tracks & Equipment

- A new clutch with a door zone safety restrictor will be installed.

- New door hanger rollers and door gibs will be installed.

- A new car door track will be installed.

- Existing car door panels will be retained.

18.	Hoistway Door Equipment:

- The existing hoistway entrances and door panels will be retained.

- New hoistway door tracks will be installed.

- New door hanger rollers, pickup rollers, door locks, door gibs and spring door closers will be installed.

19.	Hallway Fixtures:

Hall Pushbutton Stations – new hall stations will be installed at each landing.  The new hall stations will be mounted at Code required height and will have the following features:

- Pushbuttons and key switches will be ADA/Title 24 compliant and shall have Card Reader Access.

B)	Firefighter’s Service Phase I – key switch will be installed in the fire egress landing hall 			station to allow the elevator to be placed on “Fire Service” by emergency personnel.  A 			sign with instructions on how to operate the Firefighter’s key switch will be posted.

C)	Hoistway Access Switch - hoistway access key switches will be installed in the top and

bottom landing hall stations.

- A digital position indicator will be installed in each hall fixture.

20. Smoke/Fire Devices:

A new fire panel and smoke detectors at each landing may be required by state code.  The specific building requirements will need to be determined by a licensed Fire Life Safety contractor as stated in the “Work By Others” section below.

21.	State Inspection:

Upon completion of the modernization, the elevator contractor will have the elevator work inspected by the State of California.  Once the elevator has passed inspection, the building owner will be issued a permit to operate the elevator, and the elevator will be returned to service.

Work By Others:

- All general contracting necessary to complete the project must comply with current codes.

- Smoke sensors, designed to meet NFPA-72 codes as well as any local code in force, are to be installed at each landing, the elevator hoistway, and in the elevator machine room.  Wiring for the sensors must be clearly identified and terminated in the elevator machine room for connection to the elevator controller.  The sensors when installed will then be connected by The Elevator Contractor to the new firefighters' service control circuits in the elevator controller as required by code.

- Any interfacing of the smoke sensors, the firefighters' operation, or any other elevator function to the building life-safety system is the Districts responsibility.

- The 3-phase/Single phase power provided to the machine room mainline disconnect appears to be adequate.  However, there is a possibility that it may need to be upgraded to accommodate the new control equipment power requirements including a suitable ground.

- The Districts electrician will calculate and provide at a minimum 208VAC 3-phase/Single phase power with sufficient amperage to support the modernization of the elevator.

- The Districts electrician will provide dedicated 120VAC, 20AMP circuits for: (1) Elevator Machine Room Power; (2) Elevator Power; (3) Elevator Pit Power; (4) Overhead Machine Space Power (Basement Drum/Basement Traction Only).  The Districts electrician shall also provide a fused disconnect switch for the elevator power circuit located in machine room.

- The Districts electrician will provide a GFCI outlet and adequate lighting located in the following locations: (1) Elevator Machine Room; (2) Elevator Pit; (3) Overhead Machine Space (Basement Drum/Basement Traction Only).

- The Districts electrician will bring 3-Phase/Single phase electrical power and disconnect switches to the elevator machine room.  Note: The Elevator Contractor will run the main line power conduit up the elevator hoistway and stub the conduit into the machine room for the electrician if necessary.

- The District will provide one dedicated telephone line for the elevator emergency phone and terminate the line in the elevator machine room near the elevator controller.

Any other building related items that may be required, including the finish patching and painting of walls, or that are not specifically provided for elsewhere herein are the responsibility of the District