## WE 1) Int & Ext Lighting
Lodi USD: Creekside Elementary School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Creekside Elementary | MPR | Kitchen Vent Hood | Creekside Elementary: MPR: Kitchen Vent Hood | Jelly Jar | CFL 13W 1L | Creekside Elementary: MPR: Kitchen Vent Hood: Jelly Jar: CFL 13W 1L | N | 13 | 3 | 1 | 0 | No Change | 0 | 0 | 13 | 3 | 3 | 0 | 0
2 | 1.1 | Creekside Elementary | Portable | 30 | Creekside Elementary: Portable: 30 | Recessed 2'X2' Troffer | F17T82L | Creekside Elementary: Portable: 30: Recessed 2'X2' Troffer: F17T82L | N | 33 | 2 | 2 | 0 | LED 16-Watt 2'X2' Retrofit Kit w/ Ctrls | 2560 | 160 | 16 | 2 | 4 | 0 | 0
3 | 1.1 | Creekside Elementary | Portable | 29 | Creekside Elementary: Portable: 29 | Recessed 2'X2' Troffer | F17T82L | Creekside Elementary: Portable: 29: Recessed 2'X2' Troffer: F17T82L | N | 33 | 2 | 2 | 0 | LED 16-Watt 2'X2' Retrofit Kit w/ Ctrls | 2560 | 160 | 16 | 2 | 4 | 0 | 0
4 | 1.1 | Creekside Elementary | MPR | Custodian Office | Creekside Elementary: MPR: Custodian Office | Strip 4' | F32T81L | Creekside Elementary: MPR: Custodian Office: Strip 4': F32T81L | N | 31 | 4 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 4 | 4 | 4 | 0
5 | 1.1 | Creekside Elementary | MPR | Teacher Break Rm | Creekside Elementary: MPR: Teacher Break Rm | Surface Mount 2'X4' | F32T82L | Creekside Elementary: MPR: Teacher Break Rm: Surface Mount 2'X4': F32T82L | N | 59 | 6 | 2 | 1 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 6 | 12 | 6 | 0
6 | 1.1 | Creekside Elementary | MPR | Women's RR | Creekside Elementary: MPR: Women's RR | Strip 4' | F32T82L | Creekside Elementary: MPR: Women's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
7 | 1.1 | Creekside Elementary | MPR | Men's RR | Creekside Elementary: MPR: Men's RR | Strip 4' | F32T82L | Creekside Elementary: MPR: Men's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
8 | 1.1 | Creekside Elementary | Admin | File Rm | Creekside Elementary: Admin: File Rm | Strip 4' | F32T82L | Creekside Elementary: Admin: File Rm: Strip 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
9 | 1.1 | Creekside Elementary | Admin | RR | Creekside Elementary: Admin: RR | Strip 4' | F32T82L | Creekside Elementary: Admin: RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
10 | 1.1 | Creekside Elementary | MPR | Electrical Rm | Creekside Elementary: MPR: Electrical Rm | Strip 4' | F32T82L | Creekside Elementary: MPR: Electrical Rm: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Roof Access
11 | 1.1 | Creekside Elementary | MPR | Kitchen | Creekside Elementary: MPR: Kitchen | Strip 4' | F32T82L | Creekside Elementary: MPR: Kitchen: Strip 4': F32T82L | N | 59 | 11 | 2 | 2 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 11 | 22 | 11 | 0
12 | 1.1 | Creekside Elementary | MPR | Dry Goods Storage | Creekside Elementary: MPR: Dry Goods Storage | Strip 4' | F32T82L | Creekside Elementary: MPR: Dry Goods Storage: Strip 4': F32T82L | N | 59 | 4 | 2 | 1 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 4 | 8 | 4 | 0
13 | 1.1 | Creekside Elementary | MPR | Storage | Creekside Elementary: MPR: Storage | Strip 4' | F32T82L | Creekside Elementary: MPR: Storage: Strip 4': F32T82L | N | 59 | 6 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 6 | 12 | 6 | 0
14 | 1.1 | Creekside Elementary | 16-17 Bldg | Men's RR | Creekside Elementary: 16-17 Bldg: Men's RR | Strip 4' | F32T82L | Creekside Elementary: 16-17 Bldg: Men's RR: Strip 4': F32T82L | N | 59 | 6 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 6 | 12 | 6 | 0
15 | 1.1 | Creekside Elementary | 16-17 Bldg | Women's RR | Creekside Elementary: 16-17 Bldg: Women's RR | Strip 4' | F32T82L | Creekside Elementary: 16-17 Bldg: Women's RR: Strip 4': F32T82L | N | 59 | 7 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 7 | 14 | 7 | 0
16 | 1.1 | Creekside Elementary | 16-17 Bldg | Custodian | Creekside Elementary: 16-17 Bldg: Custodian | Strip 4' | F32T82L | Creekside Elementary: 16-17 Bldg: Custodian: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Estimated count
17 | 1.1 | Creekside Elementary | Portable | Girl's RR | Creekside Elementary: Portable: Girl's RR | Strip 4' | F32T82L | Creekside Elementary: Portable: Girl's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
18 | 1.1 | Creekside Elementary | Portable | Storage | Creekside Elementary: Portable: Storage | Strip 4' | F32T82L | Creekside Elementary: Portable: Storage: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
19 | 1.1 | Creekside Elementary | Portable | Staff RR | Creekside Elementary: Portable: Staff RR | Strip 4' | F32T82L | Creekside Elementary: Portable: Staff RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
20 | 1.1 | Creekside Elementary | Portable | Boy's RR | Creekside Elementary: Portable: Boy's RR | Strip 4' | F32T82L | Creekside Elementary: Portable: Boy's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
21 | 1.1 | Creekside Elementary | Kinder/TK | 31 RR | Creekside Elementary: Kinder/TK: 31 RR | Strip 4' | F32T82L | Creekside Elementary: Kinder/TK: 31 RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
22 | 1.1 | Creekside Elementary | Kinder/TK | 32 RR | Creekside Elementary: Kinder/TK: 32 RR | Strip 4' | F32T82L | Creekside Elementary: Kinder/TK: 32 RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
23 | 1.1 | Creekside Elementary | New | Custodian | Creekside Elementary: New: Custodian | Strip 4' | F32T82L | Creekside Elementary: New: Custodian: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Estimated count
24 | 1.1 | Creekside Elementary | New | Staff RR | Creekside Elementary: New: Staff RR | Strip 4' | F32T82L | Creekside Elementary: New: Staff RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
25 | 1.1 | Creekside Elementary | 33-42 Bldg | Boy's RR | Creekside Elementary: 33-42 Bldg: Boy's RR | Surface Wrap 4' | F32T82L | Creekside Elementary: 33-42 Bldg: Boy's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
26 | 1.1 | Creekside Elementary | 33-42 Bldg | Girl's RR | Creekside Elementary: 33-42 Bldg: Girl's RR | Surface Wrap 4' | F32T82L | Creekside Elementary: 33-42 Bldg: Girl's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
27 | 1.1 | Creekside Elementary | Admin | Main Office | Creekside Elementary: Admin: Main Office | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Admin: Main Office: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
28 | 1.1 | Creekside Elementary | Admin | Vice Principal | Creekside Elementary: Admin: Vice Principal | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Admin: Vice Principal: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
29 | 1.1 | Creekside Elementary | Admin | Principal | Creekside Elementary: Admin: Principal | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Admin: Principal: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
30 | 1.1 | Creekside Elementary | 5-6 Bldg | 6 | Creekside Elementary: 5-6 Bldg: 6 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 5-6 Bldg: 6: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
31 | 1.1 | Creekside Elementary | 5-6 Bldg | 5 | Creekside Elementary: 5-6 Bldg: 5 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 5-6 Bldg: 5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
32 | 1.1 | Creekside Elementary | 1-4 Bldg | 4 | Creekside Elementary: 1-4 Bldg: 4 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 1-4 Bldg: 4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
33 | 1.1 | Creekside Elementary | 1-4 Bldg | 3 | Creekside Elementary: 1-4 Bldg: 3 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 1-4 Bldg: 3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
34 | 1.1 | Creekside Elementary | 1-4 Bldg | 2 | Creekside Elementary: 1-4 Bldg: 2 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 1-4 Bldg: 2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
35 | 1.1 | Creekside Elementary | 1-4 Bldg | 1 | Creekside Elementary: 1-4 Bldg: 1 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 1-4 Bldg: 1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
36 | 1.1 | Creekside Elementary | Portable | 26 | Creekside Elementary: Portable: 26 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 26: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | 0
37 | 1.1 | Creekside Elementary | Portable | 9 | Creekside Elementary: Portable: 9 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 9: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
38 | 1.1 | Creekside Elementary | Portable | 10 | Creekside Elementary: Portable: 10 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 10: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
39 | 1.1 | Creekside Elementary | Portable | 11 | Creekside Elementary: Portable: 11 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 11: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
40 | 1.1 | Creekside Elementary | Portable | 12 | Creekside Elementary: Portable: 12 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 12: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
41 | 1.1 | Creekside Elementary | Portable | 13 | Creekside Elementary: Portable: 13 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 13: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
42 | 1.1 | Creekside Elementary | Portable | 14 | Creekside Elementary: Portable: 14 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 14: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
43 | 1.1 | Creekside Elementary | Portable | 15 | Creekside Elementary: Portable: 15 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 15: Recessed 2'X4' Troffer: F32T82L | N | 59 | 22 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 22 | 44 | 0 | 0
44 | 1.1 | Creekside Elementary | 16-17 Bldg | 16 | Creekside Elementary: 16-17 Bldg: 16 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 16-17 Bldg: 16: Recessed 2'X4' Troffer: F32T82L | N | 59 | 16 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | 0
45 | 1.1 | Creekside Elementary | 16-17 Bldg | 17 | Creekside Elementary: 16-17 Bldg: 17 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 16-17 Bldg: 17: Recessed 2'X4' Troffer: F32T82L | N | 59 | 16 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | 0
46 | 1.1 | Creekside Elementary | 7-8 Bldg | 8 | Creekside Elementary: 7-8 Bldg: 8 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 7-8 Bldg: 8: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
47 | 1.1 | Creekside Elementary | 7-8 Bldg | 7 | Creekside Elementary: 7-8 Bldg: 7 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 7-8 Bldg: 7: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
48 | 1.1 | Creekside Elementary | Library | 24 | Creekside Elementary: Library: 24 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 24: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
49 | 1.1 | Creekside Elementary | Library | 25 | Creekside Elementary: Library: 25 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 25: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
50 | 1.1 | Creekside Elementary | Library | 18 | Creekside Elementary: Library: 18 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 18: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
51 | 1.1 | Creekside Elementary | Library | 19 | Creekside Elementary: Library: 19 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 19: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
52 | 1.1 | Creekside Elementary | Library | Storage L2 | Creekside Elementary: Library: Storage L2 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: Storage L2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
53 | 1.1 | Creekside Elementary | Library | Storage L3 | Creekside Elementary: Library: Storage L3 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: Storage L3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
54 | 1.1 | Creekside Elementary | Library | 20 | Creekside Elementary: Library: 20 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 20: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
55 | 1.1 | Creekside Elementary | Library | 21 | Creekside Elementary: Library: 21 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 21: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
56 | 1.1 | Creekside Elementary | Library | 22 | Creekside Elementary: Library: 22 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 22: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
57 | 1.1 | Creekside Elementary | Library | 23 | Creekside Elementary: Library: 23 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: 23: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
58 | 1.1 | Creekside Elementary | Library | Office L1 | Creekside Elementary: Library: Office L1 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: Office L1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
59 | 1.1 | Creekside Elementary | Library | Conference L4 | Creekside Elementary: Library: Conference L4 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Library: Conference L4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
60 | 1.1 | Creekside Elementary | Portable | 27 | Creekside Elementary: Portable: 27 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 27: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | Head Start
61 | 1.1 | Creekside Elementary | Portable | 43 | Creekside Elementary: Portable: 43 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 43: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | 0
62 | 1.1 | Creekside Elementary | Portable | 30 | Creekside Elementary: Portable: 30 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Portable: 30: Recessed 2'X4' Troffer: F32T82L | N | 59 | 13 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 13 | 26 | 0 | 0
63 | 1.1 | Creekside Elementary | Kinder/TK | 31 | Creekside Elementary: Kinder/TK: 31 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Kinder/TK: 31: Recessed 2'X4' Troffer: F32T82L | N | 59 | 18 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 0
64 | 1.1 | Creekside Elementary | Kinder/TK | 32 | Creekside Elementary: Kinder/TK: 32 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: Kinder/TK: 32: Recessed 2'X4' Troffer: F32T82L | N | 59 | 18 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 0
65 | 1.1 | Creekside Elementary | 33-42 Bldg | 42 | Creekside Elementary: 33-42 Bldg: 42 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 42: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
66 | 1.1 | Creekside Elementary | 33-42 Bldg | 41 | Creekside Elementary: 33-42 Bldg: 41 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 41: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
67 | 1.1 | Creekside Elementary | 33-42 Bldg | 40 | Creekside Elementary: 33-42 Bldg: 40 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 40: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
68 | 1.1 | Creekside Elementary | 33-42 Bldg | 39 | Creekside Elementary: 33-42 Bldg: 39 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 39: Recessed 2'X4' Troffer: F32T82L | N | 59 | 5 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 5 | 10 | 0 | 0
69 | 1.1 | Creekside Elementary | 33-42 Bldg | 38 | Creekside Elementary: 33-42 Bldg: 38 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 38: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | 0
70 | 1.1 | Creekside Elementary | 33-42 Bldg | 37 | Creekside Elementary: 33-42 Bldg: 37 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 37: Recessed 2'X4' Troffer: F32T82L | N | 59 | 14 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 14 | 28 | 0 | 0
71 | 1.1 | Creekside Elementary | 33-42 Bldg | 36 | Creekside Elementary: 33-42 Bldg: 36 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 36: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | Roof Access
72 | 1.1 | Creekside Elementary | 33-42 Bldg | 35 | Creekside Elementary: 33-42 Bldg: 35 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 35: Recessed 2'X4' Troffer: F32T82L | N | 59 | 5 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 5 | 10 | 0 | 0
73 | 1.1 | Creekside Elementary | 33-42 Bldg | 34 | Creekside Elementary: 33-42 Bldg: 34 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 34: Recessed 2'X4' Troffer: F32T82L | N | 59 | 10 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 10 | 20 | 0 | 0
74 | 1.1 | Creekside Elementary | 33-42 Bldg | 33 | Creekside Elementary: 33-42 Bldg: 33 | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: 33: Recessed 2'X4' Troffer: F32T82L | N | 59 | 18 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 0
75 | 1.1 | Creekside Elementary | 33-42 Bldg | Work Rm | Creekside Elementary: 33-42 Bldg: Work Rm | Recessed 2'X4' Troffer | F32T82L | Creekside Elementary: 33-42 Bldg: Work Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 8 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 8 | 16 | 0 | 0
76 | 1.1 | Creekside Elementary | Admin | Main Office | Creekside Elementary: Admin: Main Office | Recessed 2'X4' Troffer | F32T83L | Creekside Elementary: Admin: Main Office: Recessed 2'X4' Troffer: F32T83L | N | 89 | 8 | 3 | 2 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 8 | 24 | 0 | 0
77 | 1.1 | Creekside Elementary | Admin | Work Rm | Creekside Elementary: Admin: Work Rm | Recessed 2'X4' Troffer | F32T83L | Creekside Elementary: Admin: Work Rm: Recessed 2'X4' Troffer: F32T83L | N | 89 | 4 | 3 | 0 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 4 | 12 | 0 | 0
78 | 1.1 | Creekside Elementary | Portable | 29 | Creekside Elementary: Portable: 29 | Recessed 2'X4' Troffer | F32T83L | Creekside Elementary: Portable: 29: Recessed 2'X4' Troffer: F32T83L | N | 89 | 13 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 13 | 39 | 0 | 0
79 | 1.1 | Creekside Elementary | Portable | 28 | Creekside Elementary: Portable: 28 | Recessed 2'X4' Troffer | F32T83L | Creekside Elementary: Portable: 28: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
76 | 1.1 | Creekside Elementary | Library | Library | Creekside Elementary: Library: Library | Pendant D/ID | F32T86L | Creekside Elementary: Library: Library: Pendant D/ID: F32T86L | N | 175 | 17 | 6 | 2 | (6) LED 11-Watt 4' Tubes & Driver | 9240 | 140 | 66 | 17 | 102 | 34 | TOO DARK
77 | 1.1 | Creekside Elementary | MPR | MPR | Creekside Elementary: MPR: MPR | Surface Mount Highbay 2'X4' | F54T5/HO 4L | Creekside Elementary: MPR: MPR: Surface Mount Highbay 2'X4': F54T5/HO 4L | N | 234 | 20 | 4 | 4 | LED 85-Watt Surface Mount Highbay w/ Ctrls | 15000 | 176.4706 | 85 | 20 | 80 | 0 | Missing 1x fixture, replace
Annual Total | [10 empty] | 955 |  | 82 |  |  |  |  | 955 | 2048 | 106
Lodi USD: Creekside Elementary School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
1 | 1.2 | Creekside Elementary | Combined | Exterior Area | Creekside Elementary: Combined: Exterior Area | Can Recessed 10" | CFM 32W 1L | Creekside Elementary: Combined: Exterior Area: Can Recessed 10": CFM 32W 1L |  | 36.8 | 32 | 1 | 0 | LED 12-Watt Canopy 1'x1' | 1800 | 150 | 12 | 32
ANNUAL TOTAL | [10 empty] | 32 |  | 0 |  |  |  |  | 32
Lodi USD: Delta Sierra Middle School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Delta Sierra Middle | MPR | Storage/ Take-out | Delta Sierra Middle: MPR: Storage/ Take-out | Pendant | CFL 32W 1L | Delta Sierra Middle: MPR: Storage/ Take-out: Pendant: CFL 32W 1L | N | 32 | 2 | 1 | 0 | No Change | 0 | 0 | 32 | 2 | 2 | 0 | 0
2 | 1.1 | Delta Sierra Middle | MPR | Entry | Delta Sierra Middle: MPR: Entry | Can Recessed 6" | MH 70W | Delta Sierra Middle: MPR: Entry: Can Recessed 6": MH 70W | N | 95 | 1 | 1 | 0 | LED 13-Watt 6" Downlight Retrofit | 1560 | 120 | 13 | 1 | 1 | 0 | 0
3 | 1.1 | Delta Sierra Middle | Admin | Entry | Delta Sierra Middle: Admin: Entry | Pendant 4' | F32T81L | Delta Sierra Middle: Admin: Entry: Pendant 4': F32T81L | N | 31 | 9 | 1 | 2 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 9 | 9 | 9 | 0
4 | 1.1 | Delta Sierra Middle | Library | Library Main | Delta Sierra Middle: Library: Library Main | Pendant 4' | F32T81L | Delta Sierra Middle: Library: Library Main: Pendant 4': F32T81L | N | 31 | 62 | 1 | 6 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 62 | 62 | 62 | 0
5 | 1.1 | Delta Sierra Middle | MPR | Custodian | Delta Sierra Middle: MPR: Custodian | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: MPR: Custodian: Surface Mount 2'X4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
6 | 1.1 | Delta Sierra Middle | MPR | Stage | Delta Sierra Middle: MPR: Stage | Surface Wrap 4' | F32T82L | Delta Sierra Middle: MPR: Stage: Surface Wrap 4': F32T82L | N | 59 | 15 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 15 | 30 | 0 | 0
7 | 1.1 | Delta Sierra Middle | MPR | Back Stage | Delta Sierra Middle: MPR: Back Stage | Surface Wrap 4' | F32T82L | Delta Sierra Middle: MPR: Back Stage: Surface Wrap 4': F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
8 | 1.1 | Delta Sierra Middle | MPR | Office | Delta Sierra Middle: MPR: Office | Surface Wrap 4' | F32T82L | Delta Sierra Middle: MPR: Office: Surface Wrap 4': F32T82L | Y | 59 | 6 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 6 | 12 | 0 | Hard Shell
9 | 1.1 | Delta Sierra Middle | MPR | Storage/ Take-out | Delta Sierra Middle: MPR: Storage/ Take-out | Surface Wrap 4' | F32T82L | Delta Sierra Middle: MPR: Storage/ Take-out: Surface Wrap 4': F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
10 | 1.1 | Delta Sierra Middle | MPR | Kitchen | Delta Sierra Middle: MPR: Kitchen | Surface Wrap 4' | F32T82L | Delta Sierra Middle: MPR: Kitchen: Surface Wrap 4': F32T82L | Y | 59 | 25 | 2 | 5 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 25 | 50 | 0 | Hard Shell
11 | 1.1 | Delta Sierra Middle | MPR | Staff Lounge | Delta Sierra Middle: MPR: Staff Lounge | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: MPR: Staff Lounge: Surface Mount 2'X4': F32T82L | N | 59 | 10 | 2 | 2 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 10 | 20 | 10 | 0
12 | 1.1 | Delta Sierra Middle | MPR | IT | Delta Sierra Middle: MPR: IT | Recessed 2'X4' | F32T82L | Delta Sierra Middle: MPR: IT: Recessed 2'X4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Hard Shell
13 | 1.1 | Delta Sierra Middle | MPR | Men's RR | Delta Sierra Middle: MPR: Men's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: MPR: Men's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
14 | 1.1 | Delta Sierra Middle | MPR | Women's RR | Delta Sierra Middle: MPR: Women's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: MPR: Women's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
15 | 1.1 | Delta Sierra Middle | Admin | Teacher Lounge | Delta Sierra Middle: Admin: Teacher Lounge | Recessed 2'X4' | F32T82L | Delta Sierra Middle: Admin: Teacher Lounge: Recessed 2'X4': F32T82L | Y | 59 | 4 | 2 | 1 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 4 | 8 | 4 | Hard Shell
16 | 1.1 | Delta Sierra Middle | Admin | RR | Delta Sierra Middle: Admin: RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Admin: RR: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
17 | 1.1 | Delta Sierra Middle | Admin | Nurse | Delta Sierra Middle: Admin: Nurse | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Admin: Nurse: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | Hard Shell
18 | 1.1 | Delta Sierra Middle | Admin | Work Rm | Delta Sierra Middle: Admin: Work Rm | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Admin: Work Rm: Surface Wrap 4': F32T82L | Y | 59 | 14 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 14 | 28 | 0 | 0
19 | 1.1 | Delta Sierra Middle | Building 3-6 | 4 | Delta Sierra Middle: Building 3-6: 4 | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Building 3-6: 4: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
20 | 1.1 | Delta Sierra Middle | Building 3-6 | 5 Work Rm | Delta Sierra Middle: Building 3-6: 5 Work Rm | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: Building 3-6: 5 Work Rm: Surface Mount 2'X4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
21 | 1.1 | Delta Sierra Middle | Building 3-6 | Girl's RR | Delta Sierra Middle: Building 3-6: Girl's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Building 3-6: Girl's RR: Surface Wrap 4': F32T82L | N | 59 | 6 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 6 | 12 | 0 | 0
22 | 1.1 | Delta Sierra Middle | Building 3-6 | Custodian | Delta Sierra Middle: Building 3-6: Custodian | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: Building 3-6: Custodian: Surface Mount 2'X4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
23 | 1.1 | Delta Sierra Middle | Building 3-6 | Boy's RR | Delta Sierra Middle: Building 3-6: Boy's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Building 3-6: Boy's RR: Surface Wrap 4': F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
24 | 1.1 | Delta Sierra Middle | Building 3-6 | Men's RR | Delta Sierra Middle: Building 3-6: Men's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Building 3-6: Men's RR: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
25 | 1.1 | Delta Sierra Middle | Building 3-6 | Women's RR | Delta Sierra Middle: Building 3-6: Women's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Building 3-6: Women's RR: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
26 | 1.1 | Delta Sierra Middle | Building 3-6 | Electric Rm | Delta Sierra Middle: Building 3-6: Electric Rm | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: Building 3-6: Electric Rm: Surface Mount 2'X4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | Ladder Access
27 | 1.1 | Delta Sierra Middle | Building 3-6 | 6 Weight Rm | Delta Sierra Middle: Building 3-6: 6 Weight Rm | Pendant 1'X4' | F32T82L | Delta Sierra Middle: Building 3-6: 6 Weight Rm: Pendant 1'X4': F32T82L | N | 59 | 16 | 2 | 1 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 16 | 32 | 16 | 0
28 | 1.1 | Delta Sierra Middle | Building 19-20 | 19 | Delta Sierra Middle: Building 19-20: 19 | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: Building 19-20: 19: Surface Mount 2'X4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
29 | 1.1 | Delta Sierra Middle | Building 19-20 | 19 | Delta Sierra Middle: Building 19-20: 19 | Recessed 2'X4' | F32T82L | Delta Sierra Middle: Building 19-20: 19: Recessed 2'X4': F32T82L | N | 59 | 29 | 2 | 1 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 29 | 58 | 29 | Funky Ceiling
30 | 1.1 | Delta Sierra Middle | Building 19-20 | 19 Work | Delta Sierra Middle: Building 19-20: 19 Work | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: Building 19-20: 19 Work: Surface Mount 2'X4': F32T82L | N | 59 | 4 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 4 | 8 | 4 | 0
31 | 1.1 | Delta Sierra Middle | Building 19-20 | 19 Practice Rms | Delta Sierra Middle: Building 19-20: 19 Practice Rms | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Building 19-20: 19 Practice Rms: Surface Wrap 4': F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
32 | 1.1 | Delta Sierra Middle | Portable | Boy's RR | Delta Sierra Middle: Portable: Boy's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Portable: Boy's RR: Surface Wrap 4': F32T82L | N | 59 | 6 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 6 | 12 | 0 | 0
33 | 1.1 | Delta Sierra Middle | Portable | Girl's RR | Delta Sierra Middle: Portable: Girl's RR | Surface Wrap 4' | F32T82L | Delta Sierra Middle: Portable: Girl's RR: Surface Wrap 4': F32T82L | N | 59 | 6 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 6 | 12 | 0 | 0
34 | 1.1 | Delta Sierra Middle | Portable | Custodial | Delta Sierra Middle: Portable: Custodial | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: Portable: Custodial: Surface Mount 2'X4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Roof Access
35 | 1.1 | Delta Sierra Middle | Building 35-38 | Custodial | Delta Sierra Middle: Building 35-38: Custodial | Surface Mount 2'X4' | F32T82L | Delta Sierra Middle: Building 35-38: Custodial: Surface Mount 2'X4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
36 | 1.1 | Delta Sierra Middle | MPR | F-34 | Delta Sierra Middle: MPR: F-34 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: MPR: F-34: Recessed 2'X4' Troffer: F32T82L | N | 59 | 9 | 2 | 3 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 9 | 18 | 0 | 0
37 | 1.1 | Delta Sierra Middle | Admin | Office | Delta Sierra Middle: Admin: Office | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: Office: Recessed 2'X4' Troffer: F32T82L | N | 59 | 11 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 11 | 22 | 0 | Parabolic Lens
38 | 1.1 | Delta Sierra Middle | Admin | Conference Rm | Delta Sierra Middle: Admin: Conference Rm | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: Conference Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 5 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 5 | 10 | 0 | 0
39 | 1.1 | Delta Sierra Middle | Admin | Vice Principal 1 | Delta Sierra Middle: Admin: Vice Principal 1 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: Vice Principal 1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
40 | 1.1 | Delta Sierra Middle | Admin | Principal | Delta Sierra Middle: Admin: Principal | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: Principal: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
41 | 1.1 | Delta Sierra Middle | Admin | Secretary | Delta Sierra Middle: Admin: Secretary | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: Secretary: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
42 | 1.1 | Delta Sierra Middle | Admin | Counselor | Delta Sierra Middle: Admin: Counselor | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: Counselor: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
43 | 1.1 | Delta Sierra Middle | Admin | Vice Principal 2 | Delta Sierra Middle: Admin: Vice Principal 2 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: Vice Principal 2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
44 | 1.1 | Delta Sierra Middle | Admin | 1 | Delta Sierra Middle: Admin: 1 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: 1: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 30 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 30 | 60 | 0 | 0
45 | 1.1 | Delta Sierra Middle | Admin | 2 | Delta Sierra Middle: Admin: 2 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Admin: 2: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 30 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 30 | 60 | 0 | 0
46 | 1.1 | Delta Sierra Middle | Building 3-6 | 3 | Delta Sierra Middle: Building 3-6: 3 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 3-6: 3: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 32 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 32 | 64 | 0 | 0
47 | 1.1 | Delta Sierra Middle | Building 3-6 | 4 | Delta Sierra Middle: Building 3-6: 4 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 3-6: 4: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 37 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 37 | 74 | 0 | 0
48 | 1.1 | Delta Sierra Middle | Building 3-6 | 5 | Delta Sierra Middle: Building 3-6: 5 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 3-6: 5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 26 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 26 | 52 | 0 | 0
49 | 1.1 | Delta Sierra Middle | Portable | 29 | Delta Sierra Middle: Portable: 29 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 29: Recessed 2'X4' Troffer: F32T82L | N | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
50 | 1.1 | Delta Sierra Middle | Portable | 28 | Delta Sierra Middle: Portable: 28 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 28: Recessed 2'X4' Troffer: F32T82L | N | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
51 | 1.1 | Delta Sierra Middle | Portable | 27 | Delta Sierra Middle: Portable: 27 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 27: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
52 | 1.1 | Delta Sierra Middle | Portable | 26 | Delta Sierra Middle: Portable: 26 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 26: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
53 | 1.1 | Delta Sierra Middle | Portable | 25 | Delta Sierra Middle: Portable: 25 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 25: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
54 | 1.1 | Delta Sierra Middle | Portable | 24 | Delta Sierra Middle: Portable: 24 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 24: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
55 | 1.1 | Delta Sierra Middle | Portable | 23 | Delta Sierra Middle: Portable: 23 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 23: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
56 | 1.1 | Delta Sierra Middle | Portable | 22 | Delta Sierra Middle: Portable: 22 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Portable: 22: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 20 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 0
57 | 1.1 | Delta Sierra Middle | Library | 15 | Delta Sierra Middle: Library: 15 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 15: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
58 | 1.1 | Delta Sierra Middle | Library | 16 | Delta Sierra Middle: Library: 16 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 16: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
59 | 1.1 | Delta Sierra Middle | Library | 17 | Delta Sierra Middle: Library: 17 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 17: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
60 | 1.1 | Delta Sierra Middle | Library | Storage | Delta Sierra Middle: Library: Storage | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Storage: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
61 | 1.1 | Delta Sierra Middle | Library | Foyer | Delta Sierra Middle: Library: Foyer | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Foyer: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
62 | 1.1 | Delta Sierra Middle | Library | Therapist | Delta Sierra Middle: Library: Therapist | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Therapist: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
63 | 1.1 | Delta Sierra Middle | Library | Psych | Delta Sierra Middle: Library: Psych | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Psych: Recessed 2'X4' Troffer: F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
64 | 1.1 | Delta Sierra Middle | Library | Counselor 1 | Delta Sierra Middle: Library: Counselor 1 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Counselor 1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
65 | 1.1 | Delta Sierra Middle | Library | Counselor 2 | Delta Sierra Middle: Library: Counselor 2 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Counselor 2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
66 | 1.1 | Delta Sierra Middle | Library | Library Office | Delta Sierra Middle: Library: Library Office | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Library Office: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 5 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 5 | 10 | 0 | Roof Access
67 | 1.1 | Delta Sierra Middle | Library | Work Rm | Delta Sierra Middle: Library: Work Rm | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Work Rm: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 8 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 8 | 16 | 0 | 0
68 | 1.1 | Delta Sierra Middle | Library | 14 | Delta Sierra Middle: Library: 14 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 14: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
69 | 1.1 | Delta Sierra Middle | Library | 7 | Delta Sierra Middle: Library: 7 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 7: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
70 | 1.1 | Delta Sierra Middle | Library | 8 | Delta Sierra Middle: Library: 8 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 8: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
71 | 1.1 | Delta Sierra Middle | Library | 9 | Delta Sierra Middle: Library: 9 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 9: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
72 | 1.1 | Delta Sierra Middle | Library | 10 | Delta Sierra Middle: Library: 10 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 10: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
73 | 1.1 | Delta Sierra Middle | Library | 12 | Delta Sierra Middle: Library: 12 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 12: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
74 | 1.1 | Delta Sierra Middle | Library | 11 | Delta Sierra Middle: Library: 11 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 11: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
75 | 1.1 | Delta Sierra Middle | Library | 13 | Delta Sierra Middle: Library: 13 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 13: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
76 | 1.1 | Delta Sierra Middle | Library | 18 | Delta Sierra Middle: Library: 18 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: 18: Recessed 2'X4' Troffer: F32T82L | Y | 59 | 21 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
77 | 1.1 | Delta Sierra Middle | Building 19-20 | 20 | Delta Sierra Middle: Building 19-20: 20 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 19-20: 20: Recessed 2'X4' Troffer: F32T82L | N | 59 | 28 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | 0
78 | 1.1 | Delta Sierra Middle | Building 35-38 | 35 | Delta Sierra Middle: Building 35-38: 35 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 35-38: 35: Recessed 2'X4' Troffer: F32T82L | N | 59 | 16 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | 0
79 | 1.1 | Delta Sierra Middle | Building 35-38 | Resource Rm | Delta Sierra Middle: Building 35-38: Resource Rm | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 35-38: Resource Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 7 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 7 | 14 | 0 | 0
80 | 1.1 | Delta Sierra Middle | Building 35-38 | 38 | Delta Sierra Middle: Building 35-38: 38 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 35-38: 38: Recessed 2'X4' Troffer: F32T82L | N | 59 | 16 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | 0
81 | 1.1 | Delta Sierra Middle | Building 35-38 | 37 | Delta Sierra Middle: Building 35-38: 37 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 35-38: 37: Recessed 2'X4' Troffer: F32T82L | N | 59 | 16 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | 0
82 | 1.1 | Delta Sierra Middle | Building 35-38 | 36 | Delta Sierra Middle: Building 35-38: 36 | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Building 35-38: 36: Recessed 2'X4' Troffer: F32T82L | N | 59 | 16 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | 0
83 | 1.1 | Delta Sierra Middle | Library | Library Halls | Delta Sierra Middle: Library: Library Halls | Recessed 2'X4' Troffer | F32T82L | Delta Sierra Middle: Library: Library Halls: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
84 | 1.1 | Delta Sierra Middle | Portable | P-33 | Delta Sierra Middle: Portable: P-33 | Recessed 2'X4' Troffer | F32T83L | Delta Sierra Middle: Portable: P-33: Recessed 2'X4' Troffer: F32T83L | Y | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
85 | 1.1 | Delta Sierra Middle | Portable | P-32 | Delta Sierra Middle: Portable: P-32 | Recessed 2'X4' Troffer | F32T83L | Delta Sierra Middle: Portable: P-32: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
86 | 1.1 | Delta Sierra Middle | Portable | P-31 | Delta Sierra Middle: Portable: P-31 | Recessed 2'X4' Troffer | F32T83L | Delta Sierra Middle: Portable: P-31: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
87 | 1.1 | Delta Sierra Middle | Portable | P-30 | Delta Sierra Middle: Portable: P-30 | Recessed 2'X4' Troffer | F32T83L | Delta Sierra Middle: Portable: P-30: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
88 | 1.1 | Delta Sierra Middle | Portable | P-21 | Delta Sierra Middle: Portable: P-21 | Recessed 2'X4' Troffer | F32T83L | Delta Sierra Middle: Portable: P-21: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
89 | 1.1 | Delta Sierra Middle | MPR | Kitchen Office | Delta Sierra Middle: MPR: Kitchen Office | Surface Mount 2'X4' | F32T84L | Delta Sierra Middle: MPR: Kitchen Office: Surface Mount 2'X4': F32T84L | Y | 112 | 1 | 4 | 0 | (4) LED 11-Watt 4' Tubes & Driver | 6160 | 140 | 44 | 1 | 4 | 1 | Hard Shell
Annual Total | [10 empty] | 1049 |  | 67 |  |  |  |  | 1049 | 2084 | 149
Lodi USD: Delta Sierra Middle School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
90 | 1.2 | Delta Sierra Middle | Combined | Exterior Area | Delta Sierra Middle: Combined: Exterior Area | Can Recessed 10" | CFM 32W 1L | Delta Sierra Middle: Combined: Exterior Area: Can Recessed 10": CFM 32W 1L |  | 36.8 | 30 | 1 | 0 | LED 12-Watt Canopy 1'x1' | 1800 | 150 | 12 | 30
91 | 1.2 | Delta Sierra Middle | Combined | Exterior Area | Delta Sierra Middle: Combined: Exterior Area | Wallpack | HPS 150W | Delta Sierra Middle: Combined: Exterior Area: Wallpack: HPS 150W |  | 188 | 7 | 1 | 0 | LED 28-Watt Full-Cutoff Wallpack | 4200 | 150 | 28 | 7
92 | 1.2 | Delta Sierra Middle | MPR Rooftop | Exterior Area | Delta Sierra Middle: MPR Rooftop: Exterior Area | Yoke Flood | MH 250W | Delta Sierra Middle: MPR Rooftop: Exterior Area: Yoke Flood: MH 250W |  | 295 | 2 | 1 | 0 | LED 60-Watt Yoke Flood | 9000 | 150 | 60 | 2
ANNUAL TOTAL | [10 empty] | 39 |  | 0 |  |  |  |  | 39
Lodi USD: Dorothy Mahin School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Dorothy Mahin School | Main | Back Hallway | Dorothy Mahin School: Main: Back Hallway | Recessed 1'x1' | CFL 23W 1L | Dorothy Mahin School: Main: Back Hallway: Recessed 1'x1': CFL 23W 1L | N | 23 | 1 | 1 | 0 | No Change | 0 | 0 | 23 | 1 | 1 | 0 | couldn't open, estimate
2 | 1.1 | Dorothy Mahin School | Main | Office | Dorothy Mahin School: Main: Office | Surface Wrap 4' | F32T82L | Dorothy Mahin School: Main: Office: Surface Wrap 4': F32T82L | N | 59 | 8 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 8 | 16 | 0 | 0
3 | 1.1 | Dorothy Mahin School | Main | Principle's Office | Dorothy Mahin School: Main: Principle's Office | Surface Wrap 4' | F32T82L | Dorothy Mahin School: Main: Principle's Office: Surface Wrap 4': F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
4 | 1.1 | Dorothy Mahin School | Main | Hallway | Dorothy Mahin School: Main: Hallway | Surface Wrap 4' | F32T82L | Dorothy Mahin School: Main: Hallway: Surface Wrap 4': F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
5 | 1.1 | Dorothy Mahin School | Main | Room 1 | Dorothy Mahin School: Main: Room 1 | Surface Wrap 4' | F32T82L | Dorothy Mahin School: Main: Room 1: Surface Wrap 4': F32T82L | N | 59 | 26 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 26 | 52 | 0 | 0
6 | 1.1 | Dorothy Mahin School | Main | Room 4 | Dorothy Mahin School: Main: Room 4 | Surface Wrap 4' | F32T82L | Dorothy Mahin School: Main: Room 4: Surface Wrap 4': F32T82L | N | 59 | 26 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 26 | 52 | 0 | 0
7 | 1.1 | Dorothy Mahin School | Main | Room 3 | Dorothy Mahin School: Main: Room 3 | Surface Wrap 4' | F32T82L | Dorothy Mahin School: Main: Room 3: Surface Wrap 4': F32T82L | N | 59 | 28 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | 0
8 | 1.1 | Dorothy Mahin School | Main | Room 2 | Dorothy Mahin School: Main: Room 2 | Surface Wrap 4' | F32T82L | Dorothy Mahin School: Main: Room 2: Surface Wrap 4': F32T82L | N | 59 | 28 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | 0
9 | 1.1 | Dorothy Mahin School | Main | Storage | Dorothy Mahin School: Main: Storage | Strip 4' | F32T82L | Dorothy Mahin School: Main: Storage: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
10 | 1.1 | Dorothy Mahin School | Main | Open Area | Dorothy Mahin School: Main: Open Area | Luminous Ceiling | F32T82L | Dorothy Mahin School: Main: Open Area: Luminous Ceiling: F32T82L | N | 59 | 28 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 28 | 56 | 28 | luminous ceiling
11 | 1.1 | Dorothy Mahin School | Main | Hallway Restroom | Dorothy Mahin School: Main: Hallway Restroom | Strip 4' | F32T82L | Dorothy Mahin School: Main: Hallway Restroom: Strip 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
12 | 1.1 | Dorothy Mahin School | Main | Fire Alarm Rm | Dorothy Mahin School: Main: Fire Alarm Rm | Strip 4' | F32T82L | Dorothy Mahin School: Main: Fire Alarm Rm: Strip 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
13 | 1.1 | Dorothy Mahin School | Main | Restroom Storage | Dorothy Mahin School: Main: Restroom Storage | Strip 4' | F32T82L | Dorothy Mahin School: Main: Restroom Storage: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
14 | 1.1 | Dorothy Mahin School | Main | Kitchen | Dorothy Mahin School: Main: Kitchen | Strip 4' | F32T84L | Dorothy Mahin School: Main: Kitchen: Strip 4': F32T84L | N | 112 | 2 | 4 | 0 | (4) LED 11-Watt 4' Tubes & Driver | 6160 | 140 | 44 | 2 | 8 | 2 | 0
15 | 1.1 | Dorothy Mahin School | Main | Storage | Dorothy Mahin School: Main: Storage | Strip 4' | F32T84L | Dorothy Mahin School: Main: Storage: Strip 4': F32T84L | N | 112 | 1 | 4 | 0 | (4) LED 11-Watt 4' Tubes & Driver | 6160 | 140 | 44 | 1 | 4 | 1 | In OP.
Annual Total | [10 empty] | 164 |  | 0 |  |  |  |  | 164 | 333 | 39
Lodi USD: GL Mosher Elementary School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD | Control Type (PC/MTC) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.2 | GL Mosher Elementary | Main | Exterior Area | GL Mosher Elementary: Main: Exterior Area | Canopy | HPS 50W | GL Mosher Elementary: Main: Exterior Area: Canopy: HPS 50W | MTC | 66 | 3 | 1 | 0 | LED 12-Watt Canopy 1'x1' | 1800 | 150 | 12 | 3 | 3 | 0 | Listed as Ceiling, Est. Canopy
2 | 1.2 | GL Mosher Elementary | Main | Exterior Area | GL Mosher Elementary: Main: Exterior Area | Wallpack Round 12" | HPS 100W | GL Mosher Elementary: Main: Exterior Area: Wallpack Round 12": HPS 100W | MTC | 138 | 6 | 1 | 0 | LED 22-Watt Full-Cutoff Wallpack | 3300 | 150 | 22 | 6 | 6 | 0 | 0
3 | 1.2 | GL Mosher Elementary | Main | Entryway | GL Mosher Elementary: Main: Entryway | Wallpack Round 12" | HPS 100W | GL Mosher Elementary: Main: Entryway: Wallpack Round 12": HPS 100W | MTC | 138 | 4 | 1 | 0 | LED 22-Watt Full-Cutoff Wallpack | 3300 | 150 | 22 | 4 | 4 | 0 | 0
4 | 1.2 | GL Mosher Elementary | Main | Front of Building | GL Mosher Elementary: Main: Front of Building | Wallpack Round 12" | HPS 100W | GL Mosher Elementary: Main: Front of Building: Wallpack Round 12": HPS 100W | MTC | 138 | 5 | 1 | 0 | LED 22-Watt Full-Cutoff Wallpack | 3300 | 150 | 22 | 5 | 5 | 0 | 0
5 | 1.2 | GL Mosher Elementary | Main | Side of Building | GL Mosher Elementary: Main: Side of Building | Wallpack Round 12" | HPS 100W | GL Mosher Elementary: Main: Side of Building: Wallpack Round 12": HPS 100W | MTC | 138 | 5 | 1 | 0 | LED 22-Watt Full-Cutoff Wallpack | 3300 | 150 | 22 | 5 | 5 | 0 | 0
6 | 1.2 | GL Mosher Elementary | Campus | Exterior Area | GL Mosher Elementary: Campus: Exterior Area | 15' Poletop Round | HPS 150W | GL Mosher Elementary: Campus: Exterior Area: 15' Poletop Round: HPS 150W | MTC | 188 | 15 | 1 | 0 | LED 35-Watt Pole Top | 5250 | 150 | 35 | 15 | 15 | 0 | 0
7 | 1.2 | GL Mosher Elementary | Campus | Parking | GL Mosher Elementary: Campus: Parking | 20' Round Pole Arm Area | HPS 250W | GL Mosher Elementary: Campus: Parking: 20' Round Pole Arm Area: HPS 250W | MTC | 295 | 15 | 1 | 0 | LED 75-Watt Pole Arm Area | 12000 | 160 | 75 | 15 | 15 | 0 | 0
ANNUAL TOTAL | [10 empty] | 53 |  | 0 |  |  |  |  | 53 | 53 | 0
Lodi USD: Extension Road Sites: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Extension Road Sites | Independence | Single RR | Extension Road Sites: Independence: Single RR | Recessed 2'x2' | FU31T8/6 2L | Extension Road Sites: Independence: Single RR: Recessed 2'x2': FU31T8/6 2L | N | 59 | 1 | 2 | 0 | LED 22-Watt 2'X2' Retrofit Kit w/ Ctrls | 3520 | 160 | 22 | 1 | 2 | 0
2 | 1.1 | Extension Road Sites | Henderson Main | Lounge | Extension Road Sites: Henderson Main: Lounge | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Lounge: Surface Wrap 4': F32T84L | N | 112 | 6 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 6 | 24 | 0
3 | 1.1 | Extension Road Sites | Henderson Main | Counseling | Extension Road Sites: Henderson Main: Counseling | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Counseling: Surface Wrap 4': F32T84L | N | 112 | 4 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 4 | 16 | 0
4 | 1.1 | Extension Road Sites | Henderson Main | Office | Extension Road Sites: Henderson Main: Office | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Office: Surface Wrap 4': F32T84L | N | 112 | 4 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 4 | 16 | 0
5 | 1.1 | Extension Road Sites | Henderson Main | Library | Extension Road Sites: Henderson Main: Library | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Library: Surface Wrap 4': F32T84L | N | 112 | 12 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0
6 | 1.1 | Extension Road Sites | Henderson Main | Cafeteria | Extension Road Sites: Henderson Main: Cafeteria | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Cafeteria: Surface Wrap 4': F32T84L | N | 112 | 24 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 24 | 96 | 0
7 | 1.1 | Extension Road Sites | Henderson Main | Boy's RR | Extension Road Sites: Henderson Main: Boy's RR | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Boy's RR: Surface Wrap 4': F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
8 | 1.1 | Extension Road Sites | Henderson Main | Staff RR | Extension Road Sites: Henderson Main: Staff RR | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Staff RR: Surface Wrap 4': F32T84L | N | 112 | 1 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 1 | 4 | 0
9 | 1.1 | Extension Road Sites | Henderson Main | Girl's RR | Extension Road Sites: Henderson Main: Girl's RR | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Girl's RR: Surface Wrap 4': F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
10 | 1.1 | Extension Road Sites | Henderson Main | Custodian Storage | Extension Road Sites: Henderson Main: Custodian Storage | Surface Wrap 4' | F32T84L | Extension Road Sites: Henderson Main: Custodian Storage: Surface Wrap 4': F32T84L | N | 112 | 1 | 4 | 0 | LED 30-Watt Surface Mount Wrap 4' w/ Ctrls | 4800 | 160 | 30 | 1 | 4 | 0
11 | 1.1 | Extension Road Sites | Henderson Main | Custodian Office | Extension Road Sites: Henderson Main: Custodian Office | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Henderson Main: Custodian Office: Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
12 | 1.1 | Extension Road Sites | Henderson Portable | P-4 | Extension Road Sites: Henderson Portable: P-4 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Henderson Portable: P-4: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0
13 | 1.1 | Extension Road Sites | Henderson Portable | P-5 | Extension Road Sites: Henderson Portable: P-5 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Henderson Portable: P-5: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0
14 | 1.1 | Extension Road Sites | Henderson Portable | P-6 | Extension Road Sites: Henderson Portable: P-6 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Henderson Portable: P-6: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0
15 | 1.1 | Extension Road Sites | Independence | Office (1) | Extension Road Sites: Independence: Office (1) | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Office (1): Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0
16 | 1.1 | Extension Road Sites | Independence | Principal's Office | Extension Road Sites: Independence: Principal's Office | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Principal's Office: Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
17 | 1.1 | Extension Road Sites | Independence | Vice Principal's Office | Extension Road Sites: Independence: Vice Principal's Office | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Vice Principal's Office: Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
18 | 1.1 | Extension Road Sites | Independence | Office (2) | Extension Road Sites: Independence: Office (2) | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Office (2): Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
19 | 1.1 | Extension Road Sites | Independence | Office (3) | Extension Road Sites: Independence: Office (3) | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Office (3): Recessed 2'X4' Troffer: F32T84L | N | 112 | 1 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 1 | 4 | 0
20 | 1.1 | Extension Road Sites | Independence | Copy Room | Extension Road Sites: Independence: Copy Room | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Copy Room: Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
21 | 1.1 | Extension Road Sites | Independence | Kitchen | Extension Road Sites: Independence: Kitchen | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Kitchen: Recessed 2'X4' Troffer: F32T84L | N | 112 | 1 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 1 | 4 | 0
22 | 1.1 | Extension Road Sites | Independence Portable | P-5 | Extension Road Sites: Independence Portable: P-5 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-5: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
23 | 1.1 | Extension Road Sites | Independence Portable | P-4 | Extension Road Sites: Independence Portable: P-4 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-4: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
24 | 1.1 | Extension Road Sites | Independence Portable | P-3 | Extension Road Sites: Independence Portable: P-3 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-3: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
25 | 1.1 | Extension Road Sites | Independence Portable | P-2 | Extension Road Sites: Independence Portable: P-2 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-2: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
26 | 1.1 | Extension Road Sites | Independence Portable | P-1 | Extension Road Sites: Independence Portable: P-1 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-1: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
27 | 1.1 | Extension Road Sites | Independence | Boy's RR | Extension Road Sites: Independence: Boy's RR | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Boy's RR: Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
28 | 1.1 | Extension Road Sites | Independence | Girl's RR | Extension Road Sites: Independence: Girl's RR | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence: Girl's RR: Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
29 | 1.1 | Extension Road Sites | Independence Portable | P-9 | Extension Road Sites: Independence Portable: P-9 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-9: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0
30 | 1.1 | Extension Road Sites | Independence Portable | P-10 | Extension Road Sites: Independence Portable: P-10 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-10: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
31 | 1.1 | Extension Road Sites | Independence Portable | P-11 | Extension Road Sites: Independence Portable: P-11 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-11: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
32 | 1.1 | Extension Road Sites | Independence Portable | P-15 | Extension Road Sites: Independence Portable: P-15 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-15: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
33 | 1.1 | Extension Road Sites | Independence Portable | P-14 | Extension Road Sites: Independence Portable: P-14 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-14: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0
34 | 1.1 | Extension Road Sites | Independence Portable | P-13 | Extension Road Sites: Independence Portable: P-13 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-13: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0
35 | 1.1 | Extension Road Sites | Independence Portable | P-8 | Extension Road Sites: Independence Portable: P-8 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-8: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
36 | 1.1 | Extension Road Sites | Independence Portable | P-8 Office | Extension Road Sites: Independence Portable: P-8 Office | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-8 Office: Recessed 2'X4' Troffer: F32T84L | N | 112 | 2 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 2 | 8 | 0
37 | 1.1 | Extension Road Sites | Independence Portable | P-17 | Extension Road Sites: Independence Portable: P-17 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-17: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0
38 | 1.1 | Extension Road Sites | Independence Portable | P-16 | Extension Road Sites: Independence Portable: P-16 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-16: Recessed 2'X4' Troffer: F32T84L | N | 112 | 6 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 6 | 24 | 0
39 | 1.1 | Extension Road Sites | Independence Portable | P-16 (2) | Extension Road Sites: Independence Portable: P-16 (2) | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Independence Portable: P-16 (2): Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0
40 | 1.1 | Extension Road Sites | Valley Robotics | K6 | Extension Road Sites: Valley Robotics: K6 | Recessed 2'X4' Troffer | F32T84L | Extension Road Sites: Valley Robotics: K6: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0
Annual Total | [10 empty] | 261 |  | 0 |  |  |  |  | 261 | 1042 | 0
Lodi USD: John Muir Elementary School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | John Muir Elementary | Main | Library Entry | John Muir Elementary: Main: Library Entry | Can Recessed 12'' | CFQ 26W 2L | John Muir Elementary: Main: Library Entry: Can Recessed 12'': CFQ 26W 2L | N | 66 | 8 | 2 | 0 | (2) LED 8-Watt 2-pin Lamp Ballast Bypass | 1760 | 110 | 16 | 8 | 16 | 0 | 12'' Can
2 | 1.1 | John Muir Elementary | Main | Hall | John Muir Elementary: Main: Hall | Can Recessed 8'' | CFQ 26W 2L | John Muir Elementary: Main: Hall: Can Recessed 8'': CFQ 26W 2L | N | 66 | 5 | 2 | 0 | LED 17-Watt 8" Downlight Retrofit | 2040 | 120 | 17 | 5 | 10 | 0 | 0
3 | 1.1 | John Muir Elementary | Main | MPR | John Muir Elementary: Main: MPR | Can Recessed 8'' | CFQ 26W 2L | John Muir Elementary: Main: MPR: Can Recessed 8'': CFQ 26W 2L | N | 66 | 4 | 2 | 0 | LED 17-Watt 8" Downlight Retrofit | 2040 | 120 | 17 | 4 | 8 | 0 | 0
4 | 1.1 | John Muir Elementary | Main | Stage | John Muir Elementary: Main: Stage | Can Recessed 6" | Halogen 100W | John Muir Elementary: Main: Stage: Can Recessed 6": Halogen 100W | N | 100 | 8 | 1 | 0 | LED 13-Watt 6" Downlight Retrofit | 1560 | 120 | 13 | 8 | 8 | 0 | 0
5 | 1.1 | John Muir Elementary | Main | MPR | John Muir Elementary: Main: MPR | Vapor Proof 2'x2' | F17T83L | John Muir Elementary: Main: MPR: Vapor Proof 2'x2': F17T83L | N | 47 | 12 | 3 | 0 | (3) LED 9-Watt 2' Tubes & Driver | 3780 | 140 | 27 | 12 | 36 | 12 | Vaporproof Fixt
6 | 1.1 | John Muir Elementary | Main | Library Staff Men's RR | John Muir Elementary: Main: Library Staff Men's RR | Surface Wrap 4' | F32T82L | John Muir Elementary: Main: Library Staff Men's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | Roof Access
7 | 1.1 | John Muir Elementary | Main | Library Staff Women's RR | John Muir Elementary: Main: Library Staff Women's RR | Surface Wrap 4' | F32T82L | John Muir Elementary: Main: Library Staff Women's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
8 | 1.1 | John Muir Elementary | Main | Custodial | John Muir Elementary: Main: Custodial | Strip 4' | F32T82L | John Muir Elementary: Main: Custodial: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
9 | 1.1 | John Muir Elementary | Main | RR | John Muir Elementary: Main: RR | Strip 4' | F32T82L | John Muir Elementary: Main: RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
10 | 1.1 | John Muir Elementary | Main | IDF | John Muir Elementary: Main: IDF | Strip 4' | F32T82L | John Muir Elementary: Main: IDF: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Roof Access
11 | 1.1 | John Muir Elementary | Main | Dry Goods | John Muir Elementary: Main: Dry Goods | Strip 4' | F32T82L | John Muir Elementary: Main: Dry Goods: Strip 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
12 | 1.1 | John Muir Elementary | Main | Dishwashing | John Muir Elementary: Main: Dishwashing | Vapor Proof 4' | F32T82L | John Muir Elementary: Main: Dishwashing: Vapor Proof 4': F32T82L | N | 59 | 4 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 4 | 8 | 4 | Vaporproof Fixt
13 | 1.1 | John Muir Elementary | Main | Storage | John Muir Elementary: Main: Storage | Strip 4' | F32T82L | John Muir Elementary: Main: Storage: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
14 | 1.1 | John Muir Elementary | Main | Men's RR | John Muir Elementary: Main: Men's RR | Vapor Proof 4' | F32T82L | John Muir Elementary: Main: Men's RR: Vapor Proof 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Vaporproof Fixt
15 | 1.1 | John Muir Elementary | Main | Women's RR | John Muir Elementary: Main: Women's RR | Vapor Proof 4' | F32T82L | John Muir Elementary: Main: Women's RR: Vapor Proof 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Vaporproof Fixt
16 | 1.1 | John Muir Elementary | Intermediate Bathrooms | Boy's RR | John Muir Elementary: Intermediate Bathrooms: Boy's RR | Strip 4' | F32T82L | John Muir Elementary: Intermediate Bathrooms: Boy's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
17 | 1.1 | John Muir Elementary | Intermediate Bathrooms | Girl's RR | John Muir Elementary: Intermediate Bathrooms: Girl's RR | Strip 4' | F32T82L | John Muir Elementary: Intermediate Bathrooms: Girl's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
18 | 1.1 | John Muir Elementary | Intermediate Bathrooms | Custodial 1 | John Muir Elementary: Intermediate Bathrooms: Custodial 1 | Strip 4' | F32T82L | John Muir Elementary: Intermediate Bathrooms: Custodial 1: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
19 | 1.1 | John Muir Elementary | Intermediate Bathrooms | Custodial 2 | John Muir Elementary: Intermediate Bathrooms: Custodial 2 | Strip 4' | F32T82L | John Muir Elementary: Intermediate Bathrooms: Custodial 2: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
20 | 1.1 | John Muir Elementary | Intermediate Bathrooms | Staff RR | John Muir Elementary: Intermediate Bathrooms: Staff RR | Strip 4' | F32T82L | John Muir Elementary: Intermediate Bathrooms: Staff RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
21 | 1.1 | John Muir Elementary | Primary Bathrooms | Boy's RR | John Muir Elementary: Primary Bathrooms: Boy's RR | Strip 4' | F32T82L | John Muir Elementary: Primary Bathrooms: Boy's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
22 | 1.1 | John Muir Elementary | Primary Bathrooms | Girl's RR | John Muir Elementary: Primary Bathrooms: Girl's RR | Strip 4' | F32T82L | John Muir Elementary: Primary Bathrooms: Girl's RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
23 | 1.1 | John Muir Elementary | Primary Bathrooms | Staff | John Muir Elementary: Primary Bathrooms: Staff | Strip 4' | F32T82L | John Muir Elementary: Primary Bathrooms: Staff: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
24 | 1.1 | John Muir Elementary | Primary Bathrooms | Custodial 1 | John Muir Elementary: Primary Bathrooms: Custodial 1 | Strip 4' | F32T82L | John Muir Elementary: Primary Bathrooms: Custodial 1: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
25 | 1.1 | John Muir Elementary | Primary Bathrooms | Custodial 2 | John Muir Elementary: Primary Bathrooms: Custodial 2 | Strip 4' | F32T82L | John Muir Elementary: Primary Bathrooms: Custodial 2: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
26 | 1.1 | John Muir Elementary | Main | Teacher Work Rm | John Muir Elementary: Main: Teacher Work Rm | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Teacher Work Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
27 | 1.1 | John Muir Elementary | Main | Office | John Muir Elementary: Main: Office | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Office: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | 0
28 | 1.1 | John Muir Elementary | Main | Copy Rm | John Muir Elementary: Main: Copy Rm | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Copy Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 5 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 5 | 10 | 0 | 0
29 | 1.1 | John Muir Elementary | Main | Counselor | John Muir Elementary: Main: Counselor | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Counselor: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
30 | 1.1 | John Muir Elementary | Main | Conference Rm | John Muir Elementary: Main: Conference Rm | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Conference Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
31 | 1.1 | John Muir Elementary | Main | Psychology | John Muir Elementary: Main: Psychology | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Psychology: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
32 | 1.1 | John Muir Elementary | Main | Kitchen | John Muir Elementary: Main: Kitchen | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Kitchen: Recessed 2'X4' Troffer: F32T82L | N | 59 | 16 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | Roof Access
33 | 1.1 | John Muir Elementary | Main | Staff | John Muir Elementary: Main: Staff | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Staff: Recessed 2'X4' Troffer: F32T82L | N | 59 | 9 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 9 | 18 | 0 | 0
34 | 1.1 | John Muir Elementary | Main | Custodial | John Muir Elementary: Main: Custodial | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Custodial: Recessed 2'X4' Troffer: F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
35 | 1.1 | John Muir Elementary | Main | Stage | John Muir Elementary: Main: Stage | Recessed 2'X4' Troffer | F32T82L | John Muir Elementary: Main: Stage: Recessed 2'X4' Troffer: F32T82L | N | 59 | 8 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 8 | 16 | 0 | 0
36 | 1.1 | John Muir Elementary | Main | MPR | John Muir Elementary: Main: MPR | Surface Mount Highbay 2'X4' | F54T5/HO 4L | John Muir Elementary: Main: MPR: Surface Mount Highbay 2'X4': F54T5/HO 4L | N | 234 | 8 | 4 | 0 | LED 85-Watt Surface Mount Highbay w/ Ctrls | 15000 | 176.4706 | 85 | 8 | 32 | 0 | 0
Annual Total | [10 empty] | 142 |  | 0 |  |  |  |  | 142 | 304 | 42
Lodi USD: Lockeford Elementary School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Lockeford Elementary | MPR | PE Rm | Lockeford Elementary: MPR: PE Rm | Recessed 2'X2' Troffer | FU31T8/6 2L | Lockeford Elementary: MPR: PE Rm: Recessed 2'X2' Troffer: FU31T8/6 2L | N | 59 | 5 | 2 | 0 | LED 22-Watt 2'X2' Retrofit Kit w/ Ctrls | 3520 | 160 | 22 | 5 | 10 | 0 | 0
2 | 1.1 | Lockeford Elementary | MPR | Cafeteria | Lockeford Elementary: MPR: Cafeteria | Recessed 2'X2' Troffer | FU31T8/6 2L | Lockeford Elementary: MPR: Cafeteria: Recessed 2'X2' Troffer: FU31T8/6 2L | N | 59 | 14 | 2 | 1 | LED 22-Watt 2'X2' Retrofit Kit w/ Ctrls | 3520 | 160 | 22 | 14 | 28 | 0 | 0
3 | 1.1 | Lockeford Elementary | MPR | Back Stage | Lockeford Elementary: MPR: Back Stage | Recessed 2'X2' Troffer | FU31T8/6 2L | Lockeford Elementary: MPR: Back Stage: Recessed 2'X2' Troffer: FU31T8/6 2L | N | 59 | 2 | 2 | 0 | LED 22-Watt 2'X2' Retrofit Kit w/ Ctrls | 3520 | 160 | 22 | 2 | 4 | 0 | 0
4 | 1.1 | Lockeford Elementary | Office | Girl's RR | Lockeford Elementary: Office: Girl's RR | Strip 4' | F32T81L | Lockeford Elementary: Office: Girl's RR: Strip 4': F32T81L | N | 31 | 3 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 3 | 3 | 3 | 0
5 | 1.1 | Lockeford Elementary | Office | RR | Lockeford Elementary: Office: RR | Strip 4' | F32T81L | Lockeford Elementary: Office: RR: Strip 4': F32T81L | N | 31 | 1 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 1 | 1 | 1 | 0
6 | 1.1 | Lockeford Elementary | Office | Electrical Rm | Lockeford Elementary: Office: Electrical Rm | Strip 4' | F32T81L | Lockeford Elementary: Office: Electrical Rm: Strip 4': F32T81L | N | 31 | 1 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 1 | 1 | 1 | 0
7 | 1.1 | Lockeford Elementary | Office | Men's RR | Lockeford Elementary: Office: Men's RR | Surface Wrap 4' | F32T81L | Lockeford Elementary: Office: Men's RR: Surface Wrap 4': F32T81L | N | 31 | 1 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 1 | 1 | 1 | 0
8 | 1.1 | Lockeford Elementary | Office | Lobby | Lockeford Elementary: Office: Lobby | Surface Wrap 4' | F32T82L | Lockeford Elementary: Office: Lobby: Surface Wrap 4': F32T82L | N | 59 | 4 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
9 | 1.1 | Lockeford Elementary | Office | Storage | Lockeford Elementary: Office: Storage | Surface Wrap 4' | F32T82L | Lockeford Elementary: Office: Storage: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
10 | 1.1 | Lockeford Elementary | Building 9-11 | 10 | Lockeford Elementary: Building 9-11: 10 | Surface Wrap 4' | F32T82L | Lockeford Elementary: Building 9-11: 10: Surface Wrap 4': F32T82L | N | 59 | 18 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | Needs new fixtures
11 | 1.1 | Lockeford Elementary | Building 9-11 | 9 | Lockeford Elementary: Building 9-11: 9 | Surface Wrap 4' | F32T82L | Lockeford Elementary: Building 9-11: 9: Surface Wrap 4': F32T82L | N | 59 | 18 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | Needs new fixtures
12 | 1.1 | Lockeford Elementary | Library | Work Rm | Lockeford Elementary: Library: Work Rm | Strip 4' | F32T82L | Lockeford Elementary: Library: Work Rm: Strip 4': F32T82L | N | 59 | 4 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 4 | 8 | 4 | 0
13 | 1.1 | Lockeford Elementary | Library | Entryway | Lockeford Elementary: Library: Entryway | Surface Wrap 4' | F32T82L | Lockeford Elementary: Library: Entryway: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
14 | 1.1 | Lockeford Elementary | Library | Staff RR | Lockeford Elementary: Library: Staff RR | Strip 4' | F32T82L | Lockeford Elementary: Library: Staff RR: Strip 4': F32T82L | N | 59 | 3 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 3 | 6 | 3 | 0
15 | 1.1 | Lockeford Elementary | MPR | Kitchen | Lockeford Elementary: MPR: Kitchen | Surface Wrap 4' | F32T82L | Lockeford Elementary: MPR: Kitchen: Surface Wrap 4': F32T82L | N | 59 | 14 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 14 | 28 | 0 | 0
16 | 1.1 | Lockeford Elementary | MPR | Table Storage | Lockeford Elementary: MPR: Table Storage | Surface Wrap 4' | F32T82L | Lockeford Elementary: MPR: Table Storage: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
17 | 1.1 | Lockeford Elementary | Kindergarten | K1 RR | Lockeford Elementary: Kindergarten: K1 RR | Surface Wrap 4' | F32T82L | Lockeford Elementary: Kindergarten: K1 RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
18 | 1.1 | Lockeford Elementary | Kindergarten | K2 RR | Lockeford Elementary: Kindergarten: K2 RR | Surface Wrap 4' | F32T82L | Lockeford Elementary: Kindergarten: K2 RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
19 | 1.1 | Lockeford Elementary | Office | Storage | Lockeford Elementary: Office: Storage | Strip 4' | F32T82L | Lockeford Elementary: Office: Storage: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Estimated count
20 | 1.1 | Lockeford Elementary | Building 20-23 | 20 | Lockeford Elementary: Building 20-23: 20 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Building 20-23: 20: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
21 | 1.1 | Lockeford Elementary | Building 20-23 | 21 | Lockeford Elementary: Building 20-23: 21 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Building 20-23: 21: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
22 | 1.1 | Lockeford Elementary | Building 20-23 | 22 | Lockeford Elementary: Building 20-23: 22 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Building 20-23: 22: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
23 | 1.1 | Lockeford Elementary | Building 20-23 | 23 | Lockeford Elementary: Building 20-23: 23 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Building 20-23: 23: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
24 | 1.1 | Lockeford Elementary | Building 24-26 | 24 | Lockeford Elementary: Building 24-26: 24 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Building 24-26: 24: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
25 | 1.1 | Lockeford Elementary | Building 24-26 | 25 | Lockeford Elementary: Building 24-26: 25 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Building 24-26: 25: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
26 | 1.1 | Lockeford Elementary | Building 24-26 | 26 | Lockeford Elementary: Building 24-26: 26 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Building 24-26: 26: Recessed 2'X4' Troffer: F32T83L | N | 89 | 16 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 16 | 48 | 0 | 0
27 | 1.1 | Lockeford Elementary | MPR | Girl's RR | Lockeford Elementary: MPR: Girl's RR | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: MPR: Girl's RR: Recessed 2'X4' Troffer: F32T83L | N | 89 | 3 | 3 | 0 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 3 | 9 | 0 | 0
28 | 1.1 | Lockeford Elementary | MPR | Janitor | Lockeford Elementary: MPR: Janitor | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: MPR: Janitor: Recessed 2'X4' Troffer: F32T83L | N | 89 | 1 | 3 | 0 | (3) LED 11-Watt 4' Tubes & Driver | 4620 | 140 | 33 | 1 | 3 | 1 | 0
29 | 1.1 | Lockeford Elementary | MPR | Boy's RR | Lockeford Elementary: MPR: Boy's RR | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: MPR: Boy's RR: Recessed 2'X4' Troffer: F32T83L | N | 89 | 3 | 3 | 0 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 3 | 9 | 0 | 0
30 | 1.1 | Lockeford Elementary | MPR | Storage | Lockeford Elementary: MPR: Storage | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: MPR: Storage: Recessed 2'X4' Troffer: F32T83L | N | 89 | 1 | 3 | 0 | (3) LED 11-Watt 4' Tubes & Driver | 4620 | 140 | 33 | 1 | 3 | 1 | 0
31 | 1.1 | Lockeford Elementary | MPR | PE Rm | Lockeford Elementary: MPR: PE Rm | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: MPR: PE Rm: Recessed 2'X4' Troffer: F32T83L | N | 89 | 16 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 16 | 48 | 0 | 0
32 | 1.1 | Lockeford Elementary | MPR | Cafeteria | Lockeford Elementary: MPR: Cafeteria | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: MPR: Cafeteria: Recessed 2'X4' Troffer: F32T83L | N | 89 | 28 | 3 | 4 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 28 | 84 | 0 | 0
33 | 1.1 | Lockeford Elementary | MPR | Stage | Lockeford Elementary: MPR: Stage | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: MPR: Stage: Recessed 2'X4' Troffer: F32T83L | N | 89 | 11 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 11 | 33 | 0 | 0
34 | 1.1 | Lockeford Elementary | Kindergarten | K1 | Lockeford Elementary: Kindergarten: K1 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Kindergarten: K1: Recessed 2'X4' Troffer: F32T83L | N | 89 | 16 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 16 | 48 | 0 | 0
35 | 1.1 | Lockeford Elementary | Kindergarten | K1 Work Rm | Lockeford Elementary: Kindergarten: K1 Work Rm | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Kindergarten: K1 Work Rm: Recessed 2'X4' Troffer: F32T83L | N | 89 | 2 | 3 | 0 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 2 | 6 | 0 | 0
36 | 1.1 | Lockeford Elementary | Kindergarten | K2 | Lockeford Elementary: Kindergarten: K2 | Recessed 2'X4' Troffer | F32T83L | Lockeford Elementary: Kindergarten: K2: Recessed 2'X4' Troffer: F32T83L | N | 89 | 16 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 16 | 48 | 0 | 0
37 | 1.1 | Lockeford Elementary | Office | 2 | Lockeford Elementary: Office: 2 | Strip 2'X4' | F32T84L | Lockeford Elementary: Office: 2: Strip 2'X4': F32T84L | N | 112 | 12 | 4 | 1 | (4) LED 11-Watt 4' Tubes & Driver | 6160 | 140 | 44 | 12 | 48 | 12 | 0
38 | 1.1 | Lockeford Elementary | Office | 1 | Lockeford Elementary: Office: 1 | Strip 2'X4' | F32T84L | Lockeford Elementary: Office: 1: Strip 2'X4': F32T84L | N | 112 | 12 | 4 | 1 | (4) LED 11-Watt 4' Tubes & Driver | 6160 | 140 | 44 | 12 | 48 | 12 | 0
39 | 1.1 | Lockeford Elementary | Library | Custodian Office | Lockeford Elementary: Library: Custodian Office | Surface Mount 2'X4' | F32T84L | Lockeford Elementary: Library: Custodian Office: Surface Mount 2'X4': F32T84L | N | 112 | 6 | 4 | 0 | (4) LED 11-Watt 4' Tubes & Driver | 6160 | 140 | 44 | 6 | 24 | 6 | 0
40 | 1.1 | Lockeford Elementary | Portable | 8 | Lockeford Elementary: Portable: 8 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 8: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0 | 0
41 | 1.1 | Lockeford Elementary | Portable | 14 | Lockeford Elementary: Portable: 14 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 14: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0 | 0
42 | 1.1 | Lockeford Elementary | Portable | 12 | Lockeford Elementary: Portable: 12 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 12: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0 | 0
43 | 1.1 | Lockeford Elementary | Portable | 16 | Lockeford Elementary: Portable: 16 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 16: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
44 | 1.1 | Lockeford Elementary | Portable | 17 | Lockeford Elementary: Portable: 17 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 17: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
45 | 1.1 | Lockeford Elementary | Portable | 18 | Lockeford Elementary: Portable: 18 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 18: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
46 | 1.1 | Lockeford Elementary | Portable | 15 | Lockeford Elementary: Portable: 15 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 15: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
47 | 1.1 | Lockeford Elementary | Portable | 19 | Lockeford Elementary: Portable: 19 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: 19: Recessed 2'X4' Troffer: F32T84L | N | 112 | 11 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 11 | 44 | 0 | 0
48 | 1.1 | Lockeford Elementary | Portable | P-6 | Lockeford Elementary: Portable: P-6 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: P-6: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0 | 0
49 | 1.1 | Lockeford Elementary | Portable | P-7 | Lockeford Elementary: Portable: P-7 | Recessed 2'X4' Troffer | F32T84L | Lockeford Elementary: Portable: P-7: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0 | 0
50 | 1.1 | Lockeford Elementary | Office | Main Office | Lockeford Elementary: Office: Main Office | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Main Office : Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 4 | 2 | 0 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 4 | 8 | 4 | 0
51 | 1.1 | Lockeford Elementary | Office | Principal | Lockeford Elementary: Office: Principal | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Principal: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 2 | 2 | 0 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 2 | 4 | 2 | 0
52 | 1.1 | Lockeford Elementary | Office | Nurse | Lockeford Elementary: Office: Nurse | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Nurse: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 1 | 2 | 0 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 1 | 2 | 1 | 0
53 | 1.1 | Lockeford Elementary | Office | Hall | Lockeford Elementary: Office: Hall | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Hall: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 3 | 2 | 1 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 3 | 6 | 3 | 0
54 | 1.1 | Lockeford Elementary | Office | Office | Lockeford Elementary: Office: Office | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Office: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 2 | 2 | 0 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 2 | 4 | 2 | 0
55 | 1.1 | Lockeford Elementary | Office | Meeting Rm | Lockeford Elementary: Office: Meeting Rm | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Meeting Rm: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 2 | 2 | 0 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 2 | 4 | 2 | 0
56 | 1.1 | Lockeford Elementary | Library | Computer Lab | Lockeford Elementary: Library: Computer Lab | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Library: Computer Lab: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 10 | 2 | 1 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 10 | 20 | 10 | Roof Access
57 | 1.1 | Lockeford Elementary | Office | Work Rm | Lockeford Elementary: Office: Work Rm | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Work Rm: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 6 | 2 | 1 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 6 | 12 | 6 | 0
58 | 1.1 | Lockeford Elementary | Office | Staff Lounge | Lockeford Elementary: Office: Staff Lounge | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Staff Lounge: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 6 | 2 | 1 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 6 | 12 | 6 | 0
59 | 1.1 | Lockeford Elementary | Office | Copy Rm | Lockeford Elementary: Office: Copy Rm | Surface Mount 2'x4' D/ID | F28T52L | Lockeford Elementary: Office: Copy Rm: Surface Mount 2'x4' D/ID: F28T52L | N | 64 | 5 | 2 | 1 | (2) LED 12-Watt 4' T5 Tubes & Driver | 3360 | 140 | 24 | 5 | 10 | 5 | 0
60 | 1.1 | Lockeford Elementary | Library | Library | Lockeford Elementary: Library: Library | Pendant 1'X4' | F54T5/HO 2L | Lockeford Elementary: Library: Library: Pendant 1'X4': F54T5/HO 2L | N | 117 | 36 | 2 | 4 | (2) LED 24-Watt 4' T5 HO Tubes & Driver | 6720 | 140 | 48 | 36 | 72 | 36 | 0
Annual Total | [10 empty] | 501 |  | 43 |  |  |  |  | 501 | 1463 | 126
Lodi USD: Lockeford Elementary School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
60 | 1.2 | Lockeford Elementary | Parking Lot | Parking | Lockeford Elementary: Parking Lot: Parking | 20' Pole Arm Area | HPS 250W | Lockeford Elementary: Parking Lot: Parking: 20' Pole Arm Area: HPS 250W |  | 295 | 14 | 1 | 0 | LED 75-Watt Pole Arm Area | 12000 | 160 | 75 | 14
61 | 1.2 | Lockeford Elementary | Main | Exterior | Lockeford Elementary: Main: Exterior | Round Wallpack | CFL 32W 1L | Lockeford Elementary: Main: Exterior: Round Wallpack: CFL 32W 1L |  | 32 | 23 | 1 | 0 | LED 10-Watt Mini Wallpack w/ Photocell | 1500 | 150 | 10 | 23
ANNUAL TOTAL | [10 empty] | 37 |  | 0 |  |  |  |  | 37
Lodi USD: Manlio Silva Elementary School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
1 | 1.2 | Manlio Silva Elementary | Campus | Exterior Area | Manlio Silva Elementary: Campus: Exterior Area | Round Wallpack | CFL 26W 1L | Manlio Silva Elementary: Campus: Exterior Area: Round Wallpack: CFL 26W 1L |  | 26 | 16 | 1 | 0 | LED 10-Watt Mini Wallpack w/ Photocell | 1500 | 150 | 10 | 16
2 | 1.2 | Manlio Silva Elementary | Campus | Exterior | Manlio Silva Elementary: Campus: Exterior | Porch Light | CFL 26W 1L | Manlio Silva Elementary: Campus: Exterior: Porch Light: CFL 26W 1L |  | 26 | 10 | 1 | 0 | LED 10-Watt Mini Wallpack w/ Photocell | 1500 | 150 | 10 | 10
3 | 1.2 | Manlio Silva Elementary | Campus | Exterior Area | Manlio Silva Elementary: Campus: Exterior Area | Canopy | HPS 70W | Manlio Silva Elementary: Campus: Exterior Area: Canopy: HPS 70W |  | 95 | 3 | 1 | 0 | LED 15-Watt Canopy 15"x15" | 2250 | 150 | 15 | 3
4 | 1.2 | Manlio Silva Elementary | Campus | Exterior Area | Manlio Silva Elementary: Campus: Exterior Area | Round Wallpack | HPS 100W | Manlio Silva Elementary: Campus: Exterior Area: Round Wallpack: HPS 100W |  | 138 | 11 | 1 | 0 | LED 22-Watt Full-Cutoff Wallpack | 3300 | 150 | 22 | 11
5 | 1.2 | Manlio Silva Elementary | Campus | Exterior Area | Manlio Silva Elementary: Campus: Exterior Area | Yoke Flood | HPS 150W | Manlio Silva Elementary: Campus: Exterior Area: Yoke Flood: HPS 150W |  | 188 | 8 | 1 | 0 | LED 30-Watt Yoke Flood | 4500 | 150 | 30 | 8
6 | 1.2 | Manlio Silva Elementary | Campus | Exterior Area | Manlio Silva Elementary: Campus: Exterior Area | 15' Pole Arm Area | HPS 250W | Manlio Silva Elementary: Campus: Exterior Area: 15' Pole Arm Area: HPS 250W |  | 295 | 26 | 1 | 0 | LED 75-Watt Pole Arm Area | 12000 | 160 | 75 | 26
ANNUAL TOTAL | [10 empty] | 74 |  | 0 |  |  |  |  | 74
Lodi USD: Parklane Elementary School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Parklane Elementary | Admin | K2 RR | Parklane Elementary: Admin: K2 RR | Surface Mount Round | CFL 23W 1L | Parklane Elementary: Admin: K2 RR: Surface Mount Round: CFL 23W 1L | N | 23 | 1 | 1 | 0 | No Change | 0 | 0 | 23 | 1 | 1 | 0 | Circle Surface Mount Fixt
2 | 1.1 | Parklane Elementary | Library | Library | Parklane Elementary: Library: Library | Track Lighting | INC 60W 1L PAR38 | Parklane Elementary: Library: Library: Track Lighting: INC 60W 1L PAR38 | N | 60 | 10 | 1 | 2 | No Change | 0 | 0 | 60 | 10 | 10 | 0 | 0
3 | 1.1 | Parklane Elementary | Admin | Staff Hall | Parklane Elementary: Admin: Staff Hall | Strip 4' | F32T81L | Parklane Elementary: Admin: Staff Hall: Strip 4': F32T81L | N | 31 | 1 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 1 | 1 | 1 | 0
4 | 1.1 | Parklane Elementary | Admin | K1 Storage | Parklane Elementary: Admin: K1 Storage | Strip 4' | F32T81L | Parklane Elementary: Admin: K1 Storage: Strip 4': F32T81L | N | 31 | 1 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 1 | 1 | 1 | Roof Access
5 | 1.1 | Parklane Elementary | Library | Custodial | Parklane Elementary: Library: Custodial | Strip 4' | F32T81L | Parklane Elementary: Library: Custodial: Strip 4': F32T81L | N | 31 | 1 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 1 | 1 | 1 | Roof Access
6 | 1.1 | Parklane Elementary | Admin | Office | Parklane Elementary: Admin: Office | Surface Wrap 4' | F32T82L | Parklane Elementary: Admin: Office: Surface Wrap 4': F32T82L | N | 59 | 9 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 9 | 18 | 0 | 0
7 | 1.1 | Parklane Elementary | Admin | Women's RR | Parklane Elementary: Admin: Women's RR | Surface Wrap 4' | F32T82L | Parklane Elementary: Admin: Women's RR: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
8 | 1.1 | Parklane Elementary | Admin | Work Rm | Parklane Elementary: Admin: Work Rm | Surface Wrap 4' | F32T82L | Parklane Elementary: Admin: Work Rm: Surface Wrap 4': F32T82L | N | 59 | 5 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 5 | 10 | 0 | 0
9 | 1.1 | Parklane Elementary | Admin | K1 RR | Parklane Elementary: Admin: K1 RR | Surface Wrap 4' | F32T82L | Parklane Elementary: Admin: K1 RR: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
10 | 1.1 | Parklane Elementary | Cafeteria | Custodial Office | Parklane Elementary: Cafeteria: Custodial Office | Surface Wrap 4' | F32T82L | Parklane Elementary: Cafeteria: Custodial Office: Surface Wrap 4': F32T82L | N | 59 | 4 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | Roof Access
11 | 1.1 | Parklane Elementary | Cafeteria | Stage | Parklane Elementary: Cafeteria: Stage | Surface Wrap 4' | F32T82L | Parklane Elementary: Cafeteria: Stage: Surface Wrap 4': F32T82L | N | 59 | 16 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 16 | 32 | 0 | 0
12 | 1.1 | Parklane Elementary | Cafeteria | Sprinkler | Parklane Elementary: Cafeteria: Sprinkler | Surface Wrap 4' | F32T82L | Parklane Elementary: Cafeteria: Sprinkler: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
13 | 1.1 | Parklane Elementary | Cafeteria | Storage | Parklane Elementary: Cafeteria: Storage | Surface Wrap 4' | F32T82L | Parklane Elementary: Cafeteria: Storage: Surface Wrap 4': F32T82L | N | 59 | 6 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 6 | 12 | 6 | Roof Access
14 | 1.1 | Parklane Elementary | Cafeteria | Kitchen | Parklane Elementary: Cafeteria: Kitchen | Surface Wrap 4' | F32T82L | Parklane Elementary: Cafeteria: Kitchen: Surface Wrap 4': F32T82L | N | 59 | 18 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 0
15 | 1.1 | Parklane Elementary | Cafeteria | Boy's RR | Parklane Elementary: Cafeteria: Boy's RR | Surface Wrap 4' | F32T82L | Parklane Elementary: Cafeteria: Boy's RR: Surface Wrap 4': F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
16 | 1.1 | Parklane Elementary | Cafeteria | Girl's RR | Parklane Elementary: Cafeteria: Girl's RR | Surface Wrap 4' | F32T82L | Parklane Elementary: Cafeteria: Girl's RR: Surface Wrap 4': F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
17 | 1.1 | Parklane Elementary | Admin | Copy Rm | Parklane Elementary: Admin: Copy Rm | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Admin: Copy Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
18 | 1.1 | Parklane Elementary | Admin | Vice Principal | Parklane Elementary: Admin: Vice Principal | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Admin: Vice Principal: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
19 | 1.1 | Parklane Elementary | Admin | Principal | Parklane Elementary: Admin: Principal | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Admin: Principal: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
20 | 1.1 | Parklane Elementary | Admin | Conference Rm | Parklane Elementary: Admin: Conference Rm | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Admin: Conference Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
21 | 1.1 | Parklane Elementary | Admin | K1 | Parklane Elementary: Admin: K1 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Admin: K1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
22 | 1.1 | Parklane Elementary | Admin | K2 | Parklane Elementary: Admin: K2 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Admin: K2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 0
23 | 1.1 | Parklane Elementary | Library | 5 | Parklane Elementary: Library: 5 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Library: 5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
24 | 1.1 | Parklane Elementary | Library | 6 | Parklane Elementary: Library: 6 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Library: 6: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
25 | 1.1 | Parklane Elementary | Library | 8 | Parklane Elementary: Library: 8 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Library: 8: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
26 | 1.1 | Parklane Elementary | Library | 10 | Parklane Elementary: Library: 10 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Library: 10: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
27 | 1.1 | Parklane Elementary | Library | Speech | Parklane Elementary: Library: Speech | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Library: Speech: Recessed 2'X4' Troffer: F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
28 | 1.1 | Parklane Elementary | Library | Psychology | Parklane Elementary: Library: Psychology | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Library: Psychology: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
29 | 1.1 | Parklane Elementary | Building 35-44 | 35 | Parklane Elementary: Building 35-44: 35 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 35: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
30 | 1.1 | Parklane Elementary | Building 35-44 | 36 | Parklane Elementary: Building 35-44: 36 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 36: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
31 | 1.1 | Parklane Elementary | Building 35-44 | 37 | Parklane Elementary: Building 35-44: 37 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 37: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
32 | 1.1 | Parklane Elementary | Building 35-44 | 38 | Parklane Elementary: Building 35-44: 38 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 38: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
33 | 1.1 | Parklane Elementary | Building 35-44 | 39 | Parklane Elementary: Building 35-44: 39 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 39: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
34 | 1.1 | Parklane Elementary | Building 35-44 | Nurse | Parklane Elementary: Building 35-44: Nurse | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: Nurse: Recessed 2'X4' Troffer: F32T82L | N | 59 | 8 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 8 | 16 | 0 | 0
35 | 1.1 | Parklane Elementary | Building 35-44 | 44 | Parklane Elementary: Building 35-44: 44 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 44: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
36 | 1.1 | Parklane Elementary | Building 35-44 | 43 | Parklane Elementary: Building 35-44: 43 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 43: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
37 | 1.1 | Parklane Elementary | Building 35-44 | 42 | Parklane Elementary: Building 35-44: 42 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 42: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
38 | 1.1 | Parklane Elementary | Building 35-44 | 41 | Parklane Elementary: Building 35-44: 41 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 41: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
39 | 1.1 | Parklane Elementary | Building 35-44 | 40 | Parklane Elementary: Building 35-44: 40 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Building 35-44: 40: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
40 | 1.1 | Parklane Elementary | Portable | P-22 | Parklane Elementary: Portable: P-22 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Portable: P-22: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
41 | 1.1 | Parklane Elementary | Portable | P-23 | Parklane Elementary: Portable: P-23 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Portable: P-23: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
42 | 1.1 | Parklane Elementary | Portable | P-24 | Parklane Elementary: Portable: P-24 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Portable: P-24: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
43 | 1.1 | Parklane Elementary | Portable | P-29 | Parklane Elementary: Portable: P-29 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Portable: P-29: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
44 | 1.1 | Parklane Elementary | Cafeteria | 30 | Parklane Elementary: Cafeteria: 30 | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Cafeteria: 30: Recessed 2'X4' Troffer: F32T82L | N | 59 | 17 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 17 | 34 | 0 | 80% LED
45 | 1.1 | Parklane Elementary | Cafeteria | Staff Lounge | Parklane Elementary: Cafeteria: Staff Lounge | Recessed 2'X4' Troffer | F32T82L | Parklane Elementary: Cafeteria: Staff Lounge: Recessed 2'X4' Troffer: F32T82L | N | 59 | 6 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 6 | 12 | 0 | 0
46 | 1.1 | Parklane Elementary | Portable | P-14 | Parklane Elementary: Portable: P-14 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-14: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
47 | 1.1 | Parklane Elementary | Portable | P-15 | Parklane Elementary: Portable: P-15 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-15: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
48 | 1.1 | Parklane Elementary | Portable | P-16 | Parklane Elementary: Portable: P-16 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-16: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
49 | 1.1 | Parklane Elementary | Portable | P-21 | Parklane Elementary: Portable: P-21 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-21: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
50 | 1.1 | Parklane Elementary | Portable | P-20 | Parklane Elementary: Portable: P-20 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-20: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
51 | 1.1 | Parklane Elementary | Portable | P-19 | Parklane Elementary: Portable: P-19 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-19: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
52 | 1.1 | Parklane Elementary | Portable | P-18 | Parklane Elementary: Portable: P-18 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-18: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
53 | 1.1 | Parklane Elementary | Portable | P-17 | Parklane Elementary: Portable: P-17 | Recessed 2'X4' Troffer | F32T83L | Parklane Elementary: Portable: P-17: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 0
54 | 1.1 | Parklane Elementary | Cafeteria | MPR | Parklane Elementary: Cafeteria: MPR | Surface Mount | F32T84L | Parklane Elementary: Cafeteria: MPR: Surface Mount: F32T84L | N | 112 | 9 | 4 | 2 | (4) LED 11-Watt 4' Tubes & Driver | 6160 | 140 | 44 | 9 | 36 | 9 | High Ceiling, 7 LED Fixtures
55 | 1.1 | Parklane Elementary | Library | Library | Parklane Elementary: Library: Library | Pendant D/ID | F32T86L | Parklane Elementary: Library: Library: Pendant D/ID: F32T86L | N | 175 | 14 | 1 | 2 | (6) LED 11-Watt 4' Tubes & Driver | 9240 | 140 | 66 | 14 | 14 | 28 | 0
Annual Total | [10 empty] | 715 |  | 59 |  |  |  |  | 715 | 1502 | 47
Lodi USD: Parklane Elementary School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
56 | 1.2 | Parklane Elementary | Parklane Elementary School | Exterior Area | Parklane Elementary: Parklane Elementary School: Exterior Area | 25' Round Pole Arm Area | HPS 400W | Parklane Elementary: Parklane Elementary School: Exterior Area: 25' Round Pole Arm Area: HPS 400W |  | 465 | 8 | 1 | 0 | LED 150-Watt Pole Arm Area | 24000 | 160 | 150 | 8
ANNUAL TOTAL | [10 empty] | 8 |  | 0 |  |  |  |  | 8
Lodi USD: Plaza Robles High School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Plaza Robles High | Classroom | 17 | Plaza Robles High: Classroom: 17 | Recessed 2'X2' Troffer | F17T84L | Plaza Robles High: Classroom: 17: Recessed 2'X2' Troffer: F17T84L | N | 61 | 1 | 4 | 0 | LED 22-Watt 2'X2' Retrofit Kit w/ Ctrls | 3520 | 160 | 22 | 1 | 4 | 0 | 0
2 | 1.1 | Plaza Robles High | MPR | Cafeteria | Plaza Robles High: MPR: Cafeteria | Wall Mount 3' | F25T81L | Plaza Robles High: MPR: Cafeteria: Wall Mount 3': F25T81L | N | 26 | 20 | 1 | 2 | (1) LED 10-Watt 3' Tube & Driver | 1400 | 140 | 10 | 20 | 20 | 20 | 0
3 | 1.1 | Plaza Robles High | MPR | Cafeteria | Plaza Robles High: MPR: Cafeteria | Pendant 3' | F25T83L | Plaza Robles High: MPR: Cafeteria: Pendant 3': F25T83L | N | 67 | 36 | 3 | 0 | (3) LED 10-Watt 3' Tubes & Driver | 4200 | 140 | 30 | 36 | 108 | 36 | 0
4 | 1.1 | Plaza Robles High | MPR | Cafeteria | Plaza Robles High: MPR: Cafeteria | Wall Mount 4' | F32T81L | Plaza Robles High: MPR: Cafeteria: Wall Mount 4': F32T81L | N | 31 | 12 | 1 | 1 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 12 | 12 | 12 | 0
5 | 1.1 | Plaza Robles High | MPR | Custodian | Plaza Robles High: MPR: Custodian | Surface Wrap 4' | F32T82L | Plaza Robles High: MPR: Custodian: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
6 | 1.1 | Plaza Robles High | Main | 1 | Plaza Robles High: Main: 1 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 1: Surface Wrap 4': F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
7 | 1.1 | Plaza Robles High | Main | 2 | Plaza Robles High: Main: 2 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 2: Surface Wrap 4': F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
8 | 1.1 | Plaza Robles High | Main | 3 | Plaza Robles High: Main: 3 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 3: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
9 | 1.1 | Plaza Robles High | Main | 4 | Plaza Robles High: Main: 4 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 4: Surface Wrap 4': F32T82L | N | 59 | 23 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 23 | 46 | 0 | 0
10 | 1.1 | Plaza Robles High | Main | 5 | Plaza Robles High: Main: 5 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 5: Surface Wrap 4': F32T82L | N | 59 | 25 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 25 | 50 | 0 | 0
11 | 1.1 | Plaza Robles High | Main | Pottery Kiln Rm | Plaza Robles High: Main: Pottery Kiln Rm | Strip 4' | F32T82L | Plaza Robles High: Main: Pottery Kiln Rm: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Roof Access
12 | 1.1 | Plaza Robles High | Main | 6 | Plaza Robles High: Main: 6 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 6: Surface Wrap 4': F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
13 | 1.1 | Plaza Robles High | Main | 7 | Plaza Robles High: Main: 7 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 7: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
14 | 1.1 | Plaza Robles High | Main | 8 | Plaza Robles High: Main: 8 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 8: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
15 | 1.1 | Plaza Robles High | Main | 9 | Plaza Robles High: Main: 9 | Surface Wrap 4' | F32T82L | Plaza Robles High: Main: 9: Surface Wrap 4': F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
16 | 1.1 | Plaza Robles High | Admin | Electric | Plaza Robles High: Admin: Electric | Strip 4' | F32T82L | Plaza Robles High: Admin: Electric: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | 0
17 | 1.1 | Plaza Robles High | Admin | Staff Break | Plaza Robles High: Admin: Staff Break | Surface Wrap 4' | F32T82L | Plaza Robles High: Admin: Staff Break: Surface Wrap 4': F32T82L | N | 59 | 7 | 2 | 1 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 7 | 14 | 0 | 0
18 | 1.1 | Plaza Robles High | Classroom | 10 | Plaza Robles High: Classroom: 10 | Recessed 2'X4' Troffer | F32T82L | Plaza Robles High: Classroom: 10: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | Roof Access
19 | 1.1 | Plaza Robles High | Classroom | 11 | Plaza Robles High: Classroom: 11 | Recessed 2'X4' Troffer | F32T82L | Plaza Robles High: Classroom: 11: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
20 | 1.1 | Plaza Robles High | Classroom | 14 | Plaza Robles High: Classroom: 14 | Recessed 2'X4' Troffer | F32T82L | Plaza Robles High: Classroom: 14: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | 0
21 | 1.1 | Plaza Robles High | MPR | Serveries | Plaza Robles High: MPR: Serveries | Surface Wrap 4' | F32T83L | Plaza Robles High: MPR: Serveries: Surface Wrap 4': F32T83L | N | 89 | 4 | 3 | 0 | LED 25-Watt Surface Mount Wrap 4' w/ Ctrls | 4000 | 160 | 25 | 4 | 12 | 0 | Roof Access
22 | 1.1 | Plaza Robles High | MPR | Cafeteria | Plaza Robles High: MPR: Cafeteria | Pendant 1'X4' | F32T83L | Plaza Robles High: MPR: Cafeteria: Pendant 1'X4': F32T83L | N | 89 | 24 | 3 | 4 | (3) LED 11-Watt 4' Tubes & Driver | 4620 | 140 | 33 | 24 | 72 | 24 | 0
23 | 1.1 | Plaza Robles High | Classroom | 12 | Plaza Robles High: Classroom: 12 | Recessed 2'X4' Troffer | F32T83L | Plaza Robles High: Classroom: 12: Recessed 2'X4' Troffer: F32T83L | N | 89 | 8 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 8 | 24 | 0 | 0
24 | 1.1 | Plaza Robles High | Classroom | 13 | Plaza Robles High: Classroom: 13 | Recessed 2'X4' Troffer | F32T83L | Plaza Robles High: Classroom: 13: Recessed 2'X4' Troffer: F32T83L | N | 89 | 12 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 12 | 36 | 0 | 0
25 | 1.1 | Plaza Robles High | Classroom | 15 | Plaza Robles High: Classroom: 15 | Recessed 2'X4' Troffer | F32T84L | Plaza Robles High: Classroom: 15: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0 | 0
26 | 1.1 | Plaza Robles High | Classroom | 16 | Plaza Robles High: Classroom: 16 | Recessed 2'X4' Troffer | F32T84L | Plaza Robles High: Classroom: 16: Recessed 2'X4' Troffer: F32T84L | N | 112 | 8 | 4 | 1 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 8 | 32 | 0 | 0
27 | 1.1 | Plaza Robles High | Classroom | 17 | Plaza Robles High: Classroom: 17 | Recessed 2'X4' Troffer | F32T84L | Plaza Robles High: Classroom: 17: Recessed 2'X4' Troffer: F32T84L | N | 112 | 20 | 4 | 2 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 20 | 80 | 0 | 0
Annual Total | [10 empty] | 374 |  | 36 |  |  |  |  | 374 | 874 | 96
Lodi USD: Plaza Robles High School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
28 | 1.2 | Plaza Robles High | Combined | Exterior Area | Plaza Robles High: Combined: Exterior Area | Mini Wallpack | CFL 26W 1L | Plaza Robles High: Combined: Exterior Area: Mini Wallpack: CFL 26W 1L |  | 26 | 9 | 1 | 0 | LED 10-Watt Mini Wallpack w/ Photocell | 1500 | 150 | 10 | 9
ANNUAL TOTAL | [10 empty] | 9 |  | 0 |  |  |  |  | 9
Lodi USD: Podesta Ranch Elementary School: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
1 | 1.2 | Podesta Ranch Elementary | Campus | Walkway | Podesta Ranch Elementary: Campus: Walkway | 15' Poletop Round | HPS 150W | Podesta Ranch Elementary: Campus: Walkway: 15' Poletop Round: HPS 150W |  | 188 | 13 | 1 | 0 | LED 35-Watt Pole Top | 5250 | 150 | 35 | 13
2 | 1.2 | Podesta Ranch Elementary | Campus | Parking Lot | Podesta Ranch Elementary: Campus: Parking Lot | 25' Round Pole Arm Area | HPS 250W | Podesta Ranch Elementary: Campus: Parking Lot: 25' Round Pole Arm Area: HPS 250W |  | 295 | 22 | 1 | 0 | LED 75-Watt Pole Arm Area | 12000 | 160 | 75 | 22
ANNUAL TOTAL | [10 empty] | 35 |  | 0 |  |  |  |  | 35
Lodi USD: Turner Academy: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Turner Academy | Main | 1 | Turner Academy: Main: 1 | Surface Wrap 4' | F32T82L | Turner Academy: Main: 1: Surface Wrap 4': F32T82L | N | 59 | 12 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0
2 | 1.1 | Turner Academy | Main | 2 | Turner Academy: Main: 2 | Surface Wrap 4' | F32T82L | Turner Academy: Main: 2: Surface Wrap 4': F32T82L | N | 59 | 12 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0
3 | 1.1 | Turner Academy | Main | 3 | Turner Academy: Main: 3 | Surface Wrap 4' | F32T82L | Turner Academy: Main: 3: Surface Wrap 4': F32T82L | N | 59 | 12 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0
4 | 1.1 | Turner Academy | Main | Work Rm | Turner Academy: Main: Work Rm | Surface Wrap 4' | F32T82L | Turner Academy: Main: Work Rm: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0
5 | 1.1 | Turner Academy | Main | 4 | Turner Academy: Main: 4 | Recessed 2'X4' Troffer | F32T82L | Turner Academy: Main: 4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0
6 | 1.1 | Turner Academy | Main | 5 | Turner Academy: Main: 5 | Recessed 2'X4' Troffer | F32T82L | Turner Academy: Main: 5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0
7 | 1.1 | Turner Academy | Main | 6 | Turner Academy: Main: 6 | Recessed 2'X4' Troffer | F32T82L | Turner Academy: Main: 6: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0
Annual Total | [10 empty] | 74 |  | 0 |  |  |  |  | 74 | 148 | 0
Lodi USD: Victor Elementary School: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Victor Elementary | Kindergarten | K Storage | Victor Elementary: Kindergarten: K Storage | Strip 4' | F32T81L | Victor Elementary: Kindergarten: K Storage: Strip 4': F32T81L | N | 31 | 1 | 1 | 0 | (1) LED 11-Watt 4' Tube & Driver | 1540 | 140 | 11 | 1 | 1 | 1 | 0
2 | 1.1 | Victor Elementary | Office | Staff Break Rm | Victor Elementary: Office: Staff Break Rm | Surface Wrap 4' | F32T82L | Victor Elementary: Office: Staff Break Rm: Surface Wrap 4': F32T82L | N | 59 | 5 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 5 | 10 | 0 | MISSING OFFICE AND CAFETERIA COUNT
3 | 1.1 | Victor Elementary | Office | Staff RR | Victor Elementary: Office: Staff RR | Strip 4' | F32T82L | Victor Elementary: Office: Staff RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | No access, estimated
4 | 1.1 | Victor Elementary | Library | Copy Rm | Victor Elementary: Library: Copy Rm | Surface Wrap 4' | F32T82L | Victor Elementary: Library: Copy Rm: Surface Wrap 4': F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
5 | 1.1 | Victor Elementary | Library | Storage | Victor Elementary: Library: Storage | Surface Wrap 4' | F32T82L | Victor Elementary: Library: Storage: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
6 | 1.1 | Victor Elementary | Library | Closet | Victor Elementary: Library: Closet | Strip 4' | F32T82L | Victor Elementary: Library: Closet: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | DHW
7 | 1.1 | Victor Elementary | Library | Boy's RR | Victor Elementary: Library: Boy's RR | Strip 4' | F32T82L | Victor Elementary: Library: Boy's RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | No access, estimated
8 | 1.1 | Victor Elementary | Library | Girl's RR | Victor Elementary: Library: Girl's RR | Strip 4' | F32T82L | Victor Elementary: Library: Girl's RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | No access, estimated
9 | 1.1 | Victor Elementary | Kindergarten | K RR | Victor Elementary: Kindergarten: K RR | Strip 4' | F32T82L | Victor Elementary: Kindergarten: K RR: Strip 4': F32T82L | N | 59 | 1 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 1 | 2 | 1 | Roof Access
10 | 1.1 | Victor Elementary | Library | 1 | Victor Elementary: Library: 1 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 10% LED
11 | 1.1 | Victor Elementary | Library | 2 | Victor Elementary: Library: 2 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 18 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 15% LED
12 | 1.1 | Victor Elementary | Library | 3 | Victor Elementary: Library: 3 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 10% LED
13 | 1.1 | Victor Elementary | Library | 4 | Victor Elementary: Library: 4 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
14 | 1.1 | Victor Elementary | Library | 5 | Victor Elementary: Library: 5 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 20 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 20 | 40 | 0 | 5% LED
15 | 1.1 | Victor Elementary | Library | 6 | Victor Elementary: Library: 6 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 6: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
16 | 1.1 | Victor Elementary | Library | 7 | Victor Elementary: Library: 7 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 7: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 10% LED
17 | 1.1 | Victor Elementary | Library | 8 | Victor Elementary: Library: 8 | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Library: 8: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
18 | 1.1 | Victor Elementary | Kindergarten | K | Victor Elementary: Kindergarten: K | Recessed 2'X4' Troffer | F32T82L | Victor Elementary: Kindergarten: K: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
19 | 1.1 | Victor Elementary | Portable | 10 | Victor Elementary: Portable: 10 | Recessed 2'X4' Troffer | F32T84L | Victor Elementary: Portable: 10: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
20 | 1.1 | Victor Elementary | Portable | 11 | Victor Elementary: Portable: 11 | Recessed 2'X4' Troffer | F32T84L | Victor Elementary: Portable: 11: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
21 | 1.1 | Victor Elementary | Portable | 12 | Victor Elementary: Portable: 12 | Recessed 2'X4' Troffer | F32T84L | Victor Elementary: Portable: 12: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
22 | 1.1 | Victor Elementary | Portable | 13 | Victor Elementary: Portable: 13 | Recessed 2'X4' Troffer | F32T84L | Victor Elementary: Portable: 13: Recessed 2'X4' Troffer: F32T84L | N | 112 | 10 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 10 | 40 | 0 | 0
23 | 1.1 | Victor Elementary | Portable | Staff/ Intermediate RR | Victor Elementary: Portable: Staff/ Intermediate RR | Recessed 2'X4' Troffer | F32T84L | Victor Elementary: Portable: Staff/ Intermediate RR: Recessed 2'X4' Troffer: F32T84L | N | 112 | 1 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 1 | 4 | 0 | No access, estimated
24 | 1.1 | Victor Elementary | Portable | 9 | Victor Elementary: Portable: 9 | Recessed 2'X4' Troffer | F32T84L | Victor Elementary: Portable: 9: Recessed 2'X4' Troffer: F32T84L | N | 112 | 12 | 4 | 0 | LED 30-Watt 2'X4' Retrofit Kit w/ Ctrls | 4800 | 160 | 30 | 12 | 48 | 0 | 0
25 | 1.1 | Victor Elementary | Library | Library | Victor Elementary: Library: Library | Pendant D/ID | F32T86L | Victor Elementary: Library: Library: Pendant D/ID: F32T86L | N | 175 | 16 | 6 | 0 | (6) LED 11-Watt 4' Tubes & Driver | 9240 | 140 | 66 | 16 | 96 | 32 | 0
Annual Total | [10 empty] | 267 |  | 0 |  |  |  |  | 267 | 703 | 40
Lodi USD: Wagner-Holt Elementary: Interior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Room/Area | Site: Building: Room/Area | Fixture Type | Lighting (Pre) | UD | OCS (Y/N) | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1 | 1.1 | Wagner-Holt Elementary | B | Library | Wagner-Holt Elementary: B: Library | Can Recessed 4'' | INC 45W 1L PAR30 | Wagner-Holt Elementary: B: Library: Can Recessed 4'': INC 45W 1L PAR30 | N | 45 | 10 | 1 | 0 | LED 5-Watt 4" Downlight Retrofit | 600 | 120 | 5 | 10 | 10 | 0 | 0
2 | 1.1 | Wagner-Holt Elementary | H | Custodial | Wagner-Holt Elementary: H: Custodial | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: H: Custodial: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
3 | 1.1 | Wagner-Holt Elementary | H | Staff RR 2 | Wagner-Holt Elementary: H: Staff RR 2 | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: H: Staff RR 2: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
4 | 1.1 | Wagner-Holt Elementary | H | Girl's RR | Wagner-Holt Elementary: H: Girl's RR | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: H: Girl's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
5 | 1.1 | Wagner-Holt Elementary | H | Boy's RR | Wagner-Holt Elementary: H: Boy's RR | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: H: Boy's RR: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | DS
6 | 1.1 | Wagner-Holt Elementary | H | H Work Rm | Wagner-Holt Elementary: H: H Work Rm | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: H: H Work Rm: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
7 | 1.1 | Wagner-Holt Elementary | MPR | Break Rm | Wagner-Holt Elementary: MPR: Break Rm | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: MPR: Break Rm: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
8 | 1.1 | Wagner-Holt Elementary | MPR | Stage | Wagner-Holt Elementary: MPR: Stage | Strip 4' | F32T82L | Wagner-Holt Elementary: MPR: Stage: Strip 4': F32T82L | N | 59 | 16 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 16 | 32 | 16 | 0
9 | 1.1 | Wagner-Holt Elementary | MPR | Kitchen | Wagner-Holt Elementary: MPR: Kitchen | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: MPR: Kitchen: Surface Wrap 4': F32T82L | N | 59 | 18 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 0
10 | 1.1 | Wagner-Holt Elementary | MPR | Custodial | Wagner-Holt Elementary: MPR: Custodial | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: MPR: Custodial: Surface Wrap 4': F32T82L | N | 59 | 4 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 4 | 8 | 4 | 0
11 | 1.1 | Wagner-Holt Elementary | MPR | Fire Riser Rm | Wagner-Holt Elementary: MPR: Fire Riser Rm | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: MPR: Fire Riser Rm: Surface Wrap 4': F32T82L | N | 59 | 6 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 6 | 12 | 6 | 0
12 | 1.1 | Wagner-Holt Elementary | D | Electric Rm | Wagner-Holt Elementary: D: Electric Rm | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: D: Electric Rm: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 0 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 2 | 4 | 2 | 0
13 | 1.1 | Wagner-Holt Elementary | D | D3 RR | Wagner-Holt Elementary: D: D3 RR | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: D: D3 RR: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
14 | 1.1 | Wagner-Holt Elementary | D | D4 RR | Wagner-Holt Elementary: D: D4 RR | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: D: D4 RR: Surface Wrap 4': F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
15 | 1.1 | Wagner-Holt Elementary | B | Library | Wagner-Holt Elementary: B: Library | Pendant 4' | F32T82L | Wagner-Holt Elementary: B: Library: Pendant 4': F32T82L | N | 59 | 20 | 2 | 2 | (2) LED 11-Watt 4' Tubes & Driver | 3080 | 140 | 22 | 20 | 40 | 20 | 0
16 | 1.1 | Wagner-Holt Elementary | B | AV Rm | Wagner-Holt Elementary: B: AV Rm | Surface Wrap 4' | F32T82L | Wagner-Holt Elementary: B: AV Rm: Surface Wrap 4': F32T82L | N | 59 | 2 | 2 | 2 | LED 20-Watt Surface Mount Wrap 4' w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
17 | 1.1 | Wagner-Holt Elementary | A | A2 | Wagner-Holt Elementary: A: A2 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: A: A2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 17 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 17 | 34 | 0 | Dual Switch (CB)
18 | 1.1 | Wagner-Holt Elementary | A | A3 | Wagner-Holt Elementary: A: A3 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: A: A3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 28 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | Dual Switch (CB)
19 | 1.1 | Wagner-Holt Elementary | A | A4 | Wagner-Holt Elementary: A: A4 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: A: A4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 28 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | 3 Switch
20 | 1.1 | Wagner-Holt Elementary | A | A5 | Wagner-Holt Elementary: A: A5 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: A: A5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 28 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | 3 Switch
21 | 1.1 | Wagner-Holt Elementary | A | A6 | Wagner-Holt Elementary: A: A6 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: A: A6: Recessed 2'X4' Troffer: F32T82L | N | 59 | 28 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | 2 Switch
22 | 1.1 | Wagner-Holt Elementary | A | A7 | Wagner-Holt Elementary: A: A7 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: A: A7: Recessed 2'X4' Troffer: F32T82L | N | 59 | 28 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 28 | 56 | 0 | 3 Switch
23 | 1.1 | Wagner-Holt Elementary | A | A1 | Wagner-Holt Elementary: A: A1 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: A: A1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 10 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 10 | 20 | 0 | 2 Switch
24 | 1.1 | Wagner-Holt Elementary | F | F1 | Wagner-Holt Elementary: F: F1 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: F: F1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 3 Switch
25 | 1.1 | Wagner-Holt Elementary | F | F2 | Wagner-Holt Elementary: F: F2 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: F: F2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 3 Switch
26 | 1.1 | Wagner-Holt Elementary | F | F3 | Wagner-Holt Elementary: F: F3 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: F: F3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 3 Switch
27 | 1.1 | Wagner-Holt Elementary | F | F4 | Wagner-Holt Elementary: F: F4 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: F: F4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 3 Switch
28 | 1.1 | Wagner-Holt Elementary | H | H1 | Wagner-Holt Elementary: H: H1 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | DS
29 | 1.1 | Wagner-Holt Elementary | H | H3 | Wagner-Holt Elementary: H: H3 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | DS 20% LED
30 | 1.1 | Wagner-Holt Elementary | H | H5 | Wagner-Holt Elementary: H: H5 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 12 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 12 | 24 | 0 | DS 50% LED
31 | 1.1 | Wagner-Holt Elementary | H | H7 | Wagner-Holt Elementary: H: H7 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H7: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | DS 20% LED
32 | 1.1 | Wagner-Holt Elementary | H | H8 | Wagner-Holt Elementary: H: H8 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H8: Recessed 2'X4' Troffer: F32T82L | N | 59 | 23 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 23 | 46 | 0 | DS
33 | 1.1 | Wagner-Holt Elementary | H | H10 | Wagner-Holt Elementary: H: H10 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H10: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | DS
34 | 1.1 | Wagner-Holt Elementary | H | H9 | Wagner-Holt Elementary: H: H9 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H9: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | DS
35 | 1.1 | Wagner-Holt Elementary | H | H6 | Wagner-Holt Elementary: H: H6 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H6: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | DS
36 | 1.1 | Wagner-Holt Elementary | H | H4 | Wagner-Holt Elementary: H: H4 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | DS
37 | 1.1 | Wagner-Holt Elementary | H | H2 | Wagner-Holt Elementary: H: H2 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: H: H2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | DS 10% LED
38 | 1.1 | Wagner-Holt Elementary | MPR | Break Rm | Wagner-Holt Elementary: MPR: Break Rm | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: MPR: Break Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 6 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 6 | 12 | 0 | 0
39 | 1.1 | Wagner-Holt Elementary | MPR | Music Rm | Wagner-Holt Elementary: MPR: Music Rm | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: MPR: Music Rm: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
40 | 1.1 | Wagner-Holt Elementary | D | Office | Wagner-Holt Elementary: D: Office | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: D: Office: Recessed 2'X4' Troffer: F32T82L | N | 59 | 11 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 11 | 22 | 0 | 0
41 | 1.1 | Wagner-Holt Elementary | D | Vice Principal | Wagner-Holt Elementary: D: Vice Principal | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: D: Vice Principal: Recessed 2'X4' Troffer: F32T82L | N | 59 | 2 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 2 | 4 | 0 | 0
42 | 1.1 | Wagner-Holt Elementary | D | Staff RR | Wagner-Holt Elementary: D: Staff RR | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: D: Staff RR: Recessed 2'X4' Troffer: F32T82L | N | 59 | 1 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 1 | 2 | 0 | 0
43 | 1.1 | Wagner-Holt Elementary | D | Principal | Wagner-Holt Elementary: D: Principal | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: D: Principal: Recessed 2'X4' Troffer: F32T82L | N | 59 | 4 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 4 | 8 | 0 | 0
44 | 1.1 | Wagner-Holt Elementary | D | Nurse Office | Wagner-Holt Elementary: D: Nurse Office | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: D: Nurse Office: Recessed 2'X4' Troffer: F32T82L | N | 59 | 3 | 2 | 1 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
45 | 1.1 | Wagner-Holt Elementary | D | D3 | Wagner-Holt Elementary: D: D3 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: D: D3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 18 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 0
46 | 1.1 | Wagner-Holt Elementary | D | D4 | Wagner-Holt Elementary: D: D4 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: D: D4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 18 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 18 | 36 | 0 | 0
47 | 1.1 | Wagner-Holt Elementary | E | E1 | Wagner-Holt Elementary: E: E1 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: E: E1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
48 | 1.1 | Wagner-Holt Elementary | E | E2 | Wagner-Holt Elementary: E: E2 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: E: E2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
49 | 1.1 | Wagner-Holt Elementary | E | E3 | Wagner-Holt Elementary: E: E3 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: E: E3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
50 | 1.1 | Wagner-Holt Elementary | E | E4 | Wagner-Holt Elementary: E: E4 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: E: E4: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
51 | 1.1 | Wagner-Holt Elementary | E | E5 | Wagner-Holt Elementary: E: E5 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: E: E5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 24 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 24 | 48 | 0 | 0
52 | 1.1 | Wagner-Holt Elementary | B | Psych. Office | Wagner-Holt Elementary: B: Psych. Office | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: Psych. Office: Recessed 2'X4' Troffer: F32T82L | N | 59 | 3 | 2 | 0 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 3 | 6 | 0 | 0
53 | 1.1 | Wagner-Holt Elementary | B | B3 | Wagner-Holt Elementary: B: B3 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: B3: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 0
54 | 1.1 | Wagner-Holt Elementary | B | B2 | Wagner-Holt Elementary: B: B2 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: B2: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
55 | 1.1 | Wagner-Holt Elementary | B | B6 | Wagner-Holt Elementary: B: B6 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: B6: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 0
56 | 1.1 | Wagner-Holt Elementary | B | B5 | Wagner-Holt Elementary: B: B5 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: B5: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 0
57 | 1.1 | Wagner-Holt Elementary | B | B7 | Wagner-Holt Elementary: B: B7 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: B7: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 0
58 | 1.1 | Wagner-Holt Elementary | B | B8 | Wagner-Holt Elementary: B: B8 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: B8: Recessed 2'X4' Troffer: F32T82L | N | 59 | 19 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 19 | 38 | 0 | 0
59 | 1.1 | Wagner-Holt Elementary | B | B1 | Wagner-Holt Elementary: B: B1 | Recessed 2'X4' Troffer | F32T82L | Wagner-Holt Elementary: B: B1: Recessed 2'X4' Troffer: F32T82L | N | 59 | 21 | 2 | 2 | LED 20-Watt 2'X4' Retrofit Kit w/ Ctrls | 3200 | 160 | 20 | 21 | 42 | 0 | 0
60 | 1.1 | Wagner-Holt Elementary | G | G1 | Wagner-Holt Elementary: G: G1 | Recessed 2'X4' Troffer | F32T83L | Wagner-Holt Elementary: G: G1: Recessed 2'X4' Troffer: F32T83L | N | 89 | 13 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 13 | 39 | 0 | 3 Switch
61 | 1.1 | Wagner-Holt Elementary | G | G2 | Wagner-Holt Elementary: G: G2 | Recessed 2'X4' Troffer | F32T83L | Wagner-Holt Elementary: G: G2: Recessed 2'X4' Troffer: F32T83L | N | 89 | 10 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 10 | 30 | 0 | 3 Switch
62 | 1.1 | Wagner-Holt Elementary | D | Teacher Work Rm | Wagner-Holt Elementary: D: Teacher Work Rm | Recessed 2'X4' Troffer | F32T83L | Wagner-Holt Elementary: D: Teacher Work Rm: Recessed 2'X4' Troffer: F32T83L | N | 89 | 6 | 3 | 1 | LED 24-Watt 2'X4' Retrofit Kit w/ Ctrls | 3840 | 160 | 24 | 6 | 18 | 0 | 0
63 | 1.1 | Wagner-Holt Elementary | MPR | MPR | Wagner-Holt Elementary: MPR: MPR | Surface Mount Highbay 2'X4' | F54T5/HO 4L | Wagner-Holt Elementary: MPR: MPR: Surface Mount Highbay 2'X4': F54T5/HO 4L | N | 234 | 16 | 4 | 4 | LED 85-Watt Surface Mount Highbay w/ Ctrls | 15000 | 176.4706 | 85 | 16 | 64 | 0 | 0
Annual Total | [10 empty] | 960 |  | 89 |  |  |  |  | 960 | 1971 | 50
Lodi USD: Wagner-Holt Elementary: Exterior Lighting
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
# | WE # | Site | Building | Area Served | Building: Area Served | Fixture Type | Lighting (Pre) | UD |  | Pre-Watts | Pre # Fixt | Lamps per Fixture | Approx. Emergency Fixture / Ballast Qty | Lighting (Post) | Output Lumens | Minimum Efficacy (LPW) | Post-Watts | Post # Fixt
64 | 1.2 | Wagner-Holt Elementary | Library | Exterior Area | Wagner-Holt Elementary: Library: Exterior | Can Recessed 10" | CFM 32W 1L | Wagner-Holt Elementary: Library: Exterior: Can Recessed 10": CFM 32W 1L |  | 36.8 | 5 | 1 | 0 | LED 12-Watt Canopy 1'x1' | 1800 | 150 | 12 | 5
65 | 1.2 | Wagner-Holt Elementary | A Bldg | Exterior Area | Wagner-Holt Elementary: A Bldg: Exterior | Can Recessed 10" | CFM 32W 1L | Wagner-Holt Elementary: A Bldg: Exterior: Can Recessed 10": CFM 32W 1L |  | 36.8 | 10 | 1 | 0 | LED 12-Watt Canopy 1'x1' | 1800 | 150 | 12 | 10
66 | 1.2 | Wagner-Holt Elementary | Office / MPR | Exterior Area | Wagner-Holt Elementary: Office / MPR: Exterior | Can Recessed 10" | CFM 32W 1L | Wagner-Holt Elementary: Office / MPR: Exterior: Can Recessed 10": CFM 32W 1L |  | 36.8 | 13 | 1 | 0 | LED 12-Watt Canopy 1'x1' | 1800 | 150 | 12 | 13
67 | 1.2 | Wagner-Holt Elementary | H Bldg | Exterior | Wagner-Holt Elementary: H Bldg: Exterior | Wallpack | HPS 150W | Wagner-Holt Elementary: H Bldg: Exterior: Wallpack: HPS 150W |  | 188 | 13 | 1 | 0 | LED 28-Watt Full-Cutoff Wallpack | 4200 | 150 | 28 | 13
68 | 1.2 | Wagner-Holt Elementary | Library | Exterior | Wagner-Holt Elementary: Library: Exterior | Wallpack | HPS 150W | Wagner-Holt Elementary: Library: Exterior: Wallpack: HPS 150W |  | 188 | 8 | 1 | 0 | LED 28-Watt Full-Cutoff Wallpack | 4200 | 150 | 28 | 8
69 | 1.2 | Wagner-Holt Elementary | A Bldg | Exterior | Wagner-Holt Elementary: A Bldg: Exterior | Wallpack | HPS 150W | Wagner-Holt Elementary: A Bldg: Exterior: Wallpack: HPS 150W |  | 188 | 7 | 1 | 0 | LED 28-Watt Full-Cutoff Wallpack | 4200 | 150 | 28 | 7
70 | 1.2 | Wagner-Holt Elementary | Office / MPR | Exterior | Wagner-Holt Elementary: Office / MPR: Exterior | Wallpack | HPS 150W | Wagner-Holt Elementary: Office / MPR: Exterior: Wallpack: HPS 150W |  | 188 | 14 | 1 | 0 | LED 28-Watt Full-Cutoff Wallpack | 4200 | 150 | 28 | 14
71 | 1.2 | Wagner-Holt Elementary | Portable | Exterior | Wagner-Holt Elementary: Portable: Exterior | Wallpack | HPS 150W | Wagner-Holt Elementary: Portable: Exterior: Wallpack: HPS 150W |  | 188 | 11 | 1 | 0 | LED 28-Watt Full-Cutoff Wallpack | 4200 | 150 | 28 | 11
72 | 1.2 | Wagner-Holt Elementary | Campus | Parking Lot | Wagner-Holt Elementary: Campus: Parking Lot | 25' Poletop Square | HPS 250W | Wagner-Holt Elementary: Campus: Parking Lot: 25' Poletop Square: HPS 250W |  | 295 | 3 | 1 | 0 | LED 60-Watt Pole Top | 9000 | 150 | 60 | 3
ANNUAL TOTAL | [10 empty] | 84 |  | 0 |  |  |  |  | 84
Lodi USD: WE-1.1 Replace Selected Interior Lighting with LED Lighting: Building Summary
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
WE # |  |  | Site | [7 empty] | Pre # Fixt |  | Approx. Emergency Fixture / Ballast Qty |  |  |  |  | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1.1 |  |  | Creekside Elementary | [7 empty] | 955 |  | 82 |  |  |  |  | 955 | 2048 | 106
1.1 |  |  | Delta Sierra Middle | [7 empty] | 1049 |  | 67 |  |  |  |  | 1049 | 2084 | 149
1.1 |  |  | Dorothy Mahin School | [7 empty] | 164 |  | 0 |  |  |  |  | 164 | 333 | 39
1.1 |  |  | GL Mosher Elementary | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.1 |  |  | Extension Road Sites | [7 empty] | 261 |  | 0 |  |  |  |  | 261 | 1042 | 0
1.1 |  |  | John Muir Elementary | [7 empty] | 142 |  | 0 |  |  |  |  | 142 | 304 | 42
1.1 |  |  | Lockeford Elementary | [7 empty] | 501 |  | 43 |  |  |  |  | 501 | 1463 | 126
1.1 |  |  | Manlio Silva Elementary | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.1 |  |  | McNair High | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.1 |  |  | Parklane Elementary | [7 empty] | 715 |  | 59 |  |  |  |  | 715 | 1502 | 47
1.1 |  |  | Plaza Robles High | [7 empty] | 374 |  | 36 |  |  |  |  | 374 | 874 | 96
1.1 |  |  | Podesta Ranch Elementary | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.1 |  |  | Turner Academy | [7 empty] | 74 |  | 0 |  |  |  |  | 74 | 148 | 0
1.1 |  |  | Victor Elementary | [7 empty] | 267 |  | 0 |  |  |  |  | 267 | 703 | 40
1.1 |  |  | Wagner-Holt Elementary | [7 empty] | 960 |  | 89 |  |  |  |  | 960 | 1971 | 50
ANNUAL TOTAL | [10 empty] | 5462 |  | 376 |  |  |  |  | 5462 | 12472 | 695
Lodi USD: WE-1.2 Replace Selected Exterior Lighting with LED Fixtures: Building Summary
General Information | [5 empty] | Existing Fixture Data | [7 empty] | Proposed Fixture Data
WE # |  |  | Site | [7 empty] | Pre # Fixt |  | Approx. Emergency Fixture / Ballast Qty |  |  |  |  | Post # Fixt | Total Post # Lamps | Total Post # Ballast | Notes
1.2 |  |  | Creekside Elementary | [7 empty] | 32 |  | 0 |  |  |  |  | 32 | 0 | 0
1.2 |  |  | Delta Sierra Middle | [7 empty] | 39 |  | 0 |  |  |  |  | 39 | 0 | 0
1.2 |  |  | Dorothy Mahin School | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.2 |  |  | GL Mosher Elementary | [7 empty] | 53 |  | 0 |  |  |  |  | 53 | 53 | 0
1.2 |  |  | Extension Road Sites | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.2 |  |  | John Muir Elementary | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.2 |  |  | Lockeford Elementary | [7 empty] | 37 |  | 0 |  |  |  |  | 37 | 0 | 0
1.2 |  |  | Manlio Silva Elementary | [7 empty] | 74 |  | 0 |  |  |  |  | 74 | 0 | 0
1.2 |  |  | McNair High | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.2 |  |  | Parklane Elementary | [7 empty] | 8 |  | 0 |  |  |  |  | 8 | 0 | 0
1.2 |  |  | Plaza Robles High | [7 empty] | 9 |  | 0 |  |  |  |  | 9 | 0 | 0
1.2 |  |  | Podesta Ranch Elementary | [7 empty] | 35 |  | 0 |  |  |  |  | 35 | 0 | 0
1.2 |  |  | Turner Academy | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.2 |  |  | Victor Elementary | [7 empty] | 0 |  | 0 |  |  |  |  | 0 | 0 | 0
1.2 |  |  | Wagner-Holt Elementary | [7 empty] | 84 |  | 0 |  |  |  |  | 84 | 0 | 0
ANNUAL TOTAL | [10 empty] | 371 |  | 0 |  |  |  |  | 371 | 53 | 0

## WE 2.1.0) Replace HVAC Base Bid
Lodi USD: John Muir Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units (Base Bid)
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230968 | No ID TagJohn Muir ElementaryAdmin / OfficeRooftopOfficesTrane: TTA048C300A0H08230968 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0668-0669
2 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230967 | No ID TagJohn Muir ElementaryAdmin / OfficeRooftopOfficesTrane: TTA048C300A0H08230967 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0670-0672
3 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230969 | No ID TagJohn Muir ElementaryAdmin / OfficeRooftopOfficesTrane: TTA048C300A0H08230969 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0674-0675
4 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230968 | No ID TagJohn Muir ElementaryAdmin / OfficeRooftopOfficesTrane: TTA048C300A0H08230968 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16
5 | CU 11 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230966 | CU 11John Muir ElementaryMPRGround MountMPRTrane: TTA048C300A0H08230966 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0678-0679
6 | CU 4 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230988 | CU 4John Muir ElementaryMPRGround MountMPRTrane: TTA048C300A0H08230988 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0680-0681
7 | CU 5 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230964 | CU 5John Muir ElementaryMPRGround MountMPRTrane: TTA048C300A0H08230964 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0682-0683
8 | CU 6 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Trane | TTA036C300A0 | Trane: TTA036C300A0 | H08230855 | CU 6John Muir ElementaryMPRGround MountMPRTrane: TTA036C300A0H08230855 | 1993 | 3 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 3 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0685-0686
9 | CU 7 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230971 | CU 7John Muir ElementaryMPRGround MountMPRTrane: TTA048C300A0H08230971 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0687-0689
10 | CU 3 | John Muir Elementary | MPR | Rooftop | Kitchen | Split Condenser | Trane | TTA042C300A0 | Trane: TTA042C300A0 | H08230910 | CU 3John Muir ElementaryMPRRooftopKitchenTrane: TTA042C300A0H08230910 | 1993 | 3.5 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 3.5 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0698-0699
11 | CU 10 | John Muir Elementary | MPR | Rooftop | Kitchen | Split Condenser | Trane | TTA048C300A0 | Trane: TTA048C300A0 | H08230970 | CU 10John Muir ElementaryMPRRooftopKitchenTrane: TTA048C300A0H08230970 | 1993 | 4 | 7.6 | Poor | 208 | 22 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | est. indoor fan HP | JB, 9/17/2025 | IMG_0700-0702
| ANNUAL TOTAL | [11 empty] | 42.5 | [7 empty] | 42.5
Lodi USD: Ronald McNair High: Replace Selected HVAC Units with High Efficiency HVAC Units (Base Bid)
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-C6B | Ronald McNair High | Gym | Little Gym Roof | Auxiliary Gym C4 East | Gas Package | Trane | YCD301C4H0CA | Trane: YCD301C4H0CA | 430100581D | AC-C6BRonald McNair HighGymLittle Gym RoofAuxiliary Gym C4 EastTrane: YCD301C4H0CA430100581D | 2004 | 25 | 9.875 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48QE | 25 | 15.3 | 0 | JB_8-27-2025 | IMG_9877-9882
2 | AC-C6A | Ronald McNair High | Gym | Little Gym Roof | Auxiliary Gym C4 West | Gas Package | Trane | YCD301C4H0CA | Trane: YCD301C4H0CA | 430100550D | AC-C6ARonald McNair HighGymLittle Gym RoofAuxiliary Gym C4 WestTrane: YCD301C4H0CA430100550D | 2004 | 25 | 9.875 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48QE | 25 | 15.3 | 0 | JB_8-27-2025 | IMG_9883-9887
3 | AC-C1B | Ronald McNair High | Gym | Big Gym Roof | Main Gym C2 NE | Gas Package | Trane | YCD600A4HN0B8NC40000000H0000000 | Trane: YCD600A4HN0B8NC40000000H0000000 | C04B00959 | AC-C1BRonald McNair HighGymBig Gym RoofMain Gym C2 NETrane: YCD600A4HN0B8NC40000000H0000000C04B00959 | 2004 | 50 | 9.48 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48V | 50 | 17.7 | Can't read fan size | JB_8-27-2025 | IMG_9891-9895
4 | AC-C2B | Ronald McNair High | Gym | Big Gym Roof | Main Gym C2 SE | Gas Package | Trane | YCD600A4HN0B8NC40000000H0000000 | Trane: YCD600A4HN0B8NC40000000H0000000 | C04B00961 | AC-C2BRonald McNair HighGymBig Gym RoofMain Gym C2 SETrane: YCD600A4HN0B8NC40000000H0000000C04B00961 | 2004 | 50 | 9.48 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48V | 50 | 17.7 | Can't read fan size | JB_8-27-2025 | IMG_9896-9907
5 | AC-C2A | Ronald McNair High | Gym | Big Gym Roof | Main Gym C2 SW | Gas Package | Trane | YCD600A4HN0B8NC40000000H0000000 | Trane: YCD600A4HN0B8NC40000000H0000000 | C04B00960 | AC-C2ARonald McNair HighGymBig Gym RoofMain Gym C2 SWTrane: YCD600A4HN0B8NC40000000H0000000C04B00960 | 2004 | 50 | 9.48 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48V | 50 | 17.7 | 0 | JB_8-27-2025 | IMG_9908-9913
6 | AC-C1A | Ronald McNair High | Gym | Big Gym Roof | Main Gym C2 NW | Gas Package | Trane | YCD600A4HN0B8NC40000000H0000000 | Trane: YCD600A4HN0B8NC40000000H0000000 | C04B00958 | AC-C1ARonald McNair HighGymBig Gym RoofMain Gym C2 NWTrane: YCD600A4HN0B8NC40000000H0000000C04B00958 | 2004 | 50 | 9.48 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48V | 50 | 17.7 | Can't read fan size | JB_8-27-2025 | IMG_9914-9921
7 | AC-D8 | Ronald McNair High | Performing Arts | Theater Roof | Rm D38 Theater | Gas Package | Trane | Illegible | Trane: Illegible | - | AC-D8Ronald McNair HighPerforming ArtsTheater RoofRm D38 TheaterTrane: Illegible- | 2005 | 50 | 9.6 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48V | 50 | 17.7 | Can't read Name Plate, Size est | JB_8-27-2025 | IMG_9968-9977
8 | AC-D5 | Ronald McNair High | Performing Arts | Stage Roof | Rm D33 Stage | Gas Package | Trane | YCD181C4H0CA | Trane: YCD181C4H0CA | 514100942D | AC-D5Ronald McNair HighPerforming ArtsStage RoofRm D33 StageTrane: YCD181C4H0CA514100942D | 2005 | 15 | 9.6 | Poor | 460 |  | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 15 | 16.5 | 0 | JB_8-27-2025 | IMG_9983-9989
| ANNUAL TOTAL | [11 empty] | 315 | [7 empty] | 315
Lodi USD: Parklane Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units (Base Bid)
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | No ID Tag | Parklane Elementary | K2 | Ground Mount | Classroom | Split Condenser | Carrier | No Nameplate | Carrier: No Nameplate | - | No ID TagParklane ElementaryK2Ground MountClassroomCarrier: No Nameplate- | Old | 4 | 8.5 | Poor | 460 | 0 | 3 | New High Efficiency Split Condenser + Furnace | Carrier: 26SPA6 | 4 | 16 | Older unit, replace. Est. size | JB_7-28-2025 | IMG_7264
2 | No ID Tag | Parklane Elementary | Main | Rooftop | Interior | Gas Package | Snyder General | CUR085EN | Snyder General: CUR085EN | 5U842332-02 | No ID TagParklane ElementaryMainRooftopInteriorSnyder General: CUR085EN5U842332-02 | 1996 | 8.5 | 7.825 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 8.5 | 17.3 | Can't read Name Plate, Size est | JB_8-27-2025 | IMG_0021-0024
| ANNUAL TOTAL | [11 empty] | 12.5 | [7 empty] | 12.5
Lodi USD: Sutherland Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units (Base Bid)
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | No ID Tag | Sutherland Elementary | Library | Rooftop | Library | Gas Package | Inter-City Products | PGDB036 | Inter-City Products: PGDB024 | Illegible | No ID TagSutherland ElementaryLibraryRooftopLibraryInter-City Products: PGDB024Illegible | 1992 | 2 | 7.525 | Poor | 208 | 0 | 1 | New High Efficiency Gas Package Unit | Carrier: 48NG | 2 | 15.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
2 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | R920100011 | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XR920100011 | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
3 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | R920100003 | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XR920100003 | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
4 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
5 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | R920510006 | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XR920510006 | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 12/22/2025 | 0
6 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | R920100002 | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XR920100002 | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 12/22/2025 | 0
7 | No ID Tag | Sutherland Elementary | Library | Rooftop | Library | Gas Package | Inter-City Products | PGDB036 | Inter-City Products: PGDB024 | Illegible | No ID TagSutherland ElementaryLibraryRooftopLibraryInter-City Products: PGDB024Illegible | 1992 | 2 | 7.525 | Poor | 208 | 0 | 1 | New High Efficiency Gas Package Unit | Carrier: 48NG | 2 | 15.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
8 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | R914700003 | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XR914700003 | 1991 | 4 | 7.45 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 12/22/2025 | 0
9 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
10 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | R290100014 | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XR290100014 | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
11 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
12 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryLibraryRooftopClassroomInter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
13 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryCenter PodRooftopClassroom 13-20Inter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
14 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryCenter PodRooftopClassroom 13-20Inter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
15 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryCenter PodRooftopClassroom 13-20Inter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
16 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryCenter PodRooftopClassroom 13-20Inter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
17 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryCenter PodRooftopClassroom 13-20Inter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
18 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | Illegible | No ID TagSutherland ElementaryCenter PodRooftopClassroom 13-20Inter-City Products: PGDB048F075IM2XIllegible | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est. Tons, nameplate illegable. | JB, 12/22/2025 | 0
19 | No ID Tag | Sutherland Elementary | Admin/ MPR | Admin Roof | Kindergarden 2 | Gas Package | Inter-City Products | PGDB060F095IM2X | Inter-City Products: PGDB060F095IM2X | R920500002 | No ID TagSutherland ElementaryAdmin/ MPRAdmin RoofKindergarden 2Inter-City Products: PGDB060F095IM2XR920500002 | 1992 | 5 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 12/22/2025 | 0
20 | No ID Tag | Sutherland Elementary | Admin/ MPR | Admin Roof | Kindergarden 1 | Gas Package | Inter-City Products | PGDB060F095IM2X | Inter-City Products: PGDB060F095IM2X | R920500001 | No ID TagSutherland ElementaryAdmin/ MPRAdmin RoofKindergarden 1Inter-City Products: PGDB060F095IM2XR920500001 | 1992 | 5 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 12/22/2025 | 0
21 | No ID Tag | Sutherland Elementary | Admin/ MPR | Stage Roof | Stage | Gas Package | McQuay | Illegible | McQuay: Illegible | XA84011*0* | No ID TagSutherland ElementaryAdmin/ MPRStage RoofStageMcQuay: IllegibleXA84011*0* | 1992 | 10 | 8 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 10 | 17.5 | estimated SEER, nameplate illegable | JB, 12/22/2025 | 0
22 | No ID Tag | Sutherland Elementary | Admin/ MPR | Stage Roof | Gate Classroom | Gas Package | Inter-City Products | PGDB048F075IM2X | Inter-City Products: PGDB048F075IM2X | R920500003 | No ID TagSutherland ElementaryAdmin/ MPRStage RoofGate ClassroomInter-City Products: PGDB048F075IM2XR920500003 | 1992 | 4 | 7.525 | Poor | 480 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 12/22/2025 | 0
| ANNUAL TOTAL | [11 empty] | 92 | [7 empty] | 92
Lodi USD: Wagner-Holt Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units (Base Bid)
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | Main | Ductless Split Heat-Pump | Mitsubishi | Illegible | Mitsubishi: Illegible | - | No ID TagWagner-Holt ElementaryMainRooftopMainMitsubishi: Illegible- | Old | 3 | 12.6 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split Heat-Pump System | Carrier: RAV | 3 | 22.7 | est. size | JB_9-17-2025 | 0031-0032
2 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | MPR | Gas Package | Snyder General | Illegible | Snyder General: Illegible | - | No ID TagWagner-Holt ElementaryMainRooftopMPRSnyder General: Illegible- | 1989 | 10 | 6.57 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 10 | 17.5 | est. size | JB_9-17-2025 | 0034-0038
3 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | D Admin | Gas Package | Snyder General | Illegible | Snyder General: Illegible | - | No ID TagWagner-Holt ElementaryMainRooftopD AdminSnyder General: Illegible- | 1989 | 10 | 6.57 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 10 | 17.5 | est. size | JB_9-17-2025 | 0051-0054
4 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Snyder General | PGBD024G05 | Snyder General: PGBD024G05 | R891900004 | No ID TagWagner-Holt ElementaryLibraryRooftopLibrarySnyder General: PGBD024G05R891900004 | 1989 | 2 | 6.6065 | Poor | 208/230 | 0 | 1 | New High Efficiency Gas Package Unit | Carrier: 48NG | 2 | 15.2 | 0 | JB_9-17-2025 | 0084-0087
5 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Snyder General | PGBD024G05 | Snyder General: PGBD024G05 | Illegible | No ID TagWagner-Holt ElementaryLibraryRooftopLibrarySnyder General: PGBD024G05Illegible | 1989 | 2 | 6.6065 | Poor | 208/230 | 0 | 1 | New High Efficiency Gas Package Unit | Carrier: 48NG | 2 | 15.2 | 0 | JB_9-17-2025 | 0100-0104
| ANNUAL TOTAL | [11 empty] | 27 | [7 empty] | 27

## WE 2.1.1) HVAC McNair 1st
Lodi USD: Additional Bid #1: Ronald McNair High: Replace Selected HVAC Units with High Efficiency HVAC Units: McNair Main Building 1st Floor
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Bldg. | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-AF1 | Ronald McNair High | Main | Rooftop | Rooms A103, AF7 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101417L | AC-AF1Ronald McNair HighMainRooftopRooms A103, AF7Trane: YHC036A4ELA1F02B060000600429101417L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9345-9348
2 | AC-AF2 | Ronald McNair High | Main | Rooftop | Room A104 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101807L | AC-AF2Ronald McNair HighMainRooftopRoom A104Trane: YHC048A4ELA1H02B000000600429101807L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9358-9362
3 | AC-AF3 | Ronald McNair High | Main | Rooftop | Room A105 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102495L | AC-AF3Ronald McNair HighMainRooftopRoom A105Trane: YHC048A4ELA1H02B000000600429102495L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9363-9364
4 | AC-AF4 | Ronald McNair High | Main | Rooftop | Room A106 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | Illegible | AC-AF4Ronald McNair HighMainRooftopRoom A106Trane: YHC048A4ELA1H02B000000600Illegible | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_9371-9374
5 | AC_AF10 | Ronald McNair High | Main | Rooftop | Room A107 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100274L | AC_AF10Ronald McNair HighMainRooftopRoom A107Trane: YHC048A4ELA1H02B000000600430100274L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9378-9380
6 | AC-AM8 | Ronald McNair High | Main | Rooftop | Room AM1 East | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101279L | AC-AM8Ronald McNair HighMainRooftopRoom AM1 EastTrane: YHC036A4ELA1F02B060000600429101279L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9381-9383
7 | AC_AF8 | Ronald McNair High | Main | Rooftop | Room AF1 East | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101277L | AC_AF8Ronald McNair HighMainRooftopRoom AF1 EastTrane: YHC036A4ELA1F02B060000600429101277L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9384-9385
8 | AC-AF7 | Ronald McNair High | Main | Rooftop | Room AF1 West | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101068L | AC-AF7Ronald McNair HighMainRooftopRoom AF1 WestTrane: YHC036A4ELA1F02B060000600429101068L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9386-9388
9 | AC-AM7 | Ronald McNair High | Main | Rooftop | Room AM1 West | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101209L | AC-AM7Ronald McNair HighMainRooftopRoom AM1 WestTrane: YHC036A4ELA1F02B060000600429101209L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9389-9390
10 | AC-AF5 | Ronald McNair High | Main | Rooftop | Room A102 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102429L | AC-AF5Ronald McNair HighMainRooftopRoom A102Trane: YHC048A4ELA1H02B000000600429102429L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9391-9393
11 | AC-AF6 | Ronald McNair High | Main | Rooftop | Room A101 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100272L | AC-AF6Ronald McNair HighMainRooftopRoom A101Trane: YHC048A4ELA1H02B000000600430100272L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9394-9396
12 | AC-AF12 | Ronald McNair High | Main | Rooftop | Atrium A102 | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 429101093L | AC-AF12Ronald McNair HighMainRooftopAtrium A102Trane: YHC092A4ELA1H00B000000600429101093L | 2004 | 7.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9402-9408
13 | AC-AF11 | Ronald McNair High | Main | Rooftop | Room A108 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102157L | AC-AF11Ronald McNair HighMainRooftopRoom A108Trane: YHC048A4ELA1H02B000000600429102157L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9421-9422
14 | No ID Tag | Ronald McNair High | Main | Rooftop | Main | Ductless Split | Fujitsu | AOU12RLFW1. ASU12RLF | Fujitsu: AOU12RLFW1. ASU12RLF | MYN041336 | No ID TagRonald McNair HighMainRooftopMainFujitsu: AOU12RLFW1. ASU12RLFMYN041336 | 2004 | 1 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split System | Carrier: RAV | 1 | 22.7 | 0 | JB_8-27-2025 | IMG_9427-9428
15 | No ID Tag | Ronald McNair High | Main | Rooftop | Main | Ductless Split | EMI | SCC12DM0000AA0A | EMI: SCC12DM0000AA0A | 1-04-G-4846-27 | No ID TagRonald McNair HighMainRooftopMainEMI: SCC12DM0000AA0A1-04-G-4846-27 | 2004 | 1 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split System | Carrier: RAV | 1 | 22.7 | 0 | JB_8-27-2025 | IMG_9429-9430
16 | AC-AG4 | Ronald McNair High | Main | Rooftop | Room A114 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101135L | AC-AG4Ronald McNair HighMainRooftopRoom A114Trane: YHC036A4ELA1F02B060000600429101135L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9431-9433
17 | AC-AG3 | Ronald McNair High | Main | Rooftop | Corridor A105 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102357L | AC-AG3Ronald McNair HighMainRooftopCorridor A105Trane: YHC048A4ELA1H02B000000600429102357L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9438-9440
18 | AC-AG1 | Ronald McNair High | Main | Rooftop | Room A111 | Gas Package | Trane | Illegible | Trane: Illegible | - | AC-AG1Ronald McNair HighMainRooftopRoom A111Trane: Illegible- | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read model & serial | JB_8-27-2025 | IMG_9444-9445
19 | AC-AG2 | Ronald McNair High | Main | Rooftop | Room A112 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102359L | AC-AG2Ronald McNair HighMainRooftopRoom A112Trane: YHC048A4ELA1H02B000000600429102359L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9446-9448
20 | AC-AN6 | Ronald McNair High | Main | Rooftop | Room AN1 North | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101743L | AC-AN6Ronald McNair HighMainRooftopRoom AN1 NorthTrane: YHC036A4ELA1F02B060000600429101743L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9457-9459
21 | AC-AG14 | Ronald McNair High | Main | Rooftop | Atrium A101 East | Gas Package | Trane | YHC102A4EMA1F01B000000600 | Trane: YHC102A4EMA1F01B000000600 | 429101215L | AC-AG14Ronald McNair HighMainRooftopAtrium A101 EastTrane: YHC102A4EMA1F01B000000600429101215L | 2004 | 8.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 8.5 | 17.3 | 0 | JB_8-27-2025 | IMG_9460-9464
22 | AC-AG6 | Ronald McNair High | Main | Rooftop | Room AG1 North | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101416L | AC-AG6Ronald McNair HighMainRooftopRoom AG1 NorthTrane: YHC036A4ELA1F02B060000600429101416L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9469-9471
23 | AC-AG8 | Ronald McNair High | Main | Rooftop | Room A115 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102361L | AC-AG8Ronald McNair HighMainRooftopRoom A115Trane: YHC048A4ELA1H02B000000600429102361L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9472-9475
24 | AC-AG9 | Ronald McNair High | Main | Rooftop | Room A116 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102360L | AC-AG9Ronald McNair HighMainRooftopRoom A116Trane: YHC048A4ELA1H02B000000600429102360L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9476-9478
25 | AC-AG7 | Ronald McNair High | Main | Rooftop | Room A114 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101205L | AC-AG7Ronald McNair HighMainRooftopRoom A114Trane: YHC036A4ELA1F02B060000600429101205L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9479-9481
26 | AC-AN7 | Ronald McNair High | Main | Rooftop | Room AN1 South | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101414L | AC-AN7Ronald McNair HighMainRooftopRoom AN1 SouthTrane: YHC036A4ELA1F02B060000600429101414L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9489-9492
27 | AC-AG12 | Ronald McNair High | Main | Rooftop | Room A117 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102293L | AC-AG12Ronald McNair HighMainRooftopRoom A117Trane: YHC048A4ELA1H02B000000600429102293L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9502-9503
28 | AC-AG11 | Ronald McNair High | Main | Rooftop | Room A118 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102425L | AC-AG11Ronald McNair HighMainRooftopRoom A118Trane: YHC048A4ELA1H02B000000600429102425L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9508-9509
29 | AC-AG10 | Ronald McNair High | Main | Rooftop | Room A119 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100408L | AC-AG10Ronald McNair HighMainRooftopRoom A119Trane: YHC048A4ELA1H02B000000600430100408L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9510-9512
30 | AC-AG13 | Ronald McNair High | Main | Rooftop | Corridor A106 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101061L | AC-AG13Ronald McNair HighMainRooftopCorridor A106Trane: YHC060A4ELA1H00B000000600429101061L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9515-9518
31 | AC-AN13 | Ronald McNair High | Main | Rooftop | Rooms AN12, AN14, Corridor A206 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101203L | AC-AN13Ronald McNair HighMainRooftopRooms AN12, AN14, Corridor A206Trane: YHC060A4ELA1H00B000000600429101203L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9519-9521
32 | AC-AH2 | Ronald McNair High | Main | Rooftop | Room A131 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102428L | AC-AH2Ronald McNair HighMainRooftopRoom A131Trane: YHC048A4ELA1H02B000000600429102428L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9537-9539
33 | AC-AH1 | Ronald McNair High | Main | Rooftop | Room A122 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102221L | AC-AH1Ronald McNair HighMainRooftopRoom A122Trane: YHC048A4ELA1H02B000000600429102221L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9540-9542
34 | AC-AP4 | Ronald McNair High | Main | Rooftop | Room AP1 West | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101275L | AC-AP4Ronald McNair HighMainRooftopRoom AP1 WestTrane: YHC036A4ELA1F02B060000600429101275L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9543-9545
35 | AC-AH4 | Ronald McNair High | Main | Rooftop | Room AH1 West | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101278L | AC-AH4Ronald McNair HighMainRooftopRoom AH1 WestTrane: YHC036A4ELA1F02B060000600429101278L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Est. what it serves. | JB_8-27-2025 | IMG_9546-9547
36 | AC-AH5 | Ronald McNair High | Main | Rooftop | Room AH1 East | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101276L | AC-AH5Ronald McNair HighMainRooftopRoom AH1 EastTrane: YHC036A4ELA1F02B060000600429101276L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9548-9550
37 | AC-AP5 | Ronald McNair High | Main | Rooftop | Room AP1 East | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101415L | AC-AP5Ronald McNair HighMainRooftopRoom AP1 EastTrane: YHC036A4ELA1F02B060000600429101415L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9551-9552
38 | AC-AH7 | Ronald McNair High | Main | Rooftop | Room A126 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101943L | AC-AH7Ronald McNair HighMainRooftopRoom A126Trane: YHC048A4ELA1H02B000000600429101943L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9553-9555
39 | AC-AP7 | Ronald McNair High | Main | Rooftop | Main | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100342L | AC-AP7Ronald McNair HighMainRooftopMainTrane: YHC048A4ELA1H02B000000600430100342L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9556-9557
40 | AC-AH11 | Ronald McNair High | Main | Rooftop | Room A127 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102155L | AC-AH11Ronald McNair HighMainRooftopRoom A127Trane: YHC048A4ELA1H02B000000600429102155L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9558-9560
41 | AC-AH10 | Ronald McNair High | Main | Rooftop | Room A128 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100203L | AC-AH10Ronald McNair HighMainRooftopRoom A128Trane: YHC048A4ELA1H02B000000600430100203L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9567-9568
42 | AC-AH9 | Ronald McNair High | Main | Rooftop | Room A129 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100404L | AC-AH9Ronald McNair HighMainRooftopRoom A129Trane: YHC048A4ELA1H02B000000600430100404L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9569-9572
43 | AC-AE4 | Ronald McNair High | Main | Rooftop | Rooms A133, AE2 | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | Illegible | AC-AE4Ronald McNair HighMainRooftopRooms A133, AE2Trane: YHC072A4EMA1800B000000600Illegible | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | Can't read Serial Number | JB_8-27-2025 | IMG_9584-9587
44 | AC-AL4 | Ronald McNair High | Main | Rooftop | Rooms AL3, AL4 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101207L | AC-AL4Ronald McNair HighMainRooftopRooms AL3, AL4Trane: YHC036A4ELA1F02B060000600429101207L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9596-9599
45 | AC-AE3 | Ronald McNair High | Main | Rooftop | Rooms A132, AE7, AE9 | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | 429101295L | AC-AE3Ronald McNair HighMainRooftopRooms A132, AE7, AE9Trane: YHC072A4EMA1800B000000600429101295L | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | 0 | JB_8-27-2025 | IMG_9607-9610
46 | AC-AE1 | Ronald McNair High | Main | Rooftop | Room A135 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101271L | AC-AE1Ronald McNair HighMainRooftopRoom A135Trane: YHC060A4ELA1H00B000000600429101271L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9611-9613
47 | AC-AE2 | Ronald McNair High | Main | Rooftop | Rooms A134, AE1 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101059L | AC-AE2Ronald McNair HighMainRooftopRooms A134, AE1Trane: YHC060A4ELA1H00B000000600429101059L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9618-9622
48 | AC-AH12 | Ronald McNair High | Main | Rooftop | Corridor A109 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100201L | AC-AH12Ronald McNair HighMainRooftopCorridor A109Trane: YHC048A4ELA1H02B000000600430100201L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9623-9626
49 | AC-AD4 | Ronald McNair High | Main | Rooftop | Room A137 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102156L | AC-AD4Ronald McNair HighMainRooftopRoom A137Trane: YHC048A4ELA1H02B000000600429102156L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9633-9635
50 | AC-AK3 | Ronald McNair High | Main | Rooftop | Rooms AK8, AK9, Corridor A210 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100133L | AC-AK3Ronald McNair HighMainRooftopRooms AK8, AK9, Corridor A210Trane: YHC048A4ELA1H02B000000600430100133L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9636-9638
51 | AC-AD6 | Ronald McNair High | Main | Rooftop | Room A136, Corridor A110 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101129L | AC-AD6Ronald McNair HighMainRooftopRoom A136, Corridor A110Trane: YHC060A4ELA1H00B000000600429101129L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9642-9644
52 | AC-AD1 | Ronald McNair High | Main | Rooftop | Room A141 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102291L | AC-AD1Ronald McNair HighMainRooftopRoom A141Trane: YHC048A4ELA1H02B000000600429102291L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9649-9651
53 | AC-AD7 | Ronald McNair High | Main | Rooftop | Rooms AD3, AD7, AD8, Corridor A111 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | Illegible | AC-AD7Ronald McNair HighMainRooftopRooms AD3, AD7, AD8, Corridor A111Trane: YHC048A4ELA1H02B000000600Illegible | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_9652-9655
54 | SCU-AK1 | Ronald McNair High | Main | Rooftop | Room AK2 | Ductless Split | EMI | SCC18DE0000AA0A | EMI: SCC18DE0000AA0A | 1-04-G-4315-27 | SCU-AK1Ronald McNair HighMainRooftopRoom AK2EMI: SCC18DE0000AA0A1-04-G-4315-27 | 2004 | 1.5 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split System | Carrier: RAV | 1.5 | 22.7 | 0 | JB_8-27-2025 | IMG_9656-9659
55 | AC-AD5 | Ronald McNair High | Main | Rooftop | Rooms AD10, AD11, AD12, AD13, AD14 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101344L | AC-AD5Ronald McNair HighMainRooftopRooms AD10, AD11, AD12, AD13, AD14Trane: YHC036A4ELA1F02B060000600429101344L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9660-9662
56 | AC-AD3 | Ronald McNair High | Main | Rooftop | Room A138 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102189L | AC-AD3Ronald McNair HighMainRooftopRoom A138Trane: YHC048A4ELA1H02B000000600429102189L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Hard to read serial number | JB_8-27-2025 | IMG_9666-9667
57 | AC-AD2 | Ronald McNair High | Main | Rooftop | Room A139 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102427L | AC-AD2Ronald McNair HighMainRooftopRoom A139Trane: YHC048A4ELA1H02B000000600429102427L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9669-9670
58 | AC-AK6 | Ronald McNair High | Main | Rooftop | Rooms AK3, AK4, AK5, Corridor A211 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101097L | AC-AK6Ronald McNair HighMainRooftopRooms AK3, AK4, AK5, Corridor A211Trane: YHC060A4ELA1H00B000000600429101097L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9672-9675
59 | AC-AC5 | Ronald McNair High | Main | Rooftop | Room A142 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102224L | AC-AC5Ronald McNair HighMainRooftopRoom A142Trane: YHC048A4ELA1H02B000000600429102224L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9680-9684
60 | AC-AC6 | Ronald McNair High | Main | Rooftop | Room A143 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100336L | AC-AC6Ronald McNair HighMainRooftopRoom A143Trane: YHC048A4ELA1H02B000000600430100336L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9685-9687
61 | AC-AC7 | Ronald McNair High | Main | Rooftop | Room A144 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100338L | AC-AC7Ronald McNair HighMainRooftopRoom A144Trane: YHC048A4ELA1H02B000000600430100338L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9691-9693
62 | AC-AJ4 | Ronald McNair High | Main | Rooftop | Rooms AJ10, AJ11 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101341L | AC-AJ4Ronald McNair HighMainRooftopRooms AJ10, AJ11Trane: YHC060A4ELA1H00B000000600429101341L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9712-9714
63 | AC-AC4 | Ronald McNair High | Main | Rooftop | Rooms AC10, AC11 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101085L | AC-AC4Ronald McNair HighMainRooftopRooms AC10, AC11Trane: YHC060A4ELA1H00B000000600429101085L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9715-9717
64 | AC-AC3 | Ronald McNair High | Main | Rooftop | Room A145 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101875L | AC-AC3Ronald McNair HighMainRooftopRoom A145Trane: YHC048A4ELA1H02B000000600429101875L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9722-9724
65 | AC-AC2 | Ronald McNair High | Main | Rooftop | Room A146 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100340L | AC-AC2Ronald McNair HighMainRooftopRoom A146Trane: YHC048A4ELA1H02B000000600430100340L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9731-9733
66 | AC-AC1 | Ronald McNair High | Main | Rooftop | Room A147 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101739L | AC-AC1Ronald McNair HighMainRooftopRoom A147Trane: YHC048A4ELA1H02B000000600429101739L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9734-9735
| ANNUAL TOTAL | [11 empty] | 259.5 | [7 empty] | 259.5

## WE 2.1.2) HVAC McNair 2nd
Lodi USD: Additional Bid #2: Ronald McNair High: Replace Selected HVAC Units with High Efficiency HVAC Units: McNair Main Building 2nd Floor
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Bldg. | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-AM1 | Ronald McNair High | Main | Rooftop | Rooms A203, AM7 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101347L | AC-AM1Ronald McNair HighMainRooftopRooms A203, AM7Trane: YHC036A4ELA1F02B060000600429101347L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9349-9352
2 | AC-AM2 | Ronald McNair High | Main | Rooftop | Room A204 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102151L | AC-AM2Ronald McNair HighMainRooftopRoom A204Trane: YHC048A4ELA1H02B000000600429102151L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9353-9357
3 | AC-AM3 | Ronald McNair High | Main | Rooftop | Room A205 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100268L | AC-AM3Ronald McNair HighMainRooftopRoom A205Trane: YHC048A4ELA1H02B000000600430100268L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9365-9366
4 | AC-AM4 | Ronald McNair High | Main | Rooftop | Room A206 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | Illegible | AC-AM4Ronald McNair HighMainRooftopRoom A206Trane: YHC048A4ELA1H02B000000600Illegible | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_9367-9370
5 | AC-AM10 | Ronald McNair High | Main | Rooftop | Room A207 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101603L | AC-AM10Ronald McNair HighMainRooftopRoom A207Trane: YHC048A4ELA1H02B000000600429101603L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9375-9377
6 | AC-AM5 | Ronald McNair High | Main | Rooftop | Room A202 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101335L | AC-AM5Ronald McNair HighMainRooftopRoom A202Trane: YHC048A4ELA1H02B000000600429101335L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9397-9401
7 | AC-AM12 | Ronald McNair High | Main | Rooftop | Atrium A202 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | Illegible | AC-AM12Ronald McNair HighMainRooftopAtrium A202Trane: YHC060A4ELA1H00B000000600Illegible | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_9409-9410
8 | AC-AM6 | Ronald McNair High | Main | Rooftop | Room A201 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101333L | AC-AM6Ronald McNair HighMainRooftopRoom A201Trane: YHC048A4ELA1H02B000000600429101333L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9411-9413
9 | AC-AF9 | Ronald McNair High | Main | Rooftop | Rooms AF2, AF3, AF4 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101069L | AC-AF9Ronald McNair HighMainRooftopRooms AF2, AF3, AF4Trane: YHC036A4ELA1F02B060000600429101069L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9414-9415
10 | AC-AM9 | Ronald McNair High | Main | Rooftop | Rooms AM2, AM3, AM4 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101345L | AC-AM9Ronald McNair HighMainRooftopRooms AM2, AM3, AM4Trane: YHC036A4ELA1F02B060000600429101345L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9416-9420
11 | AC-AM11 | Ronald McNair High | Main | Rooftop | Room A208 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102289L | AC-AM11Ronald McNair HighMainRooftopRoom A208Trane: YHC048A4ELA1H02B000000600429102289L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9423-9425
12 | AC-AN1 | Ronald McNair High | Main | Rooftop | Corridor A205 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101167L | AC-AN1Ronald McNair HighMainRooftopCorridor A205Trane: YHC060A4ELA1H00B000000600429101167L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9435-9437
13 | AC-AN2 | Ronald McNair High | Main | Rooftop | Room A211 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100270L | AC-AN2Ronald McNair HighMainRooftopRoom A211Trane: YHC048A4ELA1H02B000000600430100270L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9441-9443
14 | AC-AN3 | Ronald McNair High | Main | Rooftop | Room A212 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100199L | AC-AN3Ronald McNair HighMainRooftopRoom A212Trane: YHC048A4ELA1H02B000000600430100199L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9449-9450
15 | AC-AN4 | Ronald McNair High | Main | Rooftop | Room A214, AN7 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101349L | AC-AN4Ronald McNair HighMainRooftopRoom A214, AN7Trane: YHC036A4ELA1F02B060000600429101349L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9451-9453
16 | AC-AN8 | Ronald McNair High | Main | Rooftop | Room A215 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100205L | AC-AN8Ronald McNair HighMainRooftopRoom A215Trane: YHC048A4ELA1H02B000000600430100205L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9454-9456
17 | AC-AG5 | Ronald McNair High | Main | Rooftop | Rooms AG2, AG3, AG4 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101136L | AC-AG5Ronald McNair HighMainRooftopRooms AG2, AG3, AG4Trane: YHC036A4ELA1F02B060000600429101136L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9465-9468
18 | AC-AN5 | Ronald McNair High | Main | Rooftop | Rooms AN2, AN3, AN4 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101348L | AC-AN5Ronald McNair HighMainRooftopRooms AN2, AN3, AN4Trane: YHC036A4ELA1F02B060000600429101348L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9482-9484
19 | AC-AN14 | Ronald McNair High | Main | Rooftop | Atrium A201 East | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | 429101365L | AC-AN14Ronald McNair HighMainRooftopAtrium A201 EastTrane: YHC072A4EMA1800B000000600429101365L | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | 0 | JB_8-27-2025 | IMG_9485-9488
20 | AC-AN9 | Ronald McNair High | Main | Rooftop | Room A216 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100063L | AC-AN9Ronald McNair HighMainRooftopRoom A216Trane: YHC048A4ELA1H02B000000600430100063L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9493-9496
21 | AC-AN12 | Ronald McNair High | Main | Rooftop | Room A217 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101123L | AC-AN12Ronald McNair HighMainRooftopRoom A217Trane: YHC048A4ELA1H02B000000600429101123L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9497-9501
22 | AC-AN11 | Ronald McNair High | Main | Rooftop | Room A218 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100131L | AC-AN11Ronald McNair HighMainRooftopRoom A218Trane: YHC048A4ELA1H02B000000600430100131L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9504-9507
23 | AC-AN10 | Ronald McNair High | Main | Rooftop | Room A219 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100061L | AC-AN10Ronald McNair HighMainRooftopRoom A219Trane: YHC048A4ELA1H02B000000600430100061L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9513-9514
24 | AC-AP6 | Ronald McNair High | Main | Rooftop | Room A225 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102225L | AC-AP6Ronald McNair HighMainRooftopRoom A225Trane: YHC048A4ELA1H02B000000600429102225L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9522-9524
25 | AC-AP3 | Ronald McNair High | Main | Rooftop | Rooms AP2, AP3, AP4 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101138L | AC-AP3Ronald McNair HighMainRooftopRooms AP2, AP3, AP4Trane: YHC036A4ELA1F02B060000600429101138L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9525-9527
26 | AC-AH3 | Ronald McNair High | Main | Rooftop | Rooms AH2, AH3, AH4 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101137L | AC-AH3Ronald McNair HighMainRooftopRooms AH2, AH3, AH4Trane: YHC036A4ELA1F02B060000600429101137L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Hard to read serial number | JB_8-27-2025 | IMG_9528-9530
27 | AC-AP1 | Ronald McNair High | Main | Rooftop | Room A222 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101125L | AC-AP1Ronald McNair HighMainRooftopRoom A222Trane: YHC048A4ELA1H02B000000600429101125L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9531-9533
28 | AC-AP2 | Ronald McNair High | Main | Rooftop | Room A231 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101265L | AC-AP2Ronald McNair HighMainRooftopRoom A231Trane: YHC048A4ELA1H02B000000600429101265L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9534-9536
29 | AC-AP11 | Ronald McNair High | Main | Rooftop | Room A227 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101193L | AC-AP11Ronald McNair HighMainRooftopRoom A227Trane: YHC048A4ELA1H02B000000600429101193L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9561-9563
30 | AC-AP10 | Ronald McNair High | Main | Rooftop | Room A228 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101195L | AC-AP10Ronald McNair HighMainRooftopRoom A228Trane: YHC048A4ELA1H02B000000600429101195L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9564-9566
31 | AC-AP9 | Ronald McNair High | Main | Rooftop | Room A229 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101403L | AC-AP9Ronald McNair HighMainRooftopRoom A229Trane: YHC048A4ELA1H02B000000600429101403L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9573-9574
32 | AC-AP8 | Ronald McNair High | Main | Rooftop | Rooms A230, AP7 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101208L | AC-AP8Ronald McNair HighMainRooftopRooms A230, AP7Trane: YHC036A4ELA1F02B060000600429101208L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9575-9577
33 | AC-AL6 | Ronald McNair High | Main | Rooftop | Room A234 | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 429101023L | AC-AL6Ronald McNair HighMainRooftopRoom A234Trane: YHC092A4ELA1H00B000000600429101023L | 2004 | 7.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9588-9590
34 | AC-AL2 | Ronald McNair High | Main | Rooftop | Room A235 | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | 429101017L | AC-AL2Ronald McNair HighMainRooftopRoom A235Trane: YHC072A4EMA1800B000000600429101017L | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | 0 | JB_8-27-2025 | IMG_9591-9595
35 | AC-AL3 | Ronald McNair High | Main | Rooftop | Room A232 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100135L | AC-AL3Ronald McNair HighMainRooftopRoom A232Trane: YHC048A4ELA1H02B000000600430100135L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9600-9602
36 | AC-AL5 | Ronald McNair High | Main | Rooftop | Room A233 | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 429101163L | AC-AL5Ronald McNair HighMainRooftopRoom A233Trane: YHC092A4ELA1H00B000000600429101163L | 2004 | 7.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9603-9606
37 | AC-AL1 | Ronald McNair High | Main | Rooftop | Room A236 | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 429101301L | AC-AL1Ronald McNair HighMainRooftopRoom A236Trane: YHC092A4ELA1H00B000000600429101301L | 2004 | 7.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9614-9617
38 | AC-AK7 | Ronald McNair High | Main | Rooftop | Corridor A209 South | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 430100065L | AC-AK7Ronald McNair HighMainRooftopCorridor A209 SouthTrane: YHC048A4ELA1H02B000000600430100065L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9627-9629
39 | AC-AK5 | Ronald McNair High | Main | Rooftop | Room A238 South | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | 429101157L | AC-AK5Ronald McNair HighMainRooftopRoom A238 SouthTrane: YHC072A4EMA1800B000000600429101157L | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | 0 | JB_8-27-2025 | IMG_9630-9632
40 | AC-AK2 | Ronald McNair High | Main | Rooftop | Room A237 | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | 429101087L | AC-AK2Ronald McNair HighMainRooftopRoom A237Trane: YHC072A4EMA1800B000000600429101087L | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | 0 | JB_8-27-2025 | IMG_9639-9641
41 | AC-AK1 | Ronald McNair High | Main | Rooftop | Room A240 | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | Illegible | AC-AK1Ronald McNair HighMainRooftopRoom A240Trane: YHC072A4EMA1800B000000600Illegible | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | Can't read Serial Number | JB_8-27-2025 | IMG_9646-9648
42 | AC-AK4 | Ronald McNair High | Main | Rooftop | Room A238 North | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429102497L | AC-AK4Ronald McNair HighMainRooftopRoom A238 NorthTrane: YHC048A4ELA1H02B000000600429102497L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9663-9665
43 | AC-AJ5 | Ronald McNair High | Main | Rooftop | Room A241 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101339L | AC-AJ5Ronald McNair HighMainRooftopRoom A241Trane: YHC060A4ELA1H00B000000600429101339L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9677-9679
44 | AC-AJ6 | Ronald McNair High | Main | Rooftop | Room A242 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101273L | AC-AJ6Ronald McNair HighMainRooftopRoom A242Trane: YHC060A4ELA1H00B000000600429101273L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9688-9690
45 | AC-AJ7 | Ronald McNair High | Main | Rooftop | Room A243 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101057L | AC-AJ7Ronald McNair HighMainRooftopRoom A243Trane: YHC048A4ELA1H02B000000600429101057L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9694-9696
46 | AC-AJ9 | Ronald McNair High | Main | Rooftop | Corridor A209 North | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | 429101225L | AC-AJ9Ronald McNair HighMainRooftopCorridor A209 NorthTrane: YHC072A4EMA1800B000000600429101225L | 2004 | 6 | 9.9415 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | 0 | JB_8-27-2025 | IMG_9697-9699
47 | AC-ACB | Ronald McNair High | Main | Rooftop | Room A204 | Gas Package | Trane | YHC120A4ELA1L00B000000600 | Trane: YHC120A4ELA1L00B000000600 | 429101305L | AC-ACBRonald McNair HighMainRooftopRoom A204Trane: YHC120A4ELA1L00B000000600429101305L | 2004 | 10 | 9.773 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 10 | 17.5 | 0 | JB_8-27-2025 | IMG_9706-9710
48 | AC-AJ3 | Ronald McNair High | Main | Rooftop | Room A244 | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101127L | AC-AJ3Ronald McNair HighMainRooftopRoom A244Trane: YHC048A4ELA1H02B000000600429101127L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9718-9721
49 | AC-AJ8 | Ronald McNair High | Main | Rooftop | Room A212 | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101346L | AC-AJ8Ronald McNair HighMainRooftopRoom A212Trane: YHC036A4ELA1F02B060000600429101346L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9725-9727
50 | AC-AJ2 | Ronald McNair High | Main | Rooftop | Room A245 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101199L | AC-AJ2Ronald McNair HighMainRooftopRoom A245Trane: YHC060A4ELA1H00B000000600429101199L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9728-9730
51 | AC-AJ1 | Ronald McNair High | Main | Rooftop | Room A246 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101413L | AC-AJ1Ronald McNair HighMainRooftopRoom A246Trane: YHC060A4ELA1H00B000000600429101413L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9736-9737
| ANNUAL TOTAL | [11 empty] | 228.5 | [7 empty] | 228.5

## WE 2.1.3) HVAC McNair Gym
Lodi USD: Additional Bid #3: Ronald McNair High: Replace Selected HVAC Units with High Efficiency HVAC Units: McNair Gym Units Not Already Included in Base Bid
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Bldg. | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | SCU-C1 | Ronald McNair High | Gym | Lower Roof | Room C27 | Ductless Split | EMI | SCC09DM0000AA0A | EMI: SCC09DM0000AA0A | 1-04-6-4937-34 | SCU-C1Ronald McNair HighGymLower RoofRoom C27EMI: SCC09DM0000AA0A1-04-6-4937-34 | 2004 | 0.75 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split | Carrier: RAV | 0.75 | 22.7 | 0 | JB_8-27-2025 | IMG_9844-9846
2 | AC-C12 | Ronald McNair High | Gym | Lower Roof | Room C19 | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 429101231L | AC-C12Ronald McNair HighGymLower RoofRoom C19Trane: YHC092A4ELA1H00B000000600429101231L | 2004 | 7.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9851-9854
3 | AC-C11 | Ronald McNair High | Gym | Lower Roof | Room C16 | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | Illegible | AC-C11Ronald McNair HighGymLower RoofRoom C16Trane: YHC092A4ELA1H00B000000600Illegible | 2004 | 7.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | Can't read Serial Number | JB_8-27-2025 | IMG_9855-9857
4 | AC-C9 | Ronald McNair High | Gym | Lower Roof | Room C12 | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 429101161L | AC-C9Ronald McNair HighGymLower RoofRoom C12Trane: YHC092A4ELA1H00B000000600429101161L | 2004 | 7.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9858-9860
5 | AC-C10 | Ronald McNair High | Gym | Lower Roof | Room C13, Corridor C15 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101133L | AC-C10Ronald McNair HighGymLower RoofRoom C13, Corridor C15Trane: YHC060A4ELA1H00B000000600429101133L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9861-9863
6 | AC-C8 | Ronald McNair High | Gym | Lower Roof | Room C11 | Gas Package | Trane | YCD151C4L0BA | Trane: YCD151C4L0BA | 430100523D | AC-C8Ronald McNair HighGymLower RoofRoom C11Trane: YCD151C4L0BA430100523D | 2004 | 12.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 12.5 | 16.5 | 0 | JB_8-27-2025 | IMG_9864-9866
7 | AC-C7 | Ronald McNair High | Gym | Lower Roof | Rooms C5, C6, C7, C9, C10 | Gas Package | Trane | YHC102A4EMA1F01B000000600 | Trane: YHC102A4EMA1F01B000000600 | 429101235L | AC-C7Ronald McNair HighGymLower RoofRooms C5, C6, C7, C9, C10Trane: YHC102A4EMA1F01B000000600429101235L | 2004 | 8.5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 8.5 | 17.3 | 0 | JB_8-27-2025 | IMG_9867-9870
8 | AC-C3 | Ronald McNair High | Gym | Locker Rm Roof | Room C39, Corridor C18 South | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 429101139L | AC-C3Ronald McNair HighGymLocker Rm RoofRoom C39, Corridor C18 SouthTrane: YHC036A4ELA1F02B060000600429101139L | 2004 | 3 | 10.5312 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9924-9926
9 | AC-C4 | Ronald McNair High | Gym | Locker Rm Roof | Room C28, Corridor C18 North | Gas Package | Trane | YHC048A4ELA1H02B000000600 | Trane: YHC048A4ELA1H02B000000600 | 429101055L | AC-C4Ronald McNair HighGymLocker Rm RoofRoom C28, Corridor C18 NorthTrane: YHC048A4ELA1H02B000000600429101055L | 2004 | 4 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9927-9929
10 | AC-C5 | Ronald McNair High | Gym | Locker Rm Roof | Rooms C30, C31, C32, C33, C34 | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 429101343L | AC-C5Ronald McNair HighGymLocker Rm RoofRooms C30, C31, C32, C33, C34Trane: YHC060A4ELA1H00B000000600429101343L | 2004 | 5 | 10.11 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9936-9939
| ANNUAL TOTAL | [11 empty] | 61.25 | [7 empty] | 61.25

## WE 2.1.4) HVAC McNair PerfArt
Lodi USD: Additional Bid #4: Ronald McNair High: Replace Selected HVAC Units with High Efficiency HVAC Units: McNair Performing Arts Building Units Not Already Included in Base Bid
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | No ID Tag | Ronald McNair High | Performing Arts | Classrooms Roof | Rm D24 Drama | Gas Package | Trane | YHC120A4ELA1L00B000000600 | Trane: YHC120A4ELA1L00B000000600 | 513100770L | No ID TagRonald McNair HighPerforming ArtsClassrooms RoofRm D24 DramaTrane: YHC120A4ELA1L00B000000600513100770L | 2005 | 10 | 9.86 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 10 | 17.5 | 0 | JB_8-27-2025 | IMG_9942-9946
2 | No ID Tag | Ronald McNair High | Performing Arts | Classrooms Roof | Rm D16 Band | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 513100482L | No ID TagRonald McNair HighPerforming ArtsClassrooms RoofRm D16 BandTrane: YHC092A4ELA1H00B000000600513100482L | 2005 | 7.5 | 10.2 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9947-9951
3 | SCU-D3 | Ronald McNair High | Performing Arts | Classrooms Roof | Rm D35 Lighting | Ductless Split | EMI | SHC18DF0000AA0B | EMI: SHC18DF0000AA0B | Illegible | SCU-D3Ronald McNair HighPerforming ArtsClassrooms RoofRm D35 LightingEMI: SHC18DF0000AA0BIllegible | 2005 | 1.5 | 11.05 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split | Carrier: RAV | 1.5 | 22.7 | Can't read Serial Number | JB_8-27-2025 | IMG_9953-9955
4 | SCU-D1 | Ronald McNair High | Performing Arts | Classrooms Roof | Rm D12 Data | Ductless Split | EMI | SHC18DF0000AA0B | EMI: SHC18DF0000AA0B | Illegible | SCU-D1Ronald McNair HighPerforming ArtsClassrooms RoofRm D12 DataEMI: SHC18DF0000AA0BIllegible | 2005 | 1.5 | 11.05 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split | Carrier: RAV | 1.5 | 22.7 | Can't read Name Plate, Size est | JB_8-27-2025 | IMG_9956-9957
5 | No ID Tag | Ronald McNair High | Performing Arts | Classrooms Roof | Rm D4 Office | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 513100726L | No ID TagRonald McNair HighPerforming ArtsClassrooms RoofRm D4 OfficeTrane: YHC036A4ELA1F02B060000600513100726L | 2005 | 3 | 10.625 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9958-9961
6 | No ID Tag | Ronald McNair High | Performing Arts | Classrooms Roof | Rm D2 Keyboard | Gas Package | Trane | YHC072A4EMA1800B000000600 | Trane: YHC072A4EMA1800B000000600 | Illegible | No ID TagRonald McNair HighPerforming ArtsClassrooms RoofRm D2 KeyboardTrane: YHC072A4EMA1800B000000600Illegible | 2005 | 6 | 10.03 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | Can't read Serial Number | JB_8-27-2025 | IMG_9962-9964
7 | SCU-D2 | Ronald McNair High | Performing Arts | Stage Roof | Rm D39 Control Rm | Ductless Split Heat-Pump | Carrier | 38QR024C-331, 38QAQ024 | Carrier: 38QR024C-331, 38QAQ024 | Illegible | SCU-D2Ronald McNair HighPerforming ArtsStage RoofRm D39 Control RmCarrier: 38QR024C-331, 38QAQ024Illegible | 2005 | 2 | 11.05 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split Heat-Pump | Carrier: RAV | 2 | 22.7 | Can't read Name Plate, Size est | JB_8-27-2025 | IMG_9979-9981
8 | No ID Tag | Ronald McNair High | Performing Arts | Stage Roof | Performing Arts | Gas Package | Trane | YHC060A4ELA1L00C000000600 | Trane: YHC060A4ELA1L00C000000600 | 513100580L | No ID TagRonald McNair HighPerforming ArtsStage RoofPerforming ArtsTrane: YHC060A4ELA1L00C000000600513100580L | 2005 | 5 | 10.2 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9990-9993
| ANNUAL TOTAL | [11 empty] | 36.5 | [7 empty] | 36.5

## WE 2.1.5) HVAC McNair MPR
Lodi USD: Additional Bid #5: Ronald McNair High: Replace Selected HVAC Units with High Efficiency HVAC Units: McNair Cafeteria/MPR Building
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | SCU-B1 | Ronald McNair High | Cafeteria | Lower Roof | Rm B11 Custodian | Ductless Split Heat-Pump | Carrier | 38QR024C-331, 38QAQ024 | Carrier: 38QR024C-331, 38QAQ024 | 3604X94504 | SCU-B1Ronald McNair HighCafeteriaLower RoofRm B11 CustodianCarrier: 38QR024C-331, 38QAQ0243604X94504 | 2004 | 2 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split Heat-Pump | Carrier: RAV | 2 | 22.7 | 0 | JB_8-27-2025 | IMG_9798-9800
2 | SCU-B2 | Ronald McNair High | Cafeteria | Lower Roof | Rm B2 Data | Ductless Split Heat-Pump | EMI | Illegible | EMI: Illegible | Illegible | SCU-B2Ronald McNair HighCafeteriaLower RoofRm B2 DataEMI: IllegibleIllegible | 2004 | 2 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Ductless Split Heat-Pump | Carrier: RAV | 2 | 22.7 | Can't Read Nameplate, Est. 2 ton | JB_8-27-2025 | IMG_9801-9803
3 | AC-B6 | Ronald McNair High | Cafeteria | Lower Roof | Rm B6 Food Court | Gas Package | Trane | YHC120A4ELA1L00B000000600 | Trane: YHC120A4ELA1L00B000000600 | Illegible | AC-B6Ronald McNair HighCafeteriaLower RoofRm B6 Food CourtTrane: YHC120A4ELA1L00B000000600Illegible | Old | 10 | 9.773 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 10 | 17.5 | Can't read Serial Number | JB_8-27-2025 | IMG_9804-9808
4 | AC-B5 | Ronald McNair High | Cafeteria | Lower Roof | Rm B7 Prep Kitchen | Gas Package | Trane | YHC092A4ELA1H00B000000600 | Trane: YHC092A4ELA1H00B000000600 | 513100554L | AC-B5Ronald McNair HighCafeteriaLower RoofRm B7 Prep KitchenTrane: YHC092A4ELA1H00B000000600513100554L | 2005 | 7.5 | 10.2 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9815-9818
5 | AC-B2 | Ronald McNair High | Cafeteria | Lower Roof | Rm B7 Prep Kitchen | Gas Package | Trane | YHC060A4ELA1H00B000000600 | Trane: YHC060A4ELA1H00B000000600 | 513100508L | AC-B2Ronald McNair HighCafeteriaLower RoofRm B7 Prep KitchenTrane: YHC060A4ELA1H00B000000600513100508L | 2005 | 5 | 10.2 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9820-9821
6 | AC-B1 | Ronald McNair High | Cafeteria | Lower Roof | Rm B14 Locker | Gas Package | Trane | YHC036A4ELA1F02B060000600 | Trane: YHC036A4ELA1F02B060000600 | 513100954L | AC-B1Ronald McNair HighCafeteriaLower RoofRm B14 LockerTrane: YHC036A4ELA1F02B060000600513100954L | 2005 | 3 | 10.625 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9822-9825
7 | AC-B3 | Ronald McNair High | Cafeteria | Upper Roof | Rm B17 Multipurpose | Gas Package | Trane | YCD211C4LBCA | Trane: YCD211C4LBCA | 503100444D | AC-B3Ronald McNair HighCafeteriaUpper RoofRm B17 MultipurposeTrane: YCD211C4LBCA503100444D | 2005 | 17.5 | 9.35 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 17.5 | 16.3 | 0 | JB_8-27-2025 | IMG_9829-9833
8 | AC-B4 | Ronald McNair High | Cafeteria | Upper Roof | Rm B17 Multipurpose | Gas Package | Trane | YCD211C4LBCA | Trane: YCD211C4LBCA | 503100411D | AC-B4Ronald McNair HighCafeteriaUpper RoofRm B17 MultipurposeTrane: YCD211C4LBCA503100411D | 2005 | 17.5 | 9.35 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 17.5 | 16.3 | 0 | JB_8-27-2025 | IMG_9836-9841
| ANNUAL TOTAL | [11 empty] | 64.5 | [7 empty] | 64.5

## WE 2.1.6) HVAC McNair Culinary
Lodi USD: Additional Bid #6: Ronald McNair High: Replace Selected HVAC Units with High Efficiency HVAC Units: McNair Culinary Arts Building
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-E5 | Ronald McNair High | Culinary Arts | Rooftop | Rm E5 Food Serve Tech | Gas Package | Trane | YHC092A4ELA1L00C | Trane: YHC092A4ELA1L00C | 453100529L | AC-E5Ronald McNair HighCulinary ArtsRooftopRm E5 Food Serve TechTrane: YHC092A4ELA1L00C453100529L | 2004 | 7.5 | 10.11 | Fair | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_0002-0006
2 | AC-E6 | Ronald McNair High | Culinary Arts | Rooftop | Rm E17 Hospitality | Gas Package | Trane | YHC120A4ELA1L00B | Trane: YHC120A4ELA1L00B | Illegible | AC-E6Ronald McNair HighCulinary ArtsRooftopRm E17 HospitalityTrane: YHC120A4ELA1L00BIllegible | 2005 | 10 | 9.86 | Fair | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 10 | 17.5 | Can't read Serial Number | JB_8-27-2025 | IMG_0007-0010
3 | SCU-E1 | Ronald McNair High | Culinary Arts | Rooftop | Rm E12 Data Room | Ductless Split | EMI | SCC09DM0000AA0B | EMI: SCC09DM0000AA0B | 1-05-A-7548-02 | SCU-E1Ronald McNair HighCulinary ArtsRooftopRm E12 Data RoomEMI: SCC09DM0000AA0B1-05-A-7548-02 | 2005 | 0.75 | 11.05 | Good | 208/230 | 0 | 1 | New High Efficiency Ductless Split | Carrier: RAV | 0.75 | 22.7 | 0 | JB_8-27-2025 | IMG_0015-0017
| ANNUAL TOTAL | [11 empty] | 18.25 | [7 empty] | 18.25

## WE 2.1.7) HVAC Mosher 1st
Lodi USD: Additional Bid #7: GL Mosher Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units: Mosher Elementary 1st Floor
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Bldg. | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-28 | GL Mosher Elementary | Main | Rooftop | Rm 121 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102648L | AC-28GL Mosher ElementaryMainRooftopRm 121Trane: YHC043A4RMA0Y00C100000600620102648L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9155-9157
2 | AC-27 | GL Mosher Elementary | Main | Rooftop | Rm 123 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102504L | AC-27GL Mosher ElementaryMainRooftopRm 123Trane: YHC033A4RMA0W00C1620102504L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9161-9163
3 | AC-24 | GL Mosher Elementary | Main | Rooftop | Rm 125 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102300L | AC-24GL Mosher ElementaryMainRooftopRm 125Trane: YHC043A4RMA0Y00C100000600620102300L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9171-9173
4 | AC-23 | GL Mosher Elementary | Main | Rooftop | Rm 127 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102298L | AC-23GL Mosher ElementaryMainRooftopRm 127Trane: YHC043A4RMA0Y00C100000600620102298L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9174-9176
5 | AC-20 | GL Mosher Elementary | Main | Rooftop | Rm 132 | Gas Package | Trane | YHC063A4RMA0W00C1000006B0 | Trane: YHC063A4RMA0W00C1000006B0 | 620102636L | AC-20GL Mosher ElementaryMainRooftopRm 132Trane: YHC063A4RMA0W00C1000006B0620102636L | 2006 | 5 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9183-9185
6 | AC-19 | GL Mosher Elementary | Main | Rooftop | Rm 136 | Gas Package | Trane | YHC063A4RMA0W00C1000006B0 | Trane: YHC063A4RMA0W00C1000006B0 | 620102566L | AC-19GL Mosher ElementaryMainRooftopRm 136Trane: YHC063A4RMA0W00C1000006B0620102566L | 2006 | 5 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9186-9188
7 | AC-17 | GL Mosher Elementary | Main | Rooftop | Rm 101 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102570L | AC-17GL Mosher ElementaryMainRooftopRm 101Trane: YHC033A4RMA0W00C1620102570L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9193-9197
8 | AC-37 | GL Mosher Elementary | Main | Rooftop | Rm 120 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620***572L | AC-37GL Mosher ElementaryMainRooftopRm 120Trane: YHC033A4RMA0W00C1620***572L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9201-9204
9 | No ID Tag | GL Mosher Elementary | Main | Rooftop | Classroom | Package Cooling | Trane | 4TCC3018A1000AA | Trane: 4TCC3018A1000AA | 6211KRA9H | No ID TagGL Mosher ElementaryMainRooftopClassroomTrane: 4TCC3018A1000AA6211KRA9H | 2006 | 2.5 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Package Cooling Unit | Carrier: 48GE | 2.5 | 17.2 | 0 | JB_8-27-2025 | IMG_9205-9207
10 | AC-32 | GL Mosher Elementary | Main | Rooftop | Rm 146 | Gas Package | Trane | YHC063A4RMA0W00C1000006B0 | Trane: YHC063A4RMA0W00C1000006B0 | 620102508L | AC-32GL Mosher ElementaryMainRooftopRm 146Trane: YHC063A4RMA0W00C1000006B0620102508L | 2006 | 5 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_9208-9210, 9223-9225
11 | AC-39 | GL Mosher Elementary | Main | Rooftop | Rm 149 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102638L | AC-39GL Mosher ElementaryMainRooftopRm 149Trane: YHC033A4RMA0W00C1620102638L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9226-9229
12 | AC-13 | GL Mosher Elementary | Main | Rooftop | Rm 102 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102336L | AC-13GL Mosher ElementaryMainRooftopRm 102Trane: YHC033A4RMA0W00C1620102336L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Hard to read | JB_8-27-2025 | IMG_9244-9248
13 | AC-11 | GL Mosher Elementary | Main | Rooftop | Rm 103 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102646L | AC-11GL Mosher ElementaryMainRooftopRm 103Trane: YHC043A4RMA0Y00C100000600620102646L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9253-9255
14 | AC-10 | GL Mosher Elementary | Main | Rooftop | Rm 104 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102290L | AC-10GL Mosher ElementaryMainRooftopRm 104Trane: YHC033A4RMA0W00C1620102290L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9256-9259
15 | AC-7 | GL Mosher Elementary | Main | Rooftop | Rm 105 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102360L | AC-7GL Mosher ElementaryMainRooftopRm 105Trane: YHC033A4RMA0W00C1620102360L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9268-9270
16 | No ID Tag | GL Mosher Elementary | Main | Rooftop | Classroom | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102542L | No ID TagGL Mosher ElementaryMainRooftopClassroomTrane: YHC033A4RMA0W00C1620102542L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9271-9273
17 | AC-33 | GL Mosher Elementary | Main | Rooftop | Rm 151 | Package Cooling | Trane | 4TCC3018A1000AA | Trane: 4TCC3018A1000AA | 621309P9H | AC-33GL Mosher ElementaryMainRooftopRm 151Trane: 4TCC3018A1000AA621309P9H | 2006 | 2.5 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Package Cooling Unit | Carrier: 48GE | 2.5 | 17.2 | 0 | JB_8-27-2025 | IMG_9274-9277
18 | AC-6 | GL Mosher Elementary | Main | Rooftop | Rm 106 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102498L | AC-6GL Mosher ElementaryMainRooftopRm 106Trane: YHC033A4RMA0W00C1620102498L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9278-9280
19 | AC-3 | GL Mosher Elementary | Main | Rooftop | Rm 107 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102294L | AC-3GL Mosher ElementaryMainRooftopRm 107Trane: YHC033A4RMA0W00C1620102294L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9290-9293
20 | AC-2 | GL Mosher Elementary | Main | Rooftop | Rm 108 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102368L | AC-2GL Mosher ElementaryMainRooftopRm 108Trane: YHC043A4RMA0Y00C100000600620102368L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9294-9297
21 | AC-34 | GL Mosher Elementary | Main | Rooftop | Rm 153 | Gas Package | Trane | YFD211C4LHCA | Trane: YFD211C4LHCA | 620101132D | AC-34GL Mosher ElementaryMainRooftopRm 153Trane: YFD211C4LHCA620101132D | 2006 | 17.5 | 9.1467 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 17.5 | 16.3 | 0 | JB_8-27-2025 | IMG_9304-9309
22 | AC-40 | GL Mosher Elementary | Main | Rooftop | Rm 114 | Gas Package | AAON | RM-015-3-0-AA02-362 | AAON: RM-015-3-0-AA02-362 | 200606-AMGL25912 | AC-40GL Mosher ElementaryMainRooftopRm 114AAON: RM-015-3-0-AA02-362200606-AMGL25912 | 2006 | 15 | 10 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 15 | 16.5 | 0 | JB_8-27-2025 | IMG_9320-9324
| ANNUAL TOTAL | [11 empty] | 102.5 | [7 empty] | 102.5

## WE 2.1.8) HVAC Mosher 2nd
Lodi USD: Additional Bid #8: GL Mosher Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units: Mosher Elementary 2nd Floor
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-41 | GL Mosher Elementary | Main | Rooftop | Rm 209 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102574L | AC-41GL Mosher ElementaryMainRooftopRm 209Trane: YHC033A4RMA0W00C1620102574L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9144-9150
2 | AC-38 | GL Mosher Elementary | Main | Rooftop | Rm 224 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102568L | AC-38GL Mosher ElementaryMainRooftopRm 224Trane: YHC033A4RMA0W00C1620102568L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9151-9153
3 | AC-29 | GL Mosher Elementary | Main | Rooftop | Rm 213 | Gas Package | Trane | YHC043A4RMA0Y00C1 | Trane: YHC043A4RMA0Y00C1 | No Nameplate | AC-29GL Mosher ElementaryMainRooftopRm 213Trane: YHC043A4RMA0Y00C1No Nameplate | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Est Model Number | JB_8-27-2025 | IMG_9158-9160
4 | AC-26 | GL Mosher Elementary | Main | Rooftop | Rm 214 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102644L | AC-26GL Mosher ElementaryMainRooftopRm 214Trane: YHC033A4RMA0W00C1620102644L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9164-9166
5 | AC-25 | GL Mosher Elementary | Main | Rooftop | Rm 215 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102500L | AC-25GL Mosher ElementaryMainRooftopRm 215Trane: YHC033A4RMA0W00C1620102500L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9167-9170
6 | AC-22 | GL Mosher Elementary | Main | Rooftop | Rm 216 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102434L | AC-22GL Mosher ElementaryMainRooftopRm 216Trane: YHC033A4RMA0W00C1620102434L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9177-9179
7 | AC-21 | GL Mosher Elementary | Main | Rooftop | Rm 217 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102362L | AC-21GL Mosher ElementaryMainRooftopRm 217Trane: YHC033A4RMA0W00C1620102362L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9180-9182
8 | AC-18 | GL Mosher Elementary | Main | Rooftop | Rm 218 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102370L | AC-18GL Mosher ElementaryMainRooftopRm 218Trane: YHC043A4RMA0Y00C100000600620102370L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9189-9192
9 | AC-30 | GL Mosher Elementary | Main | Rooftop | Rm 228 | Gas Package | Trane | 2YCC3024A1040AA | Trane: 2YCC3024A1040AA | 6191LA89H | AC-30GL Mosher ElementaryMainRooftopRm 228Trane: 2YCC3024A1040AA6191LA89H | 2006 | 2.5 | 11.1475 | Poor | 208/230 | 0 | 1 | New High Efficiency Gas Package Unit | Carrier: 48GE | 2.5 | 17.2 | 0 | JB_8-27-2025 | IMG_9198-9200
10 | AC-16 | GL Mosher Elementary | Main | Rooftop | Rm 219 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102364L | AC-16GL Mosher ElementaryMainRooftopRm 219Trane: YHC033A4RMA0W00C1620102364L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9211-9213
11 | AC-15 | GL Mosher Elementary | Main | Rooftop | Rm 220 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102502L | AC-15GL Mosher ElementaryMainRooftopRm 220Trane: YHC033A4RMA0W00C1620102502L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9214-9217
12 | AC-36 | GL Mosher Elementary | Main | Rooftop | Rm 222 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102576L | AC-36GL Mosher ElementaryMainRooftopRm 222Trane: YHC043A4RMA0Y00C100000600620102576L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9218-9222, 9234-9236
13 | AC-31 | GL Mosher Elementary | Main | Rooftop | Rm 229 | Gas Package | Trane | YSC092A4RLA2D00C10000A600 | Trane: YSC092A4RLA2D00C10000A600 | 620102286L | AC-31GL Mosher ElementaryMainRooftopRm 229Trane: YSC092A4RLA2D00C10000A600620102286L | 2006 | 7.5 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.5 | 0 | JB_8-27-2025 | IMG_9230-9233
14 | AC-15 | GL Mosher Elementary | Main | Rooftop | Rm 220 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102302L | AC-15GL Mosher ElementaryMainRooftopRm 220Trane: YHC033A4RMA0W00C1620102302L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Hard to read | JB_8-27-2025 | IMG_9237-9238
15 | AC-14 | GL Mosher Elementary | Main | Rooftop | Rm 221 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102430L | AC-14GL Mosher ElementaryMainRooftopRm 221Trane: YHC033A4RMA0W00C1620102430L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9239-9243
16 | AC-12 | GL Mosher Elementary | Main | Rooftop | Rm 201 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102578L | AC-12GL Mosher ElementaryMainRooftopRm 201Trane: YHC043A4RMA0Y00C100000600620102578L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9249-9252
17 | AC-9 | GL Mosher Elementary | Main | Rooftop | Rm 202 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102296L | AC-9GL Mosher ElementaryMainRooftopRm 202Trane: YHC033A4RMA0W00C1620102296L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9260-9263
18 | AC-8 | GL Mosher Elementary | Main | Rooftop | Rm 203 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102640L | AC-8GL Mosher ElementaryMainRooftopRm 203Trane: YHC033A4RMA0W00C1620102640L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9264-9267
19 | AC-5 | GL Mosher Elementary | Main | Rooftop | Rm 204 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102292L | AC-5GL Mosher ElementaryMainRooftopRm 204Trane: YHC033A4RMA0W00C1620102292L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9281-9285
20 | AC-4 | GL Mosher Elementary | Main | Rooftop | Rm 206 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 620102432L | AC-4GL Mosher ElementaryMainRooftopRm 206Trane: YHC033A4RMA0W00C1620102432L | 2006 | 3 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_9286-9289
21 | AC-1 | GL Mosher Elementary | Main | Rooftop | Rm 206 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 620102438L | AC-1GL Mosher ElementaryMainRooftopRm 206Trane: YHC043A4RMA0Y00C100000600620102438L | 2006 | 4 | 11.1475 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_9298-9302
| ANNUAL TOTAL | [11 empty] | 72 | [7 empty] | 72

## WE 2.1.9) HVAC Silva
Lodi USD: Additional Bid #9: Manlio Silva Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units: Manlio Silva Elementary
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-29 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | Illegible | AC-29Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00BIllegible | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0043-0045
2 | AC-28 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | Illegible | AC-28Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00BIllegible | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0046-0048
3 | AC-27 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | Illegible | AC-27Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00BIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0049-0050
4 | AC-26 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | Illegible | AC-26Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00BIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0051-0054
5 | AC-25 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | Illegible | AC-25Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00BIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0055-0056
6 | AC-24 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | Illegible | AC-24Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00BIllegible | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0057-0058
7 | AC-23 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | 453100188L | AC-23Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00B453100188L | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_0064-0066
8 | AC-22 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | Illegible | AC-22Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00BIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0067-0069
9 | AC-21 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | Illegible | AC-21Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00BIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0070-0072
10 | AC-20 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC060A4EMA1 | Trane: YHC060A4EMA1 | Illegible | AC-20Manlio Silva ElementaryMainRooftopInteriorTrane: YHC060A4EMA1Illegible | 2004 | 5 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0073-0075
11 | AC-19 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC060A4EMA1 | Trane: YHC060A4EMA1 | Illegible | AC-19Manlio Silva ElementaryMainRooftopInteriorTrane: YHC060A4EMA1Illegible | 2004 | 5 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0076-0078
12 | AC-18 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | Illegible | AC-18Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00BIllegible | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0079-0081
13 | AC-17 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | Illegible | AC-17Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00BIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0082-0084
14 | AC-30 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 453100282L | AC-30Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B453100282L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0087-0089
15 | AC-37 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA052V | Trane: YHC036A4EMA052V | 452100430L | AC-37Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA052V452100430L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0091-0094
16 | AC-42 | Manlio Silva Elementary | Main | Rooftop | Interior | Package Cooling | Trane | TCC018F100BG | Trane: TCC018F100BG | 40612372H | AC-42Manlio Silva ElementaryMainRooftopInteriorTrane: TCC018F100BG40612372H | 2004 | 1.5 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Package Cooling Unit | Carrier: 48GE | 1.5 | 17.2 | 0 | JB_8-27-2025 | IMG_0097-0099
17 | AC-32 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC060A4EMA1 | Trane: YHC060A4EMA1 | 502100746L | AC-32Manlio Silva ElementaryMainRooftopInteriorTrane: YHC060A4EMA1502100746L | 2005 | 5 | 11.05 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB_8-27-2025 | IMG_0100-0102
18 | AC-16 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA052V | Trane: YHC036A4EMA052V | 452100482L | AC-16Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA052V452100482L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0104-0108
19 | AC-15 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA052V | Trane: YHC036A4EMA052V | 452100478L | AC-15Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA052V452100478L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0109-0112
20 | AC-36 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | 452100964L | AC-36Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00B452100964L | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_0113-0115
21 | AC-44 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA052V | Trane: YHC048A4EMA052V | 452100840L | AC-44Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA052V452100840L | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_0120-0123
22 | AC-39 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA052V | Trane: YHC036A4EMA052V | Illegible | AC-39Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA052VIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0124-0126
23 | AC-14 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA0BDE | Trane: YHC036A4EMA0BDE | 436101148L | AC-14Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA0BDE436101148L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0129-0133
24 | AC-13 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA052V | Trane: YHC036A4EMA052V | 502100575L | AC-13Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA052V502100575L | 2005 | 3 | 11.05 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.5 | 0 | JB_8-27-2025 | IMG_0134-0137
25 | AC-33 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100580L | AC-33Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100580L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0138-0140
26 | AC-43 | Manlio Silva Elementary | Main | Rooftop | Interior | Package Cooling | Trane | TCC018F100BG | Trane: TCC018F100BG | 406245X2H | AC-43Manlio Silva ElementaryMainRooftopInteriorTrane: TCC018F100BG406245X2H | 2004 | 1.5 | 10.9525 | Poor | 208/230 | 0 | 1 | New High Efficiency Package Cooling Unit | Carrier: 48GE | 1.5 | 17.2 | 0 | JB_8-27-2025 | IMG_0142-0144
27 | AC-35 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100620L | AC-35Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100620L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0145-0147
28 | AC-12 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | 502100279L | AC-12Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00B502100279L | 2005 | 4 | 11.05 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_0151-0154
29 | AC-11 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | 453100140L | AC-11Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00B453100140L | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_0155-0157
30 | AC-10 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1L00B | Trane: YHC036A4EMA1L00B | 503100281L | AC-10Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1L00B503100281L | 2005 | 3 | 11.05 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0158-0161
31 | AC-9 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100528L | AC-9Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100528L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0162-0163
32 | AC-8 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100578L | AC-8Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100578L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0164-0166
33 | AC-7 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100582L | AC-7Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100582L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0167-0169
34 | AC-6 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100631L | AC-6Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100631L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0170-0173
35 | AC-5 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100677L | AC-5Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100677L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0174-0176
36 | AC-4 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100675L | AC-4Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100675L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0177-0179
37 | AC-3 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 452100627L | AC-3Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B452100627L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0180-0182
38 | AC-2 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | 453100284L | AC-2Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00B453100284L | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_0183-0185
39 | AC-1 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC048A4EMA1L00B | Trane: YHC048A4EMA1L00B | 453100236L | AC-1Manlio Silva ElementaryMainRooftopInteriorTrane: YHC048A4EMA1L00B453100236L | 2004 | 4 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB_8-27-2025 | IMG_0186-0187
40 | AC-34 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YCD211C4LOCA | Trane: YCD211C4LOCA | 452100563D | AC-34Manlio Silva ElementaryMainRooftopInteriorTrane: YCD211C4LOCA452100563D | 2004 | 17.5 | 8.9867 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 17.5 | 16.3 | 0 | JB_8-27-2025 | IMG_0192-0197
41 | AC-38 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | Illegible | AC-38Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00BIllegible | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | Can't read Serial Number | JB_8-27-2025 | IMG_0200-0203
42 | AC-41 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Trane | YHC036A4EMA1K00B | Trane: YHC036A4EMA1K00B | 453100042L | AC-41Manlio Silva ElementaryMainRooftopInteriorTrane: YHC036A4EMA1K00B453100042L | 2004 | 3 | 10.9525 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB_8-27-2025 | IMG_0204-0206
43 | AC-40 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | AAON | No Nameplate | AAON: No Nameplate | est size | AC-40Manlio Silva ElementaryMainRooftopInteriorAAON: No Nameplateest size | - | 15 | 10 | Poor | 460 | 0 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 15 | 16.5 | est. HP | JB_8-27-2025 | IMG_0207-0212
| ANNUAL TOTAL | [11 empty] | 169.5 | [7 empty] | 169.5

## WE 2.1.10) HVAC Podesta
Lodi USD: Additional Bid #10: Podesta Ranch Elementary: Replace Selected HVAC Units with High Efficiency HVAC Units: Podesta Ranch Elementary
| General Information |  |  |  |  | Existing Equipment Data | [9 empty] | Electrical |  |  | Proposed Equipment Data
| ID Tag | Site | Bldg. | Unit Location | Serves | System Type | Make | Model | Make: Model | Serial # | UD | Mfg. Year | Size Tons (pre) | SEER (pre) | Unit Condition | Volts | Amps | PH | Proposed System Type | Savings Based on - Make: Model | Size Tons (post) | SEER (post) | Notes | Initials, Date Noted | Photo
1 | AC-1 | Podesta Ranch Elementary | Main | Rooftop | Main | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20019 | AC-1Podesta Ranch ElementaryMainRooftopMainCarrier: 48PGDM061008G20019 | 2008 | 5 | 11.3425 | Good | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0767-0769
2 | AC-2 | Podesta Ranch Elementary | Main | Rooftop | R-107 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20024 | AC-2Podesta Ranch ElementaryMainRooftopR-107Carrier: 48PGDM061008G20024 | 2008 | 5 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0770-0773
3 | AC-3 | Podesta Ranch Elementary | Main | Rooftop | R-106 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30008 | AC-3Podesta Ranch ElementaryMainRooftopR-106Carrier: 48PGDM051008G30008 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0775-0776
4 | AC-4 | Podesta Ranch Elementary | Main | Rooftop | R-206 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30016 | AC-4Podesta Ranch ElementaryMainRooftopR-206Carrier: 48PGDM051008G30016 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0777-0779
5 | AC-5 | Podesta Ranch Elementary | Main | Rooftop | R-205 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G300XX | AC-5Podesta Ranch ElementaryMainRooftopR-205Carrier: 48PGDM051008G300XX | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0780-0782
6 | AC-6 | Podesta Ranch Elementary | Main | Rooftop | R-105 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G300XX | AC-6Podesta Ranch ElementaryMainRooftopR-105Carrier: 48PGDM051008G300XX | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0783-0785
7 | AC-7 | Podesta Ranch Elementary | Main | Rooftop | R-104 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30010 | AC-7Podesta Ranch ElementaryMainRooftopR-104Carrier: 48PGDM051008G30010 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0786-0788
8 | AC-8 | Podesta Ranch Elementary | Main | Rooftop | R-204 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30011 | AC-8Podesta Ranch ElementaryMainRooftopR-204Carrier: 48PGDM051008G30011 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0789-0791
9 | AC-9 | Podesta Ranch Elementary | Main | Rooftop | R-203 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30033 | AC-9Podesta Ranch ElementaryMainRooftopR-203Carrier: 48PGDM051008G30033 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0792-0794
10 | AC-10 | Podesta Ranch Elementary | Main | Rooftop | R-103 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30012 | AC-10Podesta Ranch ElementaryMainRooftopR-103Carrier: 48PGDM051008G30012 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0795-0797
11 | AC-11 | Podesta Ranch Elementary | Main | Rooftop | R-102 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20022 | AC-11Podesta Ranch ElementaryMainRooftopR-102Carrier: 48PGDM061008G20022 | 2008 | 5 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0798-0800
12 | AC-12 | Podesta Ranch Elementary | Main | Rooftop | R-202 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20023 | AC-12Podesta Ranch ElementaryMainRooftopR-202Carrier: 48PGDM061008G20023 | 2008 | 5 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0801-0805
13 | AC-13 | Podesta Ranch Elementary | Main | Rooftop | R-101 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G20035 | AC-13Podesta Ranch ElementaryMainRooftopR-101Carrier: 48PGDM051008G20035 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0806-0808
14 | AC-14 | Podesta Ranch Elementary | Main | Rooftop | R-201 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G200XX | AC-14Podesta Ranch ElementaryMainRooftopR-201Carrier: 48PGDM051008G200XX | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0809-0811
15 | AC-35 | Podesta Ranch Elementary | Main | Rooftop | 1st Floor Corridor | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 1008G40001 | AC-35Podesta Ranch ElementaryMainRooftop1st Floor CorridorCarrier: 48PGDM041008G40001 | 2008 | 3 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB, 9/17/2025 | IMG_0812-0815
16 | AC-33 | Podesta Ranch Elementary | Main | Rooftop | Electric 1 | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 1008G40004 | AC-33Podesta Ranch ElementaryMainRooftopElectric 1Carrier: 48PGDM041008G40004 | 2008 | 3 | 11.3425 | Poor | 208 | 25 | 1 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB, 9/17/2025 | IMG_0816-0818
17 | AC-41 | Podesta Ranch Elementary | Main | Rooftop | Workroom 3 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20021 | AC-41Podesta Ranch ElementaryMainRooftopWorkroom 3Carrier: 48PGDM061008G20021 | 2008 | 5 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0820-0823
18 | AC-38 | Podesta Ranch Elementary | Main | Rooftop | 2nd Floor Corridor | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30014 | AC-38Podesta Ranch ElementaryMainRooftop2nd Floor CorridorCarrier: 48PGDM051008G30014 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0824-0825
19 | AC-34 | Podesta Ranch Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48PGDM28 | Carrier: 48PGDM28 | 0908G40050 | AC-34Podesta Ranch ElementaryMainRooftopInteriorCarrier: 48PGDM280908G40050 | 2008 | 25 | 11.3425 | Poor | 460 | 65 | 3 | New High Efficiency Gas Package Unit | Carrier: 48QE | 25 | 15.3 | 0 | JB, 9/17/2025 | IMG_0826-0829
20 | AC-29 | Podesta Ranch Elementary | Main | Rooftop | Platform | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30015 | AC-29Podesta Ranch ElementaryMainRooftopPlatformCarrier: 48PGDM051008G30015 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0830-0833
21 | AC-31 | Podesta Ranch Elementary | Main | Rooftop | Computer Lab | Gas Package | Carrier | 48PGDM08 | Carrier: 48PGDM08 | 1008G10009 | AC-31Podesta Ranch ElementaryMainRooftopComputer LabCarrier: 48PGDM081008G10009 | 2008 | 7.5 | 11.3425 | Poor | 460 | 25 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 7.5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0834-0836
22 | AC-36 | Podesta Ranch Elementary | Main | Rooftop | 2nd Floor Corridor | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30004 | AC-36Podesta Ranch ElementaryMainRooftop2nd Floor CorridorCarrier: 48PGDM051008G30004 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0837-0839
23 | AC-15 | Podesta Ranch Elementary | Main | Rooftop | R-216 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30001 | AC-15Podesta Ranch ElementaryMainRooftopR-216Carrier: 48PGDM051008G30001 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0840-0843
24 | AC-16 | Podesta Ranch Elementary | Main | Rooftop | R-215 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30038 | AC-16Podesta Ranch ElementaryMainRooftopR-215Carrier: 48PGDM051008G30038 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0844-0846
25 | AC-17 | Podesta Ranch Elementary | Main | Rooftop | AD-Corridor | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G20037 | AC-17Podesta Ranch ElementaryMainRooftopAD-CorridorCarrier: 48PGDM051008G20037 | 2008 | 4 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0847-0849
26 | AC-32 | Podesta Ranch Elementary | Main | Rooftop | Library | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20020 | AC-32Podesta Ranch ElementaryMainRooftopLibraryCarrier: 48PGDM061008G20020 | 2008 | 5 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0850-0853
27 | AC-30 | Podesta Ranch Elementary | Main | Rooftop | Conference | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 1008G40003 | AC-30Podesta Ranch ElementaryMainRooftopConferenceCarrier: 48PGDM041008G40003 | 2008 | 3 | 11.3425 | Poor | 208 | 25 | 1 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB, 9/17/2025 | IMG_0854-0856
28 | AC-37 | Podesta Ranch Elementary | Main | Rooftop | 1st Floor Corridor | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 0608G50024 | AC-37Podesta Ranch ElementaryMainRooftop1st Floor CorridorCarrier: 48PGDM040608G50024 | 2008 | 3 | 11.3425 | Poor | 208 | 25 | 1 | New High Efficiency Gas Package Unit | Carrier: 48GE | 3 | 17.2 | 0 | JB, 9/17/2025 | IMG_0857-0859
29 | AC-42 | Podesta Ranch Elementary | Main | Rooftop | Electric 4 | Package Cooling | Carrier | 50PG-M03-A-30 | Carrier: 50PG-M03-A-30 | 1108G20027 | AC-42Podesta Ranch ElementaryMainRooftopElectric 4Carrier: 50PG-M03-A-301108G20027 | 2008 | 2 | 11.072 | Poor | 208 | 21.8 | 1 | New High Efficiency Package Cooling Unit | Carrier: 48GE | 2 | 17.2 | 0 | JB, 9/17/2025 | IMG_0860-0862
30 | AC-29 | Podesta Ranch Elementary | Main | Rooftop | R-209 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20018 | AC-29Podesta Ranch ElementaryMainRooftopR-209Carrier: 48PGDM061008G20018 | 2008 | 5 | 11.3425 | Poor | 460 | 15 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0866-0868
31 | AC-28 | Podesta Ranch Elementary | Main | Rooftop | R-108 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30005 | AC-28Podesta Ranch ElementaryMainRooftopR-108Carrier: 48PGDM051008G30005 | 2008 | 4 | 11.3425 | Poor | 460 | 11.4 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0869-0870
32 | AC-27 | Podesta Ranch Elementary | Main | Rooftop | R-109 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30006 | AC-27Podesta Ranch ElementaryMainRooftopR-109Carrier: 48PGDM051008G30006 | 2008 | 4 | 11.3425 | Poor | 460 | 11.4 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0871-8072
33 | AC-26 | Podesta Ranch Elementary | Main | Rooftop | R-210 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30007 | AC-26Podesta Ranch ElementaryMainRooftopR-210Carrier: 48PGDM051008G30007 | 2008 | 4 | 11.3425 | Poor | 460 | 11.4 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0873-0874
34 | AC-25 | Podesta Ranch Elementary | Main | Rooftop | R-211 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30003 | AC-25Podesta Ranch ElementaryMainRooftopR-211Carrier: 48PGDM051008G30003 | 2008 | 4 | 11.3425 | Poor | 460 | 11.4 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0875-0876
35 | AC-24 | Podesta Ranch Elementary | Main | Rooftop | R-110 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20028 | AC-24Podesta Ranch ElementaryMainRooftopR-110Carrier: 48PGDM061008G20028 | 2008 | 5 | 11.3425 | Poor | 460 | 13 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0877-0878
36 | AC-23 | Podesta Ranch Elementary | Main | Rooftop | R-111 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20025 | AC-23Podesta Ranch ElementaryMainRooftopR-111Carrier: 48PGDM061008G20025 | 2008 | 5 | 11.3425 | Poor | 460 | 13 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0879-0890
37 | AC-22 | Podesta Ranch Elementary | Main | Rooftop | R-212 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G30002 | AC-22Podesta Ranch ElementaryMainRooftopR-212Carrier: 48PGDM051008G30002 | 2008 | 4 | 11.3425 | Poor | 460 | 11.4 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0881-0882
38 | AC-21 | Podesta Ranch Elementary | Main | Rooftop | R-213 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 1008G20036 | AC-21Podesta Ranch ElementaryMainRooftopR-213Carrier: 48PGDM051008G20036 | 2008 | 4 | 11.3425 | Poor | 460 | 11.4 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 4 | 17.2 | 0 | JB, 9/17/2025 | IMG_0883-0884
39 | AC-20 | Podesta Ranch Elementary | Main | Rooftop | Lounge | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20026 | AC-20Podesta Ranch ElementaryMainRooftopLoungeCarrier: 48PGDM061008G20026 | 2008 | 5 | 11.3425 | Poor | 460 | 13 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0885-0886
40 | AC-19 | Podesta Ranch Elementary | Main | Rooftop | Admin | Gas Package | Carrier | 48PGDM07 | Carrier: 48PGDM07 | 1008G20026 | AC-19Podesta Ranch ElementaryMainRooftopAdminCarrier: 48PGDM071008G20026 | 2008 | 6 | 11.3425 | Poor | 460 | 15.4 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 6 | 17.5 | 0 | JB, 9/17/2025 | IMG_0887-0890
41 | AC-18 | Podesta Ranch Elementary | Main | Rooftop | R-214 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 1008G20027 | AC-18Podesta Ranch ElementaryMainRooftopR-214Carrier: 48PGDM061008G20027 | 2008 | 5 | 11.3425 | Poor | 460 | 13 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 5 | 17.2 | 0 | JB, 9/17/2025 | IMG_0891-0893
42 | AC-40 | Podesta Ranch Elementary | Main | Rooftop | Kitchen | Gas Package | Carrier | 48PGFM16 | Carrier: 48PGFM16 | 0908G20041 | AC-40Podesta Ranch ElementaryMainRooftopKitchenCarrier: 48PGFM160908G20041 | 2008 | 15 | 10.47 | Poor | 460 | 35.8 | 3 | New High Efficiency Gas Package Unit | Carrier: 48GE | 15 | 16.5 | 0 | JB, 9/17/2025 | IMG_0899-0905
| ANNUAL TOTAL | [11 empty] | 210.5 | [7 empty] | 210.5

## 2.2) HVAC Controls
Lodi USD: Creekside Elementary: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | AC-1A | Creekside Elementary | Admin / Office | Rooftop | Admin / Office | Gas Package | Lennox | LGH048H4EH2G | Lennox: LGH048H4EH2G | 4 | 16.15 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | AC-5 | Creekside Elementary | Admin / Office | Rooftop | Admin / Office | Gas Package | Lennox | LGH092H4S1G | Lennox: LGH092H4S1G | 7.5 | 16.15 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | AC-1B | Creekside Elementary | Admin / Office | Rooftop | Admin / Office | Gas Package | Lennox | LGH048H4EH2G | Lennox: LGH048H4EH2G | 4 | 16.15 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | No ID Tag | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA060S4N44G | Lennox: TSA060S4N44G | 5 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | CU-4 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | CU-1 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | CU-5 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | CU-3 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | CU-4 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | CU-2 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | CU-1 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA060S4N44G | Lennox: TSA060S4N44G | 5 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | CU-5 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | CU-3 | Creekside Elementary | Library Building | Rooftop | Multi Zone Air Handler | Condensing Unit | Lennox | TSA048S4N44G | Lennox: TSA048S4N44G | 4 | 12.35 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | AC-6A | Creekside Elementary | 16-17 Building | Rooftop | Classroom | Gas Package | Lennox | LGH048H4EH2G | Lennox: LGH048H4EH2G | 4 | 17 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | AC-6B | Creekside Elementary | 16-17 Building | Rooftop | Classroom | Gas Package | Lennox | LGH048H4EM1G | Lennox: LGH048H4EM1G | 4 | 17 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| TOTAL | [8 empty] | 65.5 |  |  | 15
Lodi USD: Delta Sierra Middle: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | No ID Tag | Delta Sierra Middle | Office, 1, 2 Bldg. | Rooftop | Conference Rm | Gas Package | Lennox | ZGB060S4BS1G | Lennox: ZGB060S4BS1G | 5 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | No ID Tag | Delta Sierra Middle | Office, 1, 2 Bldg. | Rooftop | Office | Gas Package | Lennox | ZGB060S4BS1G | Lennox: ZGB060S4BS1G | 5 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | No ID Tag | Delta Sierra Middle | Office, 1, 2 Bldg. | Rooftop | Principal | Gas Package | Lennox | ZGB060S4BS1G | Lennox: ZGB060S4BS1G | 5 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | AC-5 | Delta Sierra Middle | Office, 1, 2 Bldg. | Rooftop | Classroom 2 | Gas Package | Lennox | ZGA092S4MS1G | Lennox: ZGA092S4MS1G | 7.5 | 13 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | No ID Tag | Delta Sierra Middle | Office, 1, 2 Bldg. | Rooftop | Classroom 1 | Gas Package | Lennox | ZGB036S4BS1G | Lennox: ZGB036S4BS1G | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | #2 | Delta Sierra Middle | Classroom 3-6 | Rooftop | AC6 | Split Condenser | Lennox | SSB048H4S43G | Lennox: SSB048H4S43G | 4 | 12.6 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | #4 | Delta Sierra Middle | Classroom 3-6 | Rooftop | AC6 | Split Condenser | Lennox | SSB048H4S43G | Lennox: SSB048H4S43G | 4 | 12.6 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | #1 | Delta Sierra Middle | Classroom 3-6 | Rooftop | AC6 | Split Condenser | Lennox | SSB048H4S43G | Lennox: SSB048H4S43G | 4 | 12.6 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | #3 | Delta Sierra Middle | Classroom 3-6 | Rooftop | AC6 | Split Condenser | Lennox | SSB048H4S43G | Lennox: SSB048H4S43G | 4 | 12.6 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | A/C-3 | Delta Sierra Middle | Classroom 35-38 | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | A/C-4 | Delta Sierra Middle | Classroom 35-38 | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | A/C-2 | Delta Sierra Middle | Classroom 35-38 | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | A/C-1 | Delta Sierra Middle | Classroom 35-38 | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
16 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
17 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
18 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
19 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
20 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
21 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
22 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
23 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
24 | No ID Tag | Delta Sierra Middle | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| TOTAL | [8 empty] | 101.5 |  |  | 24
Lodi USD: GL Mosher Elementary: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | AC-41 | GL Mosher Elementary | Main | Rooftop | Rm 209 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | AC-38 | GL Mosher Elementary | Main | Rooftop | Rm 224 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | AC-28 | GL Mosher Elementary | Main | Rooftop | Rm 121 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | AC-29 | GL Mosher Elementary | Main | Rooftop | Rm 213 | Gas Package | Trane | YHC043A4RMA0Y00C1 | Trane: YHC043A4RMA0Y00C1 | 4 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | AC-27 | GL Mosher Elementary | Main | Rooftop | Rm 123 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | AC-26 | GL Mosher Elementary | Main | Rooftop | Rm 214 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | AC-25 | GL Mosher Elementary | Main | Rooftop | Rm 215 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | AC-24 | GL Mosher Elementary | Main | Rooftop | Rm 125 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | AC-23 | GL Mosher Elementary | Main | Rooftop | Rm 127 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | AC-22 | GL Mosher Elementary | Main | Rooftop | Rm 216 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | AC-21 | GL Mosher Elementary | Main | Rooftop | Rm 217 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | AC-20 | GL Mosher Elementary | Main | Rooftop | Rm 132 | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | AC-19 | GL Mosher Elementary | Main | Rooftop | Rm 136 | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | AC-18 | GL Mosher Elementary | Main | Rooftop | Rm 218 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 4 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | AC-17 | GL Mosher Elementary | Main | Rooftop | Rm 101 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
16 | AC-30 | GL Mosher Elementary | Main | Rooftop | Rm 228 | Gas Package | Trane | 2YCC3024A1040AA | Trane: 2YCC3024A1040AA | 2.5 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
17 | AC-37 | GL Mosher Elementary | Main | Rooftop | Rm 120 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
18 | No ID Tag | GL Mosher Elementary | Main | Rooftop | Classroom | Package Cooling | Carrier | 48GE | Carrier: 48GE | 2.5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
19 | AC-32 | GL Mosher Elementary | Main | Rooftop | Rm 146 | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
20 | AC-16 | GL Mosher Elementary | Main | Rooftop | Rm 219 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
21 | AC-15 | GL Mosher Elementary | Main | Rooftop | Rm 220 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
22 | AC-36 | GL Mosher Elementary | Main | Rooftop | Rm 222 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 4 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
23 | AC-39 | GL Mosher Elementary | Main | Rooftop | Rm 149 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
24 | AC-31 | GL Mosher Elementary | Main | Rooftop | Rm 229 | Gas Package | Trane | YSC092A4RLA2D00C10000A600 | Trane: YSC092A4RLA2D00C10000A600 | 7.5 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
25 | AC-15 | GL Mosher Elementary | Main | Rooftop | Rm 220 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
26 | AC-14 | GL Mosher Elementary | Main | Rooftop | Rm 221 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
27 | AC-13 | GL Mosher Elementary | Main | Rooftop | Rm 102 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
28 | AC-12 | GL Mosher Elementary | Main | Rooftop | Rm 201 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 4 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
29 | AC-11 | GL Mosher Elementary | Main | Rooftop | Rm 103 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
30 | AC-10 | GL Mosher Elementary | Main | Rooftop | Rm 104 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
31 | AC-9 | GL Mosher Elementary | Main | Rooftop | Rm 202 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
32 | AC-8 | GL Mosher Elementary | Main | Rooftop | Rm 203 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
33 | AC-7 | GL Mosher Elementary | Main | Rooftop | Rm 105 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
34 | No ID Tag | GL Mosher Elementary | Main | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
35 | AC-33 | GL Mosher Elementary | Main | Rooftop | Rm 151 | Package Cooling | Carrier | 48GE | Carrier: 48GE | 2.5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
36 | AC-6 | GL Mosher Elementary | Main | Rooftop | Rm 106 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
37 | AC-5 | GL Mosher Elementary | Main | Rooftop | Rm 204 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
38 | AC-4 | GL Mosher Elementary | Main | Rooftop | Rm 206 | Gas Package | Trane | YHC033A4RMA0W00C1 | Trane: YHC033A4RMA0W00C1 | 3 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
39 | AC-3 | GL Mosher Elementary | Main | Rooftop | Rm 107 | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
40 | AC-2 | GL Mosher Elementary | Main | Rooftop | Rm 108 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
41 | AC-1 | GL Mosher Elementary | Main | Rooftop | Rm 206 | Gas Package | Trane | YHC043A4RMA0Y00C100000600 | Trane: YHC043A4RMA0Y00C100000600 | 4 | 11.765 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
42 | AC-34 | GL Mosher Elementary | Main | Rooftop | Rm 153 | Gas Package | Carrier | 48GE | Carrier: 48GE | 17.5 | 16.5 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
43 | AC-40 | GL Mosher Elementary | Main | Rooftop | Rm 114 | Gas Package | Carrier | 48GE | Carrier: 48GE | 15 | 16.3 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| No ID Tag | GL Mosher Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | N | No Change
44 | No ID Tag | GL Mosher Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
45 | No ID Tag | GL Mosher Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
46 | No ID Tag | GL Mosher Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
47 | No ID Tag | GL Mosher Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 8 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
48 | No ID Tag | GL Mosher Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 8 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
49 | No ID Tag | GL Mosher Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 8 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| TOTAL | [8 empty] | 202.5 |  |  | 49
Lodi USD: John Muir Elementary: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | No ID Tag | John Muir Elementary | Admin / Office | Rooftop | Offices | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | CU 11 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | CU 4 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | CU 5 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | CU 6 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 3 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | CU 7 | John Muir Elementary | MPR | Ground Mount | MPR | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | CU 3 | John Muir Elementary | MPR | Rooftop | Kitchen | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 3.5 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | CU 10 | John Muir Elementary | MPR | Rooftop | Kitchen | Split Condenser | Carrier | 27SCA | Carrier: 27SCA | 4 | 15 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | AC-1 | John Muir Elementary | A Bldg | Rooftop | Classroom | Gas Package | Lennox | LGH060H4EB4G | Lennox: LGH060H4EB4G | 5 | 17 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | No ID Tag | John Muir Elementary | A Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | No ID Tag | John Muir Elementary | A Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | No ID Tag | John Muir Elementary | A Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB036S4BS1G | Lennox: ZGB036S4BS1G | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
16 | No ID Tag | John Muir Elementary | A Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
17 | No ID Tag | John Muir Elementary | A Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
18 | No ID Tag | John Muir Elementary | A Bldg | Rooftop | Classroom | Gas Package | Lennox | LGH060H4EB4G | Lennox: LGH060H4EB4G | 5 | 17 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
19 | No ID Tag | John Muir Elementary | B Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
20 | No ID Tag | John Muir Elementary | B Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
21 | No ID Tag | John Muir Elementary | B Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
22 | No ID Tag | John Muir Elementary | B Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB036S4BS1G | Lennox: ZGB036S4BS1G | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
23 | No ID Tag | John Muir Elementary | B Bldg | Rooftop | Classroom | Gas Package | Lennox | LGH060H4EB4G | Lennox: LGH060H4EB4G | 5 | 17 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
24 | No ID Tag | John Muir Elementary | B Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
25 | No ID Tag | John Muir Elementary | B Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
26 | No ID Tag | John Muir Elementary | C Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
27 | No ID Tag | John Muir Elementary | C Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
28 | AC-17 | John Muir Elementary | C Bldg | Rooftop | Classroom | Gas Package | Lennox | LGH060H4EB4G | Lennox: LGH060H4EB4G | 5 | 17 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
29 | No ID Tag | John Muir Elementary | C Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB036S4BS1G | Lennox: ZGB036S4BS1G | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
30 | No ID Tag | John Muir Elementary | C Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
31 | No ID Tag | John Muir Elementary | C Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
32 | No ID Tag | John Muir Elementary | C Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
33 | No ID Tag | John Muir Elementary | D Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB036S4BS1Y | Lennox: ZGB036S4BS1Y | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
34 | No ID Tag | John Muir Elementary | D Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
35 | No ID Tag | John Muir Elementary | D Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
36 | No ID Tag | John Muir Elementary | D Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
37 | No ID Tag | John Muir Elementary | D Bldg | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BS1Y | Lennox: ZGB048S4BS1Y | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
38 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
39 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
40 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
41 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
42 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
43 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
44 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
45 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
46 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
47 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
48 | No ID Tag | John Muir Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | Est. 4-ton | Bard: Est. 4-ton | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
Gateway & Site Setup
| TOTAL | [8 empty] | 190.5 |  |  | 48
Lodi USD: Manlio Silva Elementary: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | AC-29 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | AC-28 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | AC-27 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | AC-26 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | AC-25 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | AC-24 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | AC-23 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | AC-22 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | AC-21 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | AC-20 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | AC-19 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | AC-18 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | AC-17 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | AC-30 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | AC-37 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
16 | AC-42 | Manlio Silva Elementary | Main | Rooftop | Interior | Package Cooling | Carrier | 48NG | Carrier: 48NG | 1.5 | 15.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
17 | AC-32 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
18 | AC-16 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
19 | AC-15 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
20 | AC-36 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
21 | AC-44 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
22 | AC-39 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
23 | AC-14 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
24 | AC-13 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
25 | AC-33 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
26 | AC-43 | Manlio Silva Elementary | Main | Rooftop | Interior | Package Cooling | Carrier | 48NG | Carrier: 48NG | 1.5 | 15.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
27 | AC-35 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
28 | AC-12 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
29 | AC-11 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
30 | AC-10 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
31 | AC-9 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
32 | AC-8 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
33 | AC-7 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
34 | AC-6 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
35 | AC-5 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
36 | AC-4 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
37 | AC-3 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
38 | AC-2 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
39 | AC-1 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
40 | AC-34 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 17.5 | 16.3 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
41 | AC-38 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
42 | AC-41 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 3 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
43 | AC-40 | Manlio Silva Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48GE | Carrier: 48GE | 15 | 16.5 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | C8 | Wall Mount Heat-Pump | Bard |  |  | 4 | 13 | N | N | No Change
| No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | C9 | Wall Mount Heat-Pump | Bard |  |  | 4 | 13 | N | N | No Change
44 | No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
45 | No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
46 | No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
47 | No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
48 | No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
49 | No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
50 | No ID Tag | Manlio Silva Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard | WG481-ANBVX4XXX | Bard: WG481-ANBVX4XXX | 4 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| TOTAL | [8 empty] | 205.5 |  |  | 50
Lodi USD: Podesta Ranch Elementary: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | AC-1 | Podesta Ranch Elementary | Main | Rooftop | Main | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | AC-2 | Podesta Ranch Elementary | Main | Rooftop | R-107 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | AC-3 | Podesta Ranch Elementary | Main | Rooftop | R-106 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | AC-4 | Podesta Ranch Elementary | Main | Rooftop | R-206 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | AC-5 | Podesta Ranch Elementary | Main | Rooftop | R-205 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | AC-6 | Podesta Ranch Elementary | Main | Rooftop | R-105 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | AC-7 | Podesta Ranch Elementary | Main | Rooftop | R-104 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | AC-8 | Podesta Ranch Elementary | Main | Rooftop | R-204 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | AC-9 | Podesta Ranch Elementary | Main | Rooftop | R-203 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | AC-10 | Podesta Ranch Elementary | Main | Rooftop | R-103 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | AC-11 | Podesta Ranch Elementary | Main | Rooftop | R-102 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | AC-12 | Podesta Ranch Elementary | Main | Rooftop | R-202 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | AC-13 | Podesta Ranch Elementary | Main | Rooftop | R-101 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | AC-14 | Podesta Ranch Elementary | Main | Rooftop | R-201 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | AC-35 | Podesta Ranch Elementary | Main | Rooftop | 1st Floor Corridor | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 3 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
16 | AC-33 | Podesta Ranch Elementary | Main | Rooftop | Electric 1 | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 3 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
17 | AC-41 | Podesta Ranch Elementary | Main | Rooftop | Workroom 3 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
18 | AC-38 | Podesta Ranch Elementary | Main | Rooftop | 2nd Floor Corridor | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
19 | AC-34 | Podesta Ranch Elementary | Main | Rooftop | Interior | Gas Package | Carrier | 48PGDM28 | Carrier: 48PGDM28 | 25 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
20 | AC-29 | Podesta Ranch Elementary | Main | Rooftop | Platform | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
21 | AC-31 | Podesta Ranch Elementary | Main | Rooftop | Computer Lab | Gas Package | Carrier | 48PGDM08 | Carrier: 48PGDM08 | 7.5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
22 | AC-36 | Podesta Ranch Elementary | Main | Rooftop | 2nd Floor Corridor | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
23 | AC-15 | Podesta Ranch Elementary | Main | Rooftop | R-216 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
24 | AC-16 | Podesta Ranch Elementary | Main | Rooftop | R-215 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
25 | AC-17 | Podesta Ranch Elementary | Main | Rooftop | AD-Corridor | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
26 | AC-32 | Podesta Ranch Elementary | Main | Rooftop | Library | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
27 | AC-30 | Podesta Ranch Elementary | Main | Rooftop | Conference | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 3 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
28 | AC-37 | Podesta Ranch Elementary | Main | Rooftop | 1st Floor Corridor | Gas Package | Carrier | 48PGDM04 | Carrier: 48PGDM04 | 3 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
29 | AC-42 | Podesta Ranch Elementary | Main | Rooftop | Electric 4 | Package Cooling | Carrier | 50PG-M03-A-30 | Carrier: 50PG-M03-A-30 | 2 | 12.69 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
30 | AC-29 | Podesta Ranch Elementary | Main | Rooftop | R-209 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
31 | AC-28 | Podesta Ranch Elementary | Main | Rooftop | R-108 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
32 | AC-27 | Podesta Ranch Elementary | Main | Rooftop | R-109 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
33 | AC-26 | Podesta Ranch Elementary | Main | Rooftop | R-210 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
34 | AC-25 | Podesta Ranch Elementary | Main | Rooftop | R-211 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
35 | AC-24 | Podesta Ranch Elementary | Main | Rooftop | R-110 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
36 | AC-23 | Podesta Ranch Elementary | Main | Rooftop | R-111 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
37 | AC-22 | Podesta Ranch Elementary | Main | Rooftop | R-212 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
38 | AC-21 | Podesta Ranch Elementary | Main | Rooftop | R-213 | Gas Package | Carrier | 48PGDM05 | Carrier: 48PGDM05 | 4 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
39 | AC-20 | Podesta Ranch Elementary | Main | Rooftop | Lounge | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
40 | AC-19 | Podesta Ranch Elementary | Main | Rooftop | Admin | Gas Package | Carrier | 48PGDM07 | Carrier: 48PGDM07 | 6 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
41 | AC-18 | Podesta Ranch Elementary | Main | Rooftop | R-214 | Gas Package | Carrier | 48PGDM06 | Carrier: 48PGDM06 | 5 | 11.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
42 | AC-40 | Podesta Ranch Elementary | Main | Rooftop | Kitchen | Gas Package | Carrier | 48PGFM16 | Carrier: 48PGFM16 | 15 | 10.8 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
43 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
44 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
45 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
46 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
47 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
48 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
49 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
50 | No ID Tag | Podesta Ranch Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard: | 3.5 | 12 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
Gateway & Site Setup
| TOTAL | [8 empty] | 238.5 |  |  | 50
Lodi USD: Sutherland Elementary: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | No ID Tag | Sutherland Elementary | Library | Rooftop | Library | Gas Package | Carrier | 48NG | Carrier: 48NG | 2 | 15.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | No ID Tag | Sutherland Elementary | Library | Rooftop | Library | Gas Package | Carrier | 48NG | Carrier: 48NG | 2 | 15.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | No ID Tag | Sutherland Elementary | Library | Rooftop | Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
16 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
17 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
18 | No ID Tag | Sutherland Elementary | Center Pod | Rooftop | Classroom 13-20 | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
19 | No ID Tag | Sutherland Elementary | Admin/MPR | Admin Roof | Admin Office | Gas Package | Trane | YHC092F4RLA1RTS | Trane: YHC092F4RLA1RTS | 7.5 | 12.7 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
20 | No ID Tag | Sutherland Elementary | Admin/MPR | Admin Roof | Kindergarden 2 | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
21 | No ID Tag | Sutherland Elementary | Admin/MPR | Admin Roof | Kindergarden 1 | Gas Package | Carrier | 48GE | Carrier: 48GE | 5 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| No ID Tag | Sutherland Elementary | Admin/MPR | MPR Roof | IDF closet | Ductless Split Heat-Pump | Fujitsu | AOU9RL2, ASU9RL2 | Fujitsu: AOU9RL2, ASU9RL2 | 0.75 | 16 | N | N | No Change
22 | No ID Tag | Sutherland Elementary | Admin/MPR | MPR Roof | MPR | Gas Package | Trane | YHD300G4RLD1RTS | Trane: YHD300G4RLD1RTS | 25 | 12.9 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
23 | No ID Tag | Sutherland Elementary | Admin/MPR | MPR Roof | Teacher's Lounge | Gas Package | Trane | YSC060G4ELB29D00 | Trane: YSC060G4ELB29D00 | 5 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
24 | No ID Tag | Sutherland Elementary | Admin/MPR | MPR Roof | Kitchen | Ductless Split Heat-Pump | Fujitsu | AOUH36KPAS1 | Fujitsu: AOUH36KPAS1 | 3 | 21 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
25 | No ID Tag | Sutherland Elementary | Admin/MPR | MPR Roof | Kitchen | Ductless Split Heat-Pump | Fujitsu | AOU24RLX | Fujitsu: AOU24RLX | 2 | 16 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
26 | No ID Tag | Sutherland Elementary | Admin/MPR | Stage Roof | Stage | Gas Package | Carrier | 48GE | Carrier: 48GE | 10 | 17.5 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
27 | No ID Tag | Sutherland Elementary | Admin/MPR | Stage Roof | Gate Classroom | Gas Package | Carrier | 48GE | Carrier: 48GE | 4 | 17.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
28 | No ID Tag | Sutherland Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard | 3.5 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
29 | No ID Tag | Sutherland Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard | 3.5 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
30 | No ID Tag | Sutherland Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard | 3.5 | 10 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| No ID Tag | Sutherland Elementary | Portable | Exterior Wall | Classroom | Wall Mount Heat-Pump | Bard |  | Bard | 3.5 | 10 | N | N | No Change
| TOTAL | [8 empty] | 149.25 |  |  | 30
Lodi USD: Wagner-Holt Elementary: Add Pelican Thermostats to Selected Units Where Not Already Present
| General Information |  |  |  |  | Equipment Data | [7 empty] | Proposed Controls Data
| ID Tag | Site | Building | Unit Location | Serves | System Type | Make | Model | Make: Model | Size (Tons) | SEER | Replaced Unit? (Y/N) | Add Controls? (Y/N) | Proposed System Type | Proposed Make | Proposed Model
1 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | MPR | Gas Package | Lennox | KGB300S4MH1G | Lennox: KGB300S4MH1G | 25 | 13.8 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
2 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | Main | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
3 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | MPR | Gas Package | Carrier | 48GE | Carrier: 48GE | 10 | 17.5 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
4 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | MPR | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
5 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | Admin | Gas Package | Lennox | ZGB060S4BW1G | Lennox: ZGB060S4BW1G | 5 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
6 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | D Admin | Gas Package | Carrier | 48GE | Carrier: 48GE | 10 | 17.5 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
7 | No ID Tag | Wagner-Holt Elementary | Main | Rooftop | Admin | Gas Package | Lennox | ZGB060S4BW1G | Lennox: ZGB060S4BW1G | 5 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
8 | No ID Tag | Wagner-Holt Elementary | Classroom | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
9 | No ID Tag | Wagner-Holt Elementary | Classroom | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
10 | No ID Tag | Wagner-Holt Elementary | Classroom | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
11 | No ID Tag | Wagner-Holt Elementary | Classroom | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
12 | No ID Tag | Wagner-Holt Elementary | Classroom | Rooftop | Classroom | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
13 | No ID Tag | Wagner-Holt Elementary | Classroom | Rooftop | Classroom | Gas Package | Lennox | ZGB036S4BS1G | Lennox: ZGB036S4BS1G | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
14 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Carrier | 48NG | Carrier: 48NG | 2 | 15.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
15 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
16 | B10 | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB036S4BS1G | Lennox: ZGB036S4BS1G | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
17 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
18 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
19 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
20 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Carrier | 48NG | Carrier: 48NG | 2 | 15.2 | Y | Y | Install WiFi Programmable Thermostat | Pelican | TC3
21 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
22 | B9 | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB036S4BS1G | Lennox: ZGB036S4BS1G | 3 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
23 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
24 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
25 | No ID Tag | Wagner-Holt Elementary | Library | Rooftop | Library | Gas Package | Lennox | ZGB048S4BW1G | Lennox: ZGB048S4BW1G | 4 | 14 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| AC-10 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YCP024F1LOBB | Trane: YCP024F1LOBB | 2 | 12 | N | N | No Change
| AC-4B | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA0BJU | Trane: YHC048A4RLA0BJU | 4 | 12 | N | N | No Change
| AC-9 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
| AC-4A | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
| AC-8 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
| AC-3 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
| AC-7 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
| AC-2 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
| AC-6 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
| AC-1 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Rheem | RGEA14048ADT101AA | Rheem: RGEA14048ADT101AA | 4 | 14 | N | N | No Change
| AC-5 | Wagner-Holt Elementary | H Building | Rooftop | Classroom | Gas Package | Trane | YHC048A4RLA1H | Trane: YHC048A4RLA1H | 4 | 12 | N | N | No Change
26 | No ID Tag | Wagner-Holt Elementary | Portable G1 | Wall Mount | Classroom | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
27 | No ID Tag | Wagner-Holt Elementary | Portable G2 | Wall Mount | Classroom | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
28 | No ID Tag | Wagner-Holt Elementary | Classroom E1 | Wall Mount | Classroom E1 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
29 | No ID Tag | Wagner-Holt Elementary | Classroom E2 | Wall Mount | Classroom E2 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
30 | No ID Tag | Wagner-Holt Elementary | Classroom E3 | Wall Mount | Classroom E3 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
31 | No ID Tag | Wagner-Holt Elementary | Classroom E4 | Wall Mount | Classroom E4 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
32 | No ID Tag | Wagner-Holt Elementary | Classroom E5 | Wall Mount | Classroom E5 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
33 | No ID Tag | Wagner-Holt Elementary | Classroom F1 | Wall Mount | Classroom F1 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
34 | No ID Tag | Wagner-Holt Elementary | Classroom F2 | Wall Mount | Classroom F2 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
35 | No ID Tag | Wagner-Holt Elementary | Classroom F3 | Wall Mount | Classroom F3 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
36 | No ID Tag | Wagner-Holt Elementary | Classroom F4 | Wall Mount | Classroom F4 | Wall Mount Heat-Pump | - | - | -: - | 3.5 | 11 | N | Y | Install WiFi Programmable Thermostat | Pelican | TC3
| TOTAL | [8 empty] | 208.5 |  |  | 36