| Return sealed envelope to: Shawnee Mission Unified Schools Purchasing Department 8200 W. 71st Street Shawnee Mission, Kansas 66204 ATTN: EVERETT MORGAN E-MAILED OR FAXED BIDS WILL NOT BE ACCEPTED. | DATE: May 31, 2017 BID NO. 17-024 BID TITLE: SMSD ANNUAL WATER TREATMENT AND MAINTENANCE SERVICES Bids will be accepted until and then publicly opened on: Date: JUNE 13, 2017 Day: TUESDAY Time: 10:30 a.m. Terms, conditions and specifications under which bids are requested are included. Please review thoroughly. |
| --- | --- |

You are invited to bid on SMSD ANNUAL WATER TREATMENT AND MAINTENANCE SERVICES

for the Shawnee Mission Unified Schools per the enclosed terms, conditions and specifications, F.O.B. Destination, Freight Prepaid and Add.  FREIGHT COSTS MUST BE INCLUDED IN THE BID PRICE(S).

We are enclosing only one copy of the bid specifications.   We are enclosing only one copy of the bid specifications.   Please return one (1) original, one (1) copy, for a total of two (2) hardcopies and one (1) electronic copy on a flash drive.

Unit bid price shall govern whenever a discrepancy occurs in the extended bid price on the Bid Summary page.  Bid will be awarded:  __X__All-or-None, ____ Item-by-Item, _____ Groups of Items, or ____ Groups & by-Item.  Payment will be made ON COMPLETION of Purchase Order.  DO NOT INCLUDE SALES TAX.

Any questions regarding the specifications and the bid procedures should be directed to Everett Morgan @ email; everettmorgan@smsd.org.   PHONE:  (913) 993-6474.

THIS BID IS NOT TRANSFERABLE

NOTE:  Bid Number and Name of Bidder must appear on the front of sealed envelope.  Emailed or Faxed bids will not be accepted.  Bids must be received in the Purchasing Office prior to bid opening.  If sending by U.S. Postal Service, please allow a minimum of 24 hours for your bid to be processed and delivered to the Purchasing Office by the Administrative Mail Center.  It is the responsibility of the bidder to ensure delivery of bids to the Purchasing Department.  Bidders shall hold all bid prices firm for acceptance for 90 calendar days after date of bid opening.

Bid results will be posted on the smsd.org website within approximately 5 working days after the bid opening.  Go to Public Information; Purchasing/Bidding; Bids and Bid Summaries.  Additionally, you may review the bid results in the Purchasing Office during the hours of 8:00 AM to 4:30 PM.

- NOTICE OF “NO RESPONSE FORM”

BID NO. 17-024

VENDORS WHO RESPOND TO THIS INVITATION WITH A COMPLETED NOTICE OF “NO RESPONSE” FORM WILL REMAIN ON OUR MAILING LIST, IF REQUESTED.

VENDORS MAKING NO RESPONSE AT ALL WILL BE REMOVED FROM OUR MAILING LIST.

Dear Vendor:

Please check () the appropriate box below, complete the remainder of this form and return it NO LATER THAN the scheduled Bid/Proposal/or Quote Date and Time.

Our company cannot provide the products, supplies and/or services listed in this bid, proposal or

quote.  Please MOVE our name and address to the following category(ies) so that we may bid at a later 	date ____________________________________________________________________

______________________________________________________________________________

We have chosen NOT to submit a response at this time, but would like to remain on your bid list

for this product category.  We did not submit a response because:

- Reason(s): _____________________________________________________________________

______________________________________________________________________________

- Please REMOVE our name from all SMSD bid lists until further notice.

- Reason(s): _____________________________________________________________________

______________________________________________________________________________

## COMPANY NAME:____________________________________________________

- REPRESENTATIVE (please print):________________________________________

- ADDRESS:  _______________________________  PHONE (_____)____________

- AUTHORIZED SIGNATURE: ____________________________________________

- TITLE:  ______________________________________  DATE:  ______________________

- PLEASE RETURN THIS FORM ONLY TO:

Shawnee Mission Unified School District #512

Purchasing Department

# Notice of “NO RESPONSE”

# 8200 W. 71st Street

Shawnee Mission,  KS  66204

OR

Fax to:  913/993-6225

BID NO.

BID FORM

- BID NO.  17-024

BID OF:

A CORPORATON ORGANIZED AND EXISTING UNDER THE LAWS

OF THE

A PARTNERSHIP CONSISTING OF

PARTNERS:

OR:	A SOLE PROPRIETOR; HERINAFTER CALLED THE BIDDER.

TO:	SHAWNEE MISSION PUBLIC SCHOOLS

ATTN:  Everett Morgan

8200 W. 71st Street

SHAWNEE MISSION KS  66204

The undersigned acknowledges that he has received and familiarized himself with the following:

Request for Bid

Shawnee Mission Public School District #512

Bid Number 17-024  for

ADDENDA NO(s):	 Received

The undersigned further acknowledges that he has familiarized himself with local conditions affecting the cost of the work at each place where the work is to be done.

In submitting this bid, the undersigned agrees:

| 1. | To furnish all material, labor, tools, expendable equipment, and all utility and transportation services necessary to perform and complete, in a workmanlike manner, all of the work required in accord with the bid documents. |
| --- | --- |
| 2. | To hold his bid open for ninety (90) days after receipt of bids and to accept the provisions of the instructions to bidders regarding disposition of bid security. |
| 3. | To commence the work upon receipt of Notice to Proceed, on/about , and to substantially complete the work not later than . |
| 4. | To accept the assessment of liquidated damages of $ per calendar day for each day following the substantial completion date listed above. |
| 5. | All materials to be non-proprietary, as specified, or approval equal. |

Lump Sum Bid:			Dollars

($	).

(Indicate bid in both numbers and words.  In the case of a discrepancy between the two, the amount shown in words shall govern.)

In submitting this bid, it is understood that the right to reject any and all bids and to waive irregularities in the bidding has been reserved by the owner.

Date this	 day of	, 2017.

Name of Bidder

Address of Bidder

Authorize Officer

Area Code/Telephone Number

Lump Sum Bid:

Lump Sum Bid for First Year (12 Month Period)	$

July 1, 2017 – June 30, 2018

Lump Sum Bid for Second Year/1st Renewal	$

July 1, 2018 – June 30, 2019

Lump Sum Bid for Third Year/2nd Renewal	$

July 1, 2019 – June 30, 2020

Lump Sum Bid for Fourth Year/3rd Renewal	$

July 1 2020 – June 30, 2021

Lump Sum Bid for Fifth Year/4th Renewal	$

July 1, 2021 – June 30, 2022

The undersigned hereby proposes and agrees to perform the foregoing for the unit price indicated for each bid item.  The bid cost for each item is determined by multiplying the unit price by the quantity noted.  Bid award will be determined by the sum of all the bid costs.

In submitting this bid, it is understood that the right to reject any and all bids and to waive irregularities in the bidding has been reserved by the Owner.

The undersigned has attached the required bid security.  In submitting this bid, it is understood that the right to reject any and all bids to waive irregularities in the bidding has been reserved by the owner.

Date this	 day of	, 2017.

Name of Bidder

Address of Bidder

Authorized Officer

Area Code/Telephone Number

SHAWNEE MISSION PUBLIC SCHOOLS

8200 W. 71st. Street

SHAWNEE MISSION, KS 66204

5% BID SECURITY FORM

Bid Security issued to: Shawnee Mission Public Schools, in the amount of 5% of the total amount of your Bid shall accompany your Bid as a guarantee that, if awarded all or part of the Bid, your firm will enter into contract to supply the items per the Bid Specifications.  Cashier checks & certified checks should be made payable to Shawnee Mission USD #512.

This Bid Security is to be made payable to Shawnee Mission Public Schools. If the firm awarded the Bid defaults in entering into a contract for the purchase of those items as specified, the Bid Security will become the property of the School District. Bids not accepted within ninety (90) days after the time set for submission will have their Bid Securities returned.

PLEASE NOTE:  Should you submit a cashiers or certified check instead of a bid bond, the following steps will be used by SMSD in the handling of that check:

- SMSD will deposit your check into a SMSD bank account within 2-3 days after bid opening.

- Within four (4) weeks after board approval of the bid, a district check shall be mailed to the non-successful bidder(s) to reimburse them for the exact amount of their cashiers/certified check.

- Within four (4) weeks after the completion of a formal written and properly signed contract, or the issuance of a SMSD purchase order, a district check shall be mailed to the successful bidder(s) for the exact amount of their cashiers/certified check.

NOTE:	IF SUCH SECURITY IS NOT ENCLOSED WITH THE BID, IT WILL BE CAUSE FOR REJECTION OF THE BID.

______________________________	$ _______________________________

Company	Amount of Total Bid

_______________________________	$ _______________________________

Address	Amount of Bid Bond

_______________________________

- City, State, Zip Code

________Bid Security attached to this form. (Please send the two together.)

_________________________________	_________________________________

Signature of Authorized Rep.	Phone

_________________________________	_________________________________

Please Print Name	Position

INVITATION TO BID

You are invited to quote a Lump Sum Annual Price for a twelve-month period providing a complete water treatment service, including services, testing equipment, and chemicals, as specified herein for all air conditioning and heating systems in specified school buildings for Shawnee Mission School District #512.

A list of schools with the number of boilers and cooling towers is attached.  The existing chemicals at each school will be used up or removed from the site at the beginning of this service contract.  This is to include closed loop systems.  A list is provided.

COST ACCOUNTING REQUIREMENT

Bidders are requested to classify the cost-per-year of their bid for each school.  (This is not to be considered as an Alternate Bid.)  See attached listing which is to be returned with the bid.

METHOD OF AWARD

Award will be made to the low responsible bidder.  Bidders shall include prices for services in all buildings listed as this bid will be awarded all-or-none.  Otherwise, the bid will be considered non-responsive.

PERIOD OF CONTRACT

The contract resulting from this bid shall be for a period of one (1) year.  However, SMSD retains the right to renew it annually for four (4) additional years.  The successful bidder will be given a written Notice to Proceed and shall provide contractual services for a twelve-month period, commencing on or about July 1, 2017 and ending June 30, 2018.  The services will be reviewed after the tenth (10th) month each contract year.  It will be the judgment of the Shawnee Mission School District to continue to contract for the next twelve-month period or to cancel the services at that time.

There will be no price increase allowed for the first two (2) renewal years.  There shall be a provision for a maximum increase of 5% for renewal years three and four.  Payment shall be made in twelve equal monthly installments.  All invoices are to be submitted to the Supervisor of Maintenance for his certification of satisfactory service.

SCOPE OF SERVICES TO BE PROVIDED

The successful water treatment company shall provide a complete water treatment service to the Shawnee Mission School District for the term of the contract.  This is to include twice monthly visits to each facility listed for treatment and water management.  The water treatment company will provide all necessary chemicals, testing, record keeping, labor, material, supervision, equipment, and logging of work performed to include test results, chemicals and quantity used and time spent at each facility.  This contract will cover but not be limited to chemical transportation and storage of product by water treatment contractor, all products used at a facility will have MSDS (Material Safety Data Sheets) provided to the facility and copies sent to the Maintenance Supervisor and Utility Foreman for the Shawnee Mission School District; 11475 West 93rd Street; Overland Park KS  66214.  The water treatment company is to provide easy to interpret log sheets, provide all testing kits and/or materials needed to provide a successful water treatment program.

Services shall also include consultation meetings with the head custodian at each facility on the specifics of the testing and water analysis performed on each visit to the facility.  This service contract is to be considered a turn key contract for the contractor to provide all labor, material, equipment, supervision, transportation, storage, testing, chemical treatment, reports, and consultation associated with this water treatment contract.

No chemicals will be allowed to be stored in the facilities.  Quantities provided on each visit will be recorded, logged, and copies provided to the head custodian at each facility.

The successful bidder will also provide as part of this contract installed coupon trees and coupons at each centrifugal chiller site and the periodic testing of each tree and coupons be repeatable testing laboratory with semiannual reports provided to the Supervisor of Maintenance and Utility Foreman of the Shawnee Mission School District.

SHAWNEE MISSION SCHOOL DISTRICT

COOLING TOWER, STEAM BOILER AND CLOSE SYSTEMS WATER TREATMENT

BID SPECIFICATIONS

GENERAL

This bid request is for a chemical water treatment service contractor to provide Shawnee Mission School District with a full service, comprehensive water treatment program for the HVAC systems at the locations specified.

The water treatment service contractor must be active in the field of on-site full service programs as defined by scope and letter of this specification; in the proof that is has operated a full service program in the local area no less than five (5) years.  A minimum of Ten (10) references currently operating under a full service program is required.  Shawnee Mission School District will also reserve the right to check additional customers and past customers, whether provided as references or not, in order to obtain a complete profile of the contractor’s ability to provide the specified services and their reliability in providing same.

The company must operate a qualified laboratory equipped with the instrumentation for water analysis and have qualified personnel who are experienced specifically under the guidelines of the Environmental Protection Agency.  Further, the company must be able to provide, from the laboratory, information regarding what Quality Assurance and Quality Control programs are in effect.  The maximum turn-around time for in-house lab results will be 72 hours after the lab receives the samples.

Only qualified service personnel shall inspect, analyze and service all systems.  The company shall provide all labor, chemicals, and adequate testing to properly treat and verify treatment of all systems.  The company will be responsible for the installation, adjustment and maintenance for all chemical feeding equipment.  PRODUCT SPECIFICATIONS AND MATERIAL SAFETY DATA SHEETS MUST BE POSTED AT EACH INSTALLATION.

Shawnee Mission School District will not consider any proposal wherein the District is required to supply, handle, store, order or receive any treatment chemicals in any quantity or packaging.  Furthermore, Shawnee Mission School District personnel will not be required to sample, test or treat any of the systems under this contract.  The water treatment contractor, without exception, will perform all delivery, handling, application, sampling and testing.

Absolutely no containers of chemical not currently being used, except chemicals under the feed pumps are to be delivered, received or stored within any of the facilities of the Shawnee Mission School District.  This means that treatment service person must anticipate need and replenish supply as required when on-site to ensure no void in treatment schedule.  Overflow or spillage must be cleaned from tank, pumps, floors, etc. immediately as occurring and trash or waste properly disposed of by water treatment contractor.

SERVICE FREQUENCY

All treated cooling tower systems shall be tested and treated twice per month during the cooling season.  Any cooling tower system that runs during the “off season” will be so identified by the district and shall receive a minimum of once per month service during this time.  Steam boiler systems will be tested and treated twice per month during the heating season.  All closed systems shall be tested at least once every 60 days during operation.

EMERGENCY SERVICE

Should district personnel identify an issue with the water treatment program and request immediate service such as empty chemical feed tanks for excessive bleed-off, there will be no additional charge for said service call nor will it count as part of the routine service frequency, provided it is not within 48 hours of the next scheduled service call.

All systems will be tested on the job site and the necessary treatments made at that time.  FAILURE TO INSPECT EACH FACILITY ACCORDING TO SCHEDULE AND/OR FAILURE TO TIMELY REPORT SAME SHALL CONSTITUTE BREACH OF CONTRACT.

TESTING AND REPORTING

Acceptable control parameters for condenser water, spray water and chilled/hot water systems will be established by the service report and/or testing laboratory report for each visit that will at a minimum include:

- Control Range of All Treatment Chemicals.

1.	Each systems pH including condensate return, Makeup Water pH and Recommended Control Range of pH for each system, if applicable.

2.	Each systems including feedwater and condensate return Conductivity, Makeup Water Conductivity and Recommended Control Range Conductivity for each system.

3.	Makeup Water Total Alkalinity and Steam boiler P-Alkalinity.

4.	Cooling Tower/Spray Water Total Hardness, Makeup Water Total Hardness.

5.	Water Softener effluent Total Hardness, where applicable.

7.	Water Softener and Makeup Water Chlorides.

8.	Corrosion and/or Scale inhibitor concentration for each system and recommended control range for each system consistent with manufacturer’s recommendations.

9.	Any additional on site analysis.

10.	Samples submitted for laboratory testing.

11.	Provisions for laboratory reference reporting.

- Treatment equipment condition and any repairs made or necessary.

- Treatments applications performed and signature of on site Shawnee Mission School District personnel.

PERFORMANCE

The water treatment service contractor will accompany and advise Shawnee Mission District personnel when annual inspections are made of condensers, steam boiler and spray water systems.  The contractor will be responsible for cleaning either chemically or mechanically to remove scale that was formed during the course of the treatment program.  This cleaning process is to be considered within this bid and not as an additional cost to Shawnee Mission School District.  In the case of scaled steam boilers, the failure of district personnel to properly blow down steam boilers must be addressed in writing to the district before serious scaling occurs.  Should such a boiler become scaled the district and the contractor will negotiate in good faith the cost of the descaling.

If condenser tubes are cleaned mechanically, equipment manufacturers recommended procedure must be followed to prevent damage.  Only those chemicals and methods recommended by the manufacturer shall be used to chemically clean cooler and condensers tubes in the air conditioning plants.

The water treatment service contractor’s program must deliver adequate corrosion inhibition for all treated systems and relevant metals as follows:

| System | Metal | Maximum Corrosion Rate in mils per year |
| --- | --- | --- |
| Cooling Towers | Mild Steel | 3 |
|  | Copper | 0.5 |
|  | Galvanized Steel | 3 |
| Closed Loops | Mild Steel | 0.75 |
|  | Cooper | 0.1 |

The contractor shall remove and analyze the corrosion coupons installed in the systems as identified on the system and building schedule, every 45 days during the systems operation.  A report on the findings based on the coupons, the resultant measured corrosion rate and any corrective necessary will be filed with the district within 30 days of removal of the coupons.  Replacement coupons will be provided at each location at no additional cost to the district.

The water treatment service contractor’s anti-microbial products must maintain the cooling tower and closed systems free of microbial growth as periodically identified by culturing.  Cooling tower TAB must not exceed 103 CFU/mL.

At the request of the district, the contractor shall sample each tower and have an independent laboratory test each sample for the presence of Legionella.  Such sampling and testing shall be at additional cost to the district, yet shall not exceed $250 per tower.

If Shawnee Mission School District building personnel observe any problems with the water treatment equipment between normal service inspections, they will notify the water treatment service contractor who will send a service person to correct the problem at no additional expense to Shawnee Mission School District.  If problems are caused by personnel of the Shawnee Mission School District, the contractor will notify the Director of Facility Operations.  The water treatment service contractor shall make all such notifications to Shawnee Mission School District in writing.

Contractor must provide documentation that chemical treatments are approved and as applicable registered by appropriate regulatory agencies.  Further, there will be no violation of disposal into sewer systems.

TRAINING

The water treatment service contractor will provide a basic water treatment training session for all interested parties within the district’s maintenance and custodial staff within 60 days of inception of this contract, or at a later date as requested by the district.  Additionally, the contractor will provide follow up training for district staff during the course of the contract as requested by the district at no additional cost.  Further, impromptu training as requested by onsite custodial staff on topics such as chemical safety and blow down will be provided as requested at no additional cost.

EQUIPMENT

The district currently owns all of the treatment related equipment at each location.  Should this equipment not meet the requirements of the bidder, bidder is to include the cost of replacement equipment as part of this proposal, and not an additional separate cost.  Any new equipment is to be installed at the bidder’s cost and shall become the property of the district.

Should any treatment related equipment fail or require repair, the repair or replacement of the equipment will be done by the water treatment contractor and shall be done without approval of the district.  The contractor shall include with this bid a complete schedule of routine equipment replacements and their associated  cost to install, such as bleed solenoids, chemical feed pumps, feed tubing, etc.  This schedule shall become part of this contract and therefore will be binding.  Any repairs outside of routine maintenance will be priced separately and approved at the discretion of the district.  It is anticipated that the total annual cost of routine repairs and replacements will not exceed $1,500.00.

Should any repair require the shut down of a system, the water treatment contractor must coordinate the shut down with the district.

CONDENSER WATER AND SPRAY WATER SYSTEMS

The contractor shall provide an effective chemical program to control corrosion, prevent scale formation and prevent microbiological growth.

The microbiological program will consist of three distinct micro biocides to be added alternately in slug dosage or via biocide feed systems.

BIOCIDES

As a minimum, the antimicrobial program will include:

- A non-foaming poly-quat. at least 50% active.

B.	A thiocyanate blend 20% active.

C.	An organo sulfonate compound at least 30% active.

*NO LIQUID SODIUM HYPOCHLORITE SHALL BE USED AS BIOCIDE*

CONDENSER/SPRAY WATER SCALE AND CORROSION INHIBITOR.

The cooling tower/condenser scale and corrosion inhibitor shall be at least a phosphonate, and polyacrylate blend with azole.  This program shall be free of inorganic phosphates and molybdate.

| Parameter | Control Limit |
| --- | --- |
| Cycles of Concentration, as control by Conductivity with Hard Water Makeup | 4-6 cycles 1400 – 2250 micro Siemens |
| Phosphonate, active | 5-8 ppm |
| Triazole | 2-4 ppm |

CHILLED/HOT WATER BOILER SYSTEMS

The chemical company shall provide suitable scale and corrosion inhibitors to provide protection of iron, steel, copper and brass.  Product must have the following minimum characteristics.

Closed chill water scale and corrosion inhibitor shall be a nitire/triazole blend.

| Parameter | Control Limit |
| --- | --- |
| Nitrite | 1000 – 1400 ppm |
| pH | 9.5 – 11 |
| Triazole | 4-6 ppm |

STEAM BOILER SYSTEMS

The water treatment service contractor shall provide suitable scale and corrosion protection for the steam boilers and their related condensate and feedwater systems.  In any location wherein steam is used for direct injected humidification, appropriate measures will be taken to provide adequate pH control while maintaining the concentration of amine in the humidification steam.  The treatment shall be at a minimum based on the following parameters:

| Parameter | Control Limit |
| --- | --- |
| Cycles of Concentration, as control by Conductivity with Hard Water Makeup | 9-15 Makeup water cycles 2500 – 4500 micro Siemens |
| P-Alkalinity | 300 – 600 ppm |
| Sulfite | 40 – 60 ppm |
| Polyacrylate Dispersant, as part of internal treatment blend | 15 – 30 ppm active polymer |
| Condensate pH | 8 - 9 |

CLOSED LOOP

|  | Heating | Cooling |  |
| --- | --- | --- | --- |
| East HS | X | X | 4 Pipe Boiler Room |
| Horizons HS |  |  | Condenser Loop with Tower |
| North HS | X | X | 2 Tower |
| Northwest HS | X | X | Boiler Room; 4 Pipe |
| South HS |  | X | 2 Tower |
| West HS | X | X | 4 Pipe Chiller Room & Boiler Room; 2 Tower |
| Bluejacket-Flint |  | X | Chiller, 2 Towers |
| Broken Arrow | X | X | Heat Pumps Loop |
| Carpenter | X | X | 2 Pipe |
| Diemer | X | X | 2 Pipe |
| McAuliffe | X | X | 2 Pipe |
| Prairie |  | X | Chill Water Tower |
| Rushton | X | X | 4 Pipe |
| Trailridge |  | X | Tower |
| Westwood View | X |  |  |

QUANTITIES OF EACH SYSTEM PER FACILITY

| Facility | Steam Boilers | Hot Water Boilers | Cooling Towers |
| --- | --- | --- | --- |
| East HS |  | 3 |  |
| North HS |  | 3 | 2 |
| Northwest HS |  | 2 | 2 |
| South HS |  |  | 2 |
| West HS |  | 2 | 2 |
| Broadmoor Center | 1 | 2 |  |
| Hocker Grove MS |  | 2 |  |
| Indian Creek Center |  | 1 | 1 |
| Indian Hills MS |  | 2 | 1 |
| Indian Woods MS |  | 4 | 1 |
| Trailridge MS |  |  | 1 |
| Westridge MS |  | 3 |  |
| Horizons HS |  | 1 | 1 |
| Apache |  | 2 |  |
| Bluejacket-Flint |  |  | 2 |
| Broken Arrow |  | 1 | 1 |
| Carpenter |  | 1 | 1 |
| Diemer |  | 2 |  |
| McAuliffe |  | 2 |  |

| Facility | Steam Boilers | Hot Water Boilers | Cooling Towers |
| --- | --- | --- | --- |
| Prairie |  |  | 1 |
| Rushton |  | 2 |  |
| Westwood View |  | 1 |  |

TREATMENTS PRESENTLY IN USE IN THE SHAWNEE MISSION SCHOOL DISTRICT

| American # | Basic Formulation | Principal Application |
| --- | --- | --- |
| 33 | Alkalinity | FDA and Non FDA Steam Boilers |
| 99 | Sulfite | FDA and Non FDA Steam Boilers |
| 138 | Nitrite, Borate, Tirazole | Closed Loop Systems |
| 202 | Amine | Steam Line Treatment |
| 475 | Sulfite, Phosphonate, Alkalinity, Polymer | FDA and Non FDA Steam Boilers |
| 840 | Carbamate | Biocide |
| 850 | Quat. Ammonium chloride | Biocide |
| 1524 | Phosphonate, Polymer | Cooling Tower Systems |
| 2100 | Dispersant | FDA and Non FDA Steam Boilers |

GUARANTEE OF SERVICE

The water treatment company specifically guarantees, as part of his quotation, the effectiveness of his water treatment program.  Any failure of the prescribed water treatment program to fulfill the requirements of this invitation will be construed as non-performance by the company.

If, after an inspection of any system by a representative of the water treatment company and the representative of Operations and Maintenance, it is determined that purging, descaling or cleaning to the system is necessary as a result of insufficient or improper water treatment service or chemicals furnished by the company, the representative of Operations and Maintenance has the right to order the treatment company to perform the needed work and chemicals for cleaning at no additional cost to the district.

The successful company may request an inspection of the equipment, prior to using his products; if this is not allowed, then the above paragraph is not applicable.

VISIT TO THE BUILDING

It will be the responsibility of the bidders to determine the quality of service involved, compare the specifications with the work to be done, and inform themselves as to all conditions, including other work, if any being performed.  Failure to do so will in no way relieve the successful bidder from the necessity of furnishing any materials or performing any work that may be required to carry out the contract in accordance with the true intent and meaning of the specifications without additional cost to the district.

The bidder shall base his bid for treatment of heating and air conditioning systems upon his best past experience with similar equipment or on the basis of his evaluation of the systems.

LICENSED CHEMIST

Each company submitting a bid shall certify that a licensed chemist is employed or retained by the company.

WATER TREATMENT CHEMICALS

The company shall submit a list of chemicals by generic name of the water treatment prescribed for each building.  The company’s chemicals must be compatible with the products already used in the systems.  The treatment must not clean the old corrosion that with its removal would cause the old building systems to leak.

Terms and Conditions

| A. | Bid Requirements and Considerations: 1. The Board of Education reserves the right to reject any or all bids, to accept any item or items in the bid, and to waive any informality in bids. 2. Each bid must be completed on SMSD bid forms. 3. Alternate bids will be considered only if the alternate properly meets specifications outlined in the bid. 4. Each bid shall be accompanied by bid security in the amount of five percent (5%) of the base bid, made payable unconditionally to the school district. This security will be submitted as evidence of good faith as a guarantee that, if awarded the contract, the bidder will execute required bonds and insurance within ten (10) days after receipt of Notice to Proceed. 5. Each bidder shall carefully examine the bidding documents and thoroughly inform himself with all requirements prior to submitting a bid. Should a bidder find discrepancies or ambiguities in, or omission from bidding documents, or should he be in doubt as to their meaning, he will at one and at least three days prior to bid date, notify the school district. Any subsequent addenda sent to bidders will become part of the contract documents. 6. Prior to submitting a bid, each bidder shall examine and thoroughly familiarize himself with all existing conditions; including applicable laws, codes, ordinances, rules, and regulations that will affect his work. Bidders shall visit the site, examine the existing conditions, and shall ascertain by reasonable means, all conditions that will in any manner affect the work. Contractors and/or bidders are required to check in with building authorities at the school immediately upon entering the school premises. 7. Prices quoted are to be free of all Federal, state, and local taxes, unless otherwise imposed by a governmental body and applicable to the work or material. The school district will obtain from the State of Kansas a sales tax exemption certificate number. The sales tax exemption certificate will permit the contractor to purchase materials for incorporation into this project without paying sales tax, provided that the contractor furnishes the certificate number to the supplier. 8. When submitting a substitute article as equal, the full name and illustrated description must be given. The Board of Education reserves the right, however, to decide upon its suitability for the intended use. Upon request, samples of substitute articles must be submitted. 9. Envelopes containing bids must be sealed and marked on the lower-left hand corner with the firm name and address of the bidder, bid number, bid opening date, and bid opening time. a. No special effort shall be made to sort incoming mail for potential bids. b. Bids not at the appointed place at time of bid opening will be rejected. c. Faxed Bid/Proposals will not be accepted as sealed bids. 10. If bid is accepted, USD #512 must be supplied with seller’s employer identification number of social security number, per IRS regulations. 11. Each contractor is responsible for his/her own worker’s compensation and liability insurance coverage. Shawnee Mission Unified School District #512 assumes this COVERAGE IS INCLUDED IN THE PRICE OF EACH BID TOTAL. 12. Any catalog, brand name or manufacturer’s reference used herein is intended to be descriptive and not restrictive. Offers on any reputable manufacturer’s regularly produced product which is similar and substantially equivalent will be considered. SMSD reserves the right to make final decisions as to the acceptability of comparable items. 13. Vendors who do not bid, but wish to remain on our bid list, should notify the Shawnee Mission USD #512 Purchasing Department in writing using the enclosed “Notice of No Response” form. Failure to do so may result in removal from this list. 14. If required by the bid form, the contractor shall submit with his bid a list of subcontractors and other persons or organizations that will perform work on this project. |
| --- | --- |
| B. | Form and Requirements of the Contract: |
|  | 1. The form of contract will be a Purchase Order issued by Shawnee Mission School District. In submitting his bid for consideration, each bidder agrees to commence work as soon as practical upon receipt of the school district purchase order and subsequent execution of applicable bonds and certificates of insurance. 2. The district shall not be responsible for any goods delivered or services performed without its purchase order signed by an authorized representative of the Purchasing Department. 3. The contractor shall not commence work under this contract until he has obtained the owner’s approval of a certificate of insurance providing evidence that the has obtained all the insurance required under this section, at least equal to the limits set forth hereinafter, with an insurance company acceptable to the owner. All policies shall provide for ten (10) days written notice to the owner prior to effective date of any changes affecting the policy. Two copies of the certificate of insurance in a form acceptable to the owner shall be delivered to the owner. The contractor shall not allow any subcontractor to commence work until the subcontractor has obtained insurance coverage similar to that required of the contractor. 4. For projects with a value of $20,000 or more; subsequent to award, the contractor shall furnish Performance Bond, Labor and Materials Payment Bond, and Kansas Statutory Bond covering the faithful performance of the contract and the payment of all obligations arising thereunder. All such bonds shall be submitted to the school district prior to the commencement of any contract work. 5. Contracts entered into on the basis of submitted bids are revocable if contrary to law. 6. The laws of the State of Kansas shall govern any contracts resulting from this bid. Actions must be filed in the Johnson County Courthouse in Johnson County, Kansas. 7. The seller shall provide the standard patent infringement indemnity clause which shall hold and save the Board of Education and its officers, agents, servants, and employees, harmless from liability of any patented, or unpatented invention, process, article, or appliance manufactured, or used, in the performance of the contract, including its use by the Board of Education. |
| C. | General Work Requirements. |
|  | 1. The contractor will be required to start the work per the schedule included herein. Liquidated damages as stated on the bid form will be assessed for each consecutive calendar day which the work is not substantially complete, beginning with the first day beyond the substantial completion time stated. Substantial completion is the owner’s ability to utilize the facility for its intended purpose. Shawnee Mission Public Schools will be the sole judge of substantial completion. 2. The owner reserves the right and may delay work if scheduling between school administration and contractor cannot be resolved. 3. It will be the contractor’s responsibility to have the approaching licenses and permits required by the state and/or municipality in which the work will be performed. It is also the contractor’s responsibility to make certain all work ad material meets local and state codes. Bidders shall include permit fees in their bid. 4. The contractor shall observe and comply with all ordinances, laws, and regulations, and shall protect and indemnify the owner against any claim or liability arising from or based on any violation of the same. The contractor shall comply with all regulations of agencies having jurisdiction with respect to sanitation and safety during construction. 5. All items shall be new and unused, unless otherwise specified by the district, and in first class condition. 6. Contractor shall be responsible for protection of the adjacent spaces during all phases of the project, demolition material storage and new construction. 7. All items furnished must be of their respective kinds, and will be free from defects in material and workmanship. Items will be subject to our inspection and approval at any time. Items furnished must be manufactured in compliance with all existing legal or governmental directives. 8. All work shall be of the highest quality. The contractor and subcontractor shall check their work regularly for quality and conformance as the work is in progress. Unsatisfactory work shall be corrected immediately. 9. The contractor shall promptly correct work rejected by the owner or failing to conform to the requirements of the contract documents, whether observed before or after substantially completion and whether or not fabricated, installed or completed. The contractor shall bear all costs of correcting such rejected work, including additional testing and inspections and compensation for owner services and expenses made necessary thereby. 10. As work is completed by the contractor/subcontractor, it shall be his responsibility to remove all excess material, equipment and debris from the premises. 11. Upon substantial completion, a scheduled punchlist inspection shall be conducted by the school district to identify any item(s) requiring additional work. All items noted on the punchlist shall be accomplished by the contractor prior to final payment. |
|  | D. Miscellaneous Requirements |
|  | The law requires that Section 1 through 5 of KSA 44-1030 (as follows) are to be included in all contracts to which our agency is a party: Except those with contractors, vendors or suppliers whose cumulative dollar total in any fiscal year is $5,000.00 or less, or who have fewer than four (4) employees: 1. The contractor shall observe the provisions of the Kansas act against discrimination and shall not discriminate against any person in the performance of work under the present contract because of race, religion, color, sex, physical handicap unrelated to such person’s ability to engage in the particular work, national origin or ancestry; 2. In all solicitations or advertisements for employees, the contractor shall include the phrase, “equal opportunity employer” or similar phrase to be approved by the commission; 3. If the contractor fails to comply with the manner in which the contractor reports to the commission in accordance with the provisions of KSA 1976 Supp .44-1030, as amended, the contractor shall be deemed to have breached the present contract and it may be canceled, terminated or suspended, in whole or in part, by the contracting agency; 4. If the contractor is found guilty of violation of the Kansas act against discrimination under a decision or order of the commission which has become final, the contractor shall be deemed to have breached the present contract and it may be canceled, terminated or suspended, in whole or in part, by the contract and it may be canceled, terminated or suspended, in whole or in part, by the contracting agency; and 5. The contractor shall include the provisions or paragraphs one (1) through (4) inclusively of this subsection (a) in every subcontract or purchase order so that such provisions will be binding upon such subcontractor or vendor. |
| E. | Payments to the Contractor: |
|  | In order for payment to occur on the “Payment Release Date”, the vendor’s INVOICE and the “BLUE” receiving copy of the Shawnee Mission purchase order must be received into the Business Office by the school cut-off date (preferably earlier) so that sufficient time is allowed for the payment to actually be processed through the Accounts Payable system. INVOICES MUST BE SUBMITTED TO THE APPROPRIATE PROJECT MANAGER THREE DAYS PRIOR TO THE SCHOOL CUT-OFF DATE. |

CONTRACTOR AND VENDOR CODE OF CONDUCT

Shawnee Mission School District requests that all contractor and vendor employees conduct themselves in an acceptable manner while performing work on school district property.  The following items are prohibited on school district properties:

- Physical or verbal contact with students or non-designated staff.

- All school district properties are tobacco free.  All tobacco, including smokeless tobacco, is prohibited.  There are no designated areas for tobacco use.  Contractors are required to post no tobacco signs.  Smoking will not be permitted inside private vehicles which are on school district property.  Workers may be required to sign a consent form acknowledging no tobacco use on the property.  Violators may be required to leave the work site.

- Drugs and/or alcohol consumed or present on district properties.

- Firearms and hunting items.

- Foul or abrasive language.

Additionally, all workers shall wear appropriate clothing on all parts of the body.  All workers shall utilize areas for vehicle access and parking, material storage, etc.  All workers shall wear nametags identifying their name and the name of the company they are representing.

INSURANCE REQUIREMENTS

| A. | Worker’s Compensation Insurance: Worker’s Compensation and Employer’s Liability Insurance as required by law to cover fully all employees. |
| --- | --- |
| B. | Bodily Injury and Property Damage Insurance: A comprehensive general bodily injury and property damage policy, including automobiles, covering the work to be performed. The policy shall be written to provide damage arising from one accident, with not less than $1,000,000 aggregate damages to, or destruction of property during the policy period; except, in case of automobile damage coverage, the minimum provided shall be not less than $1,000,000 bodily injury and $1,000,000 property damage per accident for any vehicle used on the project, whether owned, hired or nonowned. |
| C. | Special Insurance: Contractor for General Construction work shall take out and maintain insurance providing a minimum coverage of $1,000,000 for the following hazards: |
|  | Where the work to be performed involves excavation or other underground work or construction, the property damage insurance provided shall cover all injury to or destruction of property below the surface of the ground, such as wires, conduits, pipes, mains, sewers, etc., caused by the contractor’s operations, or injury to or destruction of property above or below ground resulting therefrom. Property damage insurance shall also cover the collapse of, or structural injury to, any building or structures on or adjacent to the owner’s premises, or the injury to or destruction of equipment and/or property resulting therefrom, caused by the removal of other buildings, structures, or supports, or by excavation below the ground, where the construction of a new structure or the demolition of any existing structure involves any of the foregoing designated hazards and in all cases where the contract provides for alterations in, additions to, or the underpinning of, and existing structure or structures. |
| D. | Subcontractor’s Insurance: If a part of this contract is sublet, the contractor shall either cover any or all subcontractors in his insurance policies; or require each subcontractor to secure insurance which will protect him against all applicable hazards not covered by the contractor’s insurance. |
|  | Certificate and Maintenance of Insurance: The contractor shall submit three (3) copies of Certificate of Insurance to the owner. The required insurance shall be maintained in force until the project is completed. |

| SHAWNEE MISSION PUBLIC SCHOOLS |  |  |  |  |
| --- | --- | --- | --- | --- |
| ACCOUNTS PAYABLE SCHEDULE |  |  |  |  |
| School |  | Payments |  |  |
| Cut Off |  | Released |  |  |
| 7/14/2016 |  | 7/26/2016 |  |  |
| 8/5/2016 |  | 8/16/2016 |  |  |
| 9/16/2016 |  | 9/27/2016 |  |  |
| 10/14/2016 |  | 10/25/2016 |  |  |
| 11/18/2016 |  | 11/29/2016 |  |  |
| 12/9/2016 |  | 12/20/2016 |  |  |
| 1/13/2017 |  | 1/24/2017 |  |  |
| 2/17/2017 |  | 2/28/2017 |  |  |
| 3/10/2017 |  | 3/28/2017 |  |  |
| 4/14/2017 |  | 4/25/2017 |  |  |
| 5/12/2017 |  | 5/23/2017 |  |  |
| 6/16/2017 |  | 6/27/2017 |  |  |