| Return sealed envelope to: Shawnee Mission Unified Schools Purchasing Department 8200 W. 71st Street Shawnee Mission, Kansas 66204 ATTN: EVERETT MORGAN E-MAILED OR FAXED BIDS WILL NOT BE ACCEPTED. | DATE: April 26, 2019 BID NO. 19-021 BID TITLE: Annual Fire Extinguisher Inspection & Maintenance Bids will be accepted until and then publicly opened on: Date: MAY 15, 2019 Day: WEDNESDAY Time: 10:00 a.m. CST Terms, conditions and specifications under which bids are requested are included. Please review thoroughly. |
| --- | --- |

You are invited to bid on Annual Fire Extinguisher Inspection & Maintenance for the Shawnee Mission Unified Schools per the enclosed terms, conditions and specifications, F.O.B. Destination, Freight Prepaid and Add.  FREIGHT COSTS MUST BE INCLUDED IN THE BID PRICE(S).

We are enclosing only one copy of the bid specifications.   Please return one (1) original, one (1) copy, for a total of two (2) hardcopies and one (1) electronic copy on a flash drive.

Unit bid price shall govern whenever a discrepancy occurs in the extended bid price on the Bid Summary page.  Bid will be awarded:  __X__All-or-None, _____ Item-by-Item, _____ Groups of Items, or ____ Groups & by-Item.  Payment will be made ON COMPLETION of Purchase Order.  DO NOT INCLUDE SALES TAX.

Any questions regarding the specifications should be directed to C. Alan Menn @ email ormenn@smsd.org ; PHONE:  (913) 993-8505.  Any questions regarding the bid procedure should be directed to Everett Morgan at everettmorgan@smsd.org ; Phone (913) 993-6474.

THIS BID IS NOT TRANSFERABLE

NOTE:  Bid Number and Name of Bidder must appear on the front of sealed envelope.  Emailed or Faxed bids will not be accepted.  Bids must be received in the Purchasing Office prior to bid opening.  If sending by U.S. Postal Service, please allow a minimum of 24 hours for your bid to be processed and delivered to the Purchasing Office by the Administrative Mail Center.  It is the responsibility of the bidder to ensure delivery of bids to the Purchasing Department.  Bidders shall hold all bid prices firm for acceptance for 90 calendar days after date of bid opening.

Bid results will be posted on the smsd.org website within approximately 5 working days after the bid opening.  Go to About; Departments; Purchasing/Bidding; Bids and Bid Summaries.  Additionally, you may review the bid results in the Purchasing Office during the hours of 8:00 AM to 4:30 PM.

The Shawnee Mission School District seeks interested fire extinguisher service contractors to provide annual inspection, testing and/or maintenance to include all labor, supervision, transportation, insurance, licenses, permits, tools, equipment, materials and services needed to complete all necessary work for all varieties and classes of fire extinguishers as prescribed by NFPA, and as exist in all of the school district facilities.  The contract shall be for one year beginning June 1, 2019 and ending May 31, 2020 with the option to renew it annually (see conditions for renewal under “Work Timeline and Renewal Terms”, page 25 of 28.  For the basis of bid award, interested contractors are to provide a total lump sum bid (based on noted quantities and unit costs) for all of the work identified per the enclosed Bid Form and Requirements, and Scope of Work.  Please note that actual costs for the noted services will be based on the unit prices noted for each extinguisher type/service for the number of extinguishers in any given year.

Inspection Time:

Inspections and testing may proceed on/about June 2, 2019 and are to be completed not later than August 8, 2019.  School is scheduled to resume on/about August 12, 2019.  Inspections and testing conducted during summer school hours or other summer activities shall be coordinated with individual school administration so as to not disrupt normal school activities. A twenty four (24) hour in advance notice is required. Inspections and testing in buildings receiving construction shall be coordinated with the Operations and Maintenance Department for access and appropriate timeframes.  Construction activities at some buildings may prohibit the completion of all inspection and testing until after the August 8, 2019 date.  Any such extensions beyond August 8 shall be mutually agreeable to both the school district and contractor.

Bid Submission:

Please provide your bid by no later than May 14, 2019 at 10:00 a.m.  Submit bids in accordance with the bid cover sheet.

- NOTICE OF “NO RESPONSE FORM”

BID NO. 19-021

VENDORS WHO RESPOND TO THIS INVITATION WITH A COMPLETED NOTICE OF “NO RESPONSE” FORM WILL REMAIN ON OUR MAILING LIST, IF REQUESTED.

VENDORS MAKING NO RESPONSE AT ALL WILL BE REMOVED FROM OUR MAILING LIST.

Dear Vendor:

Please check () the appropriate box below, complete the remainder of this form and return it NO LATER THAN the scheduled Bid/Proposal/or Quote Date and Time.

Our company cannot provide the products, supplies and/or services listed in this bid, proposal or

quote.  Please MOVE our name and address to the following category(ies) so that we may bid at a later date ____________________________________________________________________

______________________________________________________________________________

We have chosen NOT to submit a response at this time, but would like to remain on your bid list

for this product category.  We did not submit a response because:

- Reason(s): _____________________________________________________________________

______________________________________________________________________________

- Please REMOVE our name from all SMSD bid lists until further notice.

- Reason(s): _____________________________________________________________________

______________________________________________________________________________

- COMPANY NAME: ____________________________________________________

- REPRESENTATIVE (please print):________________________________________

- ADDRESS:  _______________________________ PHONE (_____)____________

- AUTHORIZED SIGNATURE: ____________________________________________

- TITLE:  ______________________________________ DATE:  ______________________

- PLEASE RETURN THIS FORM ONLY TO:

Shawnee Mission Unified School District #512

Purchasing Department

- Notice of “NO RESPONSE”

- 8200 W. 71st Street

Shawnee Mission,  KS  66204

OR

Fax to:  913/993-6225

SHAWNEE MISSION PUBLIC SCHOOLS

8200 W. 71st. Street

SHAWNEE MISSION, KS 66204

5% BID SECURITY FORM

Bid Security issued to: Shawnee Mission Public Schools, in the amount of 5% of the total amount of your Bid shall accompany your Bid as a guarantee that, if awarded all or part of the Bid, your firm will enter into contract to supply the items per the Bid Specifications.  Cashier checks & certified checks should be made payable to Shawnee Mission USD #512.

This Bid Security is to be made payable to Shawnee Mission Public Schools. If the firm awarded the Bid defaults in entering into a contract for the purchase of those items as specified, the Bid Security will become the property of the School District. Bids not accepted within ninety (90) days after the time set for submission will have their Bid Securities returned.

PLEASE NOTE:  Should you submit a cashiers or certified check instead of a bid bond, the following steps will be used by SMSD in the handling of that check:

- SMSD will deposit your check into a SMSD bank account within 2-3 days after bid opening.

- Within four (4) weeks after board approval of the bid, a district check shall be mailed to the non-successful bidder(s) to reimburse them for the exact amount of their cashiers/certified check.

- Within four (4) weeks after the completion of a formal written and properly signed contract, or the issuance of a SMSD purchase order, a district check shall be mailed to the successful bidder(s) for the exact amount of their cashiers/certified check.

NOTE:	IF SUCH SECURITY IS NOT ENCLOSED WITH THE BID, IT WILL BE CAUSE FOR REJECTION OF THE BID.

______________________________	$ _______________________________

Company	Amount of Total Bid

_______________________________	$ _______________________________

Address	Amount of Bid Bond

_______________________________

- City, State, Zip Code

________Bid Security attached to this form. (Please send the two together.)

_________________________________	_____________________________

Signature of Authorized Rep.	Phone

_________________________________	______________________________

Please Print Name	Position

BID NO. 19-021

BID FORM

BID OF:

A CORPORATON ORGANIZED AND EXISTING UNDER THE LAWS

OF THE

A PARTNERSHIP CONSISTING OF

PARTNERS:

OR:	A SOLE PROPRIETOR; HERINAFTER CALLED THE BIDDER.

TO:	SHAWNEE MISSION PUBLIC SCHOOLS

ATTN:  Everett Morgan

8200 W. 71st Street

SHAWNEE MISSION KS  66204

The undersigned acknowledges that he has received and familiarized himself with the following:

Request for Bid

Shawnee Mission Public School District #512

Bid Number 19-021 for Annual Fire Extinguisher Inspection & Maintenance-SMSD

ADDENDA NO(s):	 Received

The undersigned further acknowledges that he has familiarized himself with local conditions affecting the cost of the work at each place where the work is to be done.

In submitting this bid, the undersigned agrees:

| 1. | To furnish all material, labor, tools, expendable equipment, and all utility and transportation services necessary to perform and complete, in a workmanlike manner, all of the work required in accord with the bid documents. |
| --- | --- |
| 2. | To hold his bid open for ninety (90) days after receipt of bids and to accept the provisions of the instructions to bidders regarding disposition of bid security. |
| 3. | To commence the work upon receipt of Notice to Proceed, on/about , and to substantially complete the work not later than . |
| 4. | To accept the assessment of liquidated damages of $ per calendar day for each day following the substantial completion date listed above. |
| 5. | All materials to be non-proprietary, as specified, or approval equal. |

Lump Sum Bid:			Dollars

($	).

(Indicate bid in both numbers and words.  In the case of a discrepancy between the two, the amount shown in words shall govern.)

In submitting this bid, it is understood that the right to reject any and all bids and to waive irregularities in the bidding has been reserved by the owner.

Date this	 day of	, 2019.

Name of Bidder

Address of Bidder

Authorize Officer

Area Code/Telephone Number

In submitting this bid, the undersigned agrees:

1.	To furnish all material, labor, tools, expendable equipment, and all utility and transportation services necessary to perform and complete in a workmanlike manner, all of the work required in accord with the bid requirements.

2.	To hold his bid open for ninety (90) days after receipt of bids and to accept the provisions of the instructions to bidders regarding disposition of bid security.

3.	To commence the work upon receipt of Notice to Proceed (on/about June 2, 2019), and to complete work as quickly as possible, but not later than August 8, 2019 for the 1st year’s inspections.

The undersigned hereby proposes and agrees to perform the foregoing for the unit price indicated for each bid item.  The bid cost for each item is determined by multiplying the unit price by the quantity noted.  Bid award will be determined by the sum of all the bid costs.  Additional locations may be added to this contract in subsequent years as they become available.

A.	Annual Inspection/ Services

*Quantities indicated are based on the estimated quantity of all fire extinguishers or systems in the school district at the time of bidding.

|  | ### Type | Qty. | ### Unit Price | ### Ext Price |
| --- | --- | --- | --- | --- |
| 1. | ### Type ABC a. 2.5 pound b. 5 pound c. 10 pound d. 20 pound | 12 1,148 464 2 | $ $ $ $ | $ $ $ $ |
| 2. | ### Type BC a. 5 pound b. 10 pound | 9 0 | $ $ | $ $ |
| 3. | ### Type C02 a. 5 pound b. 10 pound c. 15 pound d. 20 pound | 16 9 4 4 | $ $ $ $ | $ $ $ $ |
| 4. | ### Type K a. 2.5 pound b. 6 Litre | 9 49 | $ $ | $ $ |
| 5. | Pressurized Water a. 2.5 gallon | 1 | $ | $ |
| 6. | ### Halon a. 5 pound | 3 | ### $ | ### $ |
|  |  |  | (A) SUBTOTAL: | ### $ |

B.	Fire Extinguisher Maintenance (Repair/Maintenance and Refill)

*Quantities indicated are based on an estimated quantity of 2% (or at least one of each applicable type) of extinguishers requiring this maintenance in the average year.

|  | ### Type | Qty. | ### Unit Price | ### Ext Price |
| --- | --- | --- | --- | --- |
| 1. | ### Type ABC a. 2.5 pound b. 5 pound c. 10 pound d. 20 pound | 1 25 10 1 | $ $ $ $ | $ $ $ $ |
| 2. | ### Type BC a. 5 pound b. 10 pound | 1 1 | $ $ | $ $ |
| 3. | ### Type C02 a. 5 pound b. 10 pound c. 15 pound d. 20 pound | 1 1 1 1 | $ $ $ $ | $ $ $ $ |
| 4. | ### Type K a. 2.5 pound b. 6 Litre | 1 1 | $ $ | $ $ |
| 5. | ### Halon a. 5 pound | 1 | ### $ | ### $ |
|  |  |  | (B) SUBTOTAL: | ### $ |

C.	Six (6)-Year Maintenance for Dry Chemicals and Halon Units

*Quantities indicated are based on maintenance due for 2019 or an estimated 1/6 (or at least one of each type) of each extinguisher type requiring this maintenance in the average year, whichever is greater.

|  | ### Type | Qty. | ### Unit Price | ### Ext Price |
| --- | --- | --- | --- | --- |
| 1. | ### Type ABC a. 2.5 pound b. 5 pound c. 10 pound d. 20 pound | 2 192 78 1 | $ $ $ $ | $ $ $ $ |
| 2. | ### Type BC a. 5 pound b. 10 pound | 1 1 | $ $ | $ $ |
| 3. | ### Type K a. 2.5 pound b. 6 Litre | 0 0 | $ $ | $ $ |
| 4. | ### Halon a. 5 pound | 1 | ### $ | ### $ |
|  |  |  | (C) SUBTOTAL: | ### $ |

D.	Five Year Hydro Test for Co2 and K-Class Units

*Quantities indicated are based on approximately 1/5 (or at least one of each applicable unit type) of each extinguisher type requiring this test in the average year.

|  | ### Type | Qty. | ### Unit Price | ### Ext Price |
| --- | --- | --- | --- | --- |
| 1. | ### Type CO2 a. 5 pound b. 10 pound c. 15 pound d. 20 pound | 1 1 1 1 | $ $ $ $______________ | $ $ $ $______________ |
| 2. | ### Type K a. 2.5 pound b. 6 litre | 1 11 | ### $ $______________ | ### $ $______________ |
|  |  |  | (D) SUBTOTAL: | ### $ |

E.	Twelve (12)-Year Hydro Test for Dry Chemical and Halon Units

*Quantities indicated are based on units due in 2014 or approximately 1/12 (or at least one of each applicable unit type) of each extinguisher type requiring this test in the average year.

|  | ### Type | Qty. | ### Unit Price | ### Ext Price |
| --- | --- | --- | --- | --- |
| 1. | ### Type ABC a. 2.5 pound b. 5 pound c. 10 pound d. 20 pound | 1 234 66 1 | $ $ $ $ | $ $ $ $ |
| 2. | ### Type BC a. 5 pound b. 10 pound | 1 1 | $ $ | $ $ |
| 3. | ### Halon a. 5 pound | 1 | ### $ | ### $ |
|  |  |  | (E) SUBTOTAL: | ### $ |

F.	Service Call Maintenance/Repair Requested by the School District

*Quantities indicated are based on an average of 1% (or at least one of each type) of extinguishers requiring replacement in the average year.

|  | ### Type | Qty. | ### Unit Price | ### Ext Price |
| --- | --- | --- | --- | --- |
| 1. | ### Type ABC a. 2.5 pound b. 5 pound c. 10 pound d. 20 pound | 1 12 5 1 | $ $ $ $ | $ $ $ $ |
| 2. | ### Type BC a. 5 pound b. 10 pound | 1 1 | $ $ | $ $ |
| 3. | ### Type C02 a. 2.5 pound b. 5 pound c. 10 pound d. 15 pound e. 20 pound | 1 1 1 1 1 | $ $ $ $ $ | $ $ $ $ $ |
| 4. | ### Type K a. 2.5 pound b. 6 Litre | 1 1 | $ $ | $ $ |
| 5. | ### Halon a. 5 pound | 1 | ### $ | ### $ |
|  |  |  | (F) SUBTOTAL: | ### $ |

G.	Trip Fee/Stop Charge

*An estimated quantity of 8 trip charges (outside of those trips to be included as part of the annual inspection services) are anticipated during the average year.

|  | ### Type | Qty. | ### Unit Price | ### Ext Price |
| --- | --- | --- | --- | --- |
| 1. | 8 Trip Charges | 8 | $ | $ |
|  |  |  | ### (F) SUBTOTAL: | ### $ |

|  | Total Bid Based on Items (A) thru (G) | ### $ |
| --- | --- | --- |

Terms and Conditions

| A. | Bid Requirements and Considerations: 1. The Board of Education reserves the right to reject any or all bids, to accept any item or items in the bid, and to waive any informality in bids. 2. Each bid must be completed on SMSD bid forms. 3. Alternate bids will be considered only if the alternate properly meets specifications outlined in the bid. 4. Each bid shall be accompanied by bid security in the amount of five percent (5%) of the base bid, made payable unconditionally to the school district. This security will be submitted as evidence of good faith as a guarantee that, if awarded the contract, the bidder will execute required bonds and insurance within ten (10) days after receipt of Notice to Proceed. 5. Each bidder shall carefully examine the bidding documents and thoroughly inform himself with all requirements prior to submitting a bid. Should a bidder find discrepancies or ambiguities in, or omission from bidding documents, or should he be in doubt as to their meaning, he will at one and at least three days prior to bid date, notify the school district. Any subsequent addenda sent to bidders will become part of the contract documents. 6. Prior to submitting a bid, each bidder shall examine and thoroughly familiarize himself with all existing conditions; including applicable laws, codes, ordinances, rules, and regulations that will affect his work. Bidders shall visit the site, examine the existing conditions, and shall ascertain by reasonable means, all conditions that will in any manner affect the work. Contractors and/or bidders are required to check in with building authorities at the school immediately upon entering the school premises. 7. Prices quoted are to be free of all Federal, state, and local taxes, unless otherwise imposed by a governmental body and applicable to the work or material. The school district will obtain from the State of Kansas a sales tax exemption certificate number. The sales tax exemption certificate will permit the contractor to purchase materials for incorporation into this project without paying sales tax, provided that the contractor furnishes the certificate number to the supplier. 8. When submitting a substitute article as equal, the full name and illustrated description must be given. The Board of Education reserves the right, however, to decide upon its suitability for the intended use. Upon request, samples of substitute articles must be submitted. 9. Envelopes containing bids must be sealed and marked on the lower-left hand corner with the firm name and address of the bidder, bid number, bid opening date, and bid opening time. a. No special effort shall be made to sort incoming mail for potential bids. b. Bids not at the appointed place at time of bid opening will be rejected. c. Faxed Bid/Proposals will not be accepted as sealed bids. 10. If bid is accepted, USD #512 must be supplied with seller’s employer identification number of social security number, per IRS regulations. 11. Each contractor is responsible for his/her own worker’s compensation and liability insurance coverage. Shawnee Mission Unified School District #512 assumes this COVERAGE IS INCLUDED IN THE PRICE OF EACH BID TOTAL. 12. Any catalog, brand name or manufacturer’s reference used herein is intended to be descriptive and not restrictive. Offers on any reputable manufacturer’s regularly produced product which is similar and substantially equivalent will be considered. SMSD reserves the right to make final decisions as to the acceptability of comparable items. 13. Vendors who do not bid, but wish to remain on our bid list, should notify the Shawnee Mission USD #512 Purchasing Department in writing using the enclosed “Notice of No Response” form. Failure to do so may result in removal from this list. 14. If required by the bid form, the contractor shall submit with his bid a list of subcontractors and other persons or organizations that will perform work on this project. |
| --- | --- |
| B. | Form and Requirements of the Contract: |
|  | 1. The form of contract will be a Purchase Order issued by Shawnee Mission School District. In submitting his bid for consideration, each bidder agrees to commence work as soon as practical upon receipt of the school district purchase order and subsequent execution of applicable bonds and certificates of insurance. 2. The district shall not be responsible for any goods delivered or services performed without its purchase order signed by an authorized representative of the Purchasing Department. 3. The contractor shall not commence work under this contract until he has obtained the owner’s approval of a certificate of insurance providing evidence that the has obtained all the insurance required under this section, at least equal to the limits set forth hereinafter, with an insurance company acceptable to the owner. All policies shall provide for ten (10) days written notice to the owner prior to effective date of any changes affecting the policy. Two copies of the certificate of insurance in a form acceptable to the owner shall be delivered to the owner. The contractor shall not allow any subcontractor to commence work until the subcontractor has obtained insurance coverage similar to that required of the contractor. 4. For projects with a value of $20,000 or more; subsequent to award, the contractor shall furnish Performance Bond, Labor and Materials Payment Bond, and Kansas Statutory Bond covering the faithful performance of the contract and the payment of all obligations arising thereunder. All such bonds shall be submitted to the school district prior to the commencement of any contract work. 5. Contracts entered into on the basis of submitted bids are revocable if contrary to law. 6. The laws of the State of Kansas shall govern any contracts resulting from this bid. Actions must be filed in the Johnson County Courthouse in Johnson County, Kansas. 7. The seller shall provide the standard patent infringement indemnity clause which shall hold and save the Board of Education and its officers, agents, servants, and employees, harmless from liability of any patented, or unpatented invention, process, article, or appliance manufactured, or used, in the performance of the contract, including its use by the Board of Education. |
| C. | General Work Requirements. |
|  | 1. The contractor will be required to start the work per the schedule included herein. Liquidated damages as stated on the bid form will be assessed for each consecutive calendar day which the work is not substantially complete, beginning with the first day beyond the substantial completion time stated. Substantial completion is the owner’s ability to utilize the facility for its intended purpose. Shawnee Mission Public Schools will be the sole judge of substantial completion. 2. The owner reserves the right and may delay work if scheduling between school administration and contractor cannot be resolved. 3. It will be the contractor’s responsibility to have the approaching licenses and permits required by the state and/or municipality in which the work will be performed. It is also the contractor’s responsibility to make certain all work ad material meets local and state codes. Bidders shall include permit fees in their bid. 4. The contractor shall observe and comply with all ordinances, laws, and regulations, and shall protect and indemnify the owner against any claim or liability arising from or based on any violation of the same. The contractor shall comply with all regulations of agencies having jurisdiction with respect to sanitation and safety during construction. 5. All items shall be new and unused, unless otherwise specified by the district, and in first class condition. 6. Contractor shall be responsible for protection of the adjacent spaces during all phases of the project, demolition material storage and new construction. 7. All items furnished must be of their respective kinds, and will be free from defects in material and workmanship. Items will be subject to our inspection and approval at any time. Items furnished must be manufactured in compliance with all existing legal or governmental directives. 8. All work shall be of the highest quality. The contractor and subcontractor shall check their work regularly for quality and conformance as the work is in progress. Unsatisfactory work shall be corrected immediately. 9. The contractor shall promptly correct work rejected by the owner or failing to conform to the requirements of the contract documents, whether observed before or after substantially completion and whether or not fabricated, installed or completed. The contractor shall bear all costs of correcting such rejected work, including additional testing and inspections and compensation for owner services and expenses made necessary thereby. 10. As work is completed by the contractor/subcontractor, it shall be his responsibility to remove all excess material, equipment and debris from the premises. 11. Upon substantial completion, a scheduled punchlist inspection shall be conducted by the school district to identify any item(s) requiring additional work. All items noted on the punchlist shall be accomplished by the contractor prior to final payment. |

| D. | Miscellaneous Requirements |
| --- | --- |
|  | The law requires that Section 1 through 5 of KSA 44-1030 (as follows) are to be included in all contracts to which our agency is a party: Except those with contractors, vendors or suppliers whose cumulative dollar total in any fiscal year is $5,000.00 or less, or who have fewer than four (4) employees: 1. The contractor shall observe the provisions of the Kansas act against discrimination and shall not discriminate against any person in the performance of work under the present contract because of race, religion, color, sex, physical handicap unrelated to such person’s ability to engage in the particular work, national origin or ancestry; 2. In all solicitations or advertisements for employees, the contractor shall include the phrase, “equal opportunity employer” or similar phrase to be approved by the commission; 3. If the contractor fails to comply with the manner in which the contractor reports to the commission in accordance with the provisions of KSA 1976 Supp .44-1030, as amended, the contractor shall be deemed to have breached the present contract and it may be canceled, terminated or suspended, in whole or in part, by the contracting agency; 4. If the contractor is found guilty of violation of the Kansas act against discrimination under a decision or order of the commission which has become final, the contractor shall be deemed to have breached the present contract and it may be canceled, terminated or suspended, in whole or in part, by the contract and it may be canceled, terminated or suspended, in whole or in part, by the contracting agency; and 5. The contractor shall include the provisions or paragraphs one (1) through (4) inclusively of this subsection (a) in every subcontract or purchase order so that such provisions will be binding upon such subcontractor or vendor. |
| E. | Payments to the Contractor: |
|  | In order for payment to occur on the “Payment Release Date”, the vendor’s INVOICE and the “BLUE” receiving copy of the Shawnee Mission purchase order must be received into the Business Office by the school cut-off date (preferably earlier) so that sufficient time is allowed for the payment to actually be processed through the Accounts Payable system. INVOICES MUST BE SUBMITTED TO THE APPROPRIATE PROJECT MANAGER THREE DAYS PRIOR TO THE SCHOOL CUT-OFF DATE. |

CONTRACTOR AND VENDOR CODE OF CONDUCT

Shawnee Mission School District requests that all contractor and vendor employees conduct themselves in an acceptable manner while performing work on school district property.  The following items are prohibited on school district properties:

- Physical or verbal contact with students or non-designated staff.

- All school district properties are tobacco free.  All tobacco, including smokeless tobacco, is prohibited.  There are no designated areas for tobacco use.  Contractors are required to post no tobacco signs.  Smoking will not be permitted inside private vehicles which are on school district property.  Workers may be required to sign a consent form acknowledging no tobacco use on the property.  Violators may be required to leave the work site.

- Drugs and/or alcohol consumed or present on district properties.

- Firearms and hunting items.

- Foul or abrasive language.

Additionally, all workers shall wear appropriate clothing on all parts of the body.  All workers shall utilize areas for vehicle access and parking, material storage, etc.  All workers shall wear nametags identifying their name and the name of the company they are representing.

INSURANCE REQUIREMENTS

| A. | Worker’s Compensation Insurance: Worker’s Compensation and Employer’s Liability Insurance as required by law to cover fully all employees. |
| --- | --- |
| B. | Bodily Injury and Property Damage Insurance: A comprehensive general bodily injury and property damage policy, including automobiles, covering the work to be performed. The policy shall be written to provide damage arising from one accident, with not less than $1,000,000 aggregate damages to, or destruction of property during the policy period; except, in case of automobile damage coverage, the minimum provided shall be not less than $1,000,000 bodily injury and $1,000,000 property damage per accident for any vehicle used on the project, whether owned, hired or nonowned. |
| C. | Special Insurance: Contractor for General Construction work shall take out and maintain insurance providing a minimum coverage of $1,000,000 for the following hazards: |
|  | Where the work to be performed involves excavation or other underground work or construction, the property damage insurance provided shall cover all injury to or destruction of property below the surface of the ground, such as wires, conduits, pipes, mains, sewers, etc., caused by the contractor’s operations, or injury to or destruction of property above or below ground resulting therefrom. Property damage insurance shall also cover the collapse of, or structural injury to, any building or structures on or adjacent to the owner’s premises, or the injury to or destruction of equipment and/or property resulting therefrom, caused by the removal of other buildings, structures, or supports, or by excavation below the ground, where the construction of a new structure or the demolition of any existing structure involves any of the foregoing designated hazards and in all cases where the contract provides for alterations in, additions to, or the underpinning of, and existing structure or structures. |
| D. | Subcontractor’s Insurance: If a part of this contract is sublet, the contractor shall either cover any or all subcontractors in his insurance policies; or require each subcontractor to secure insurance which will protect him against all applicable hazards not covered by the contractor’s insurance. |
|  | Certificate and Maintenance of Insurance: The contractor shall submit three (3) copies of Certificate of Insurance to the owner. The required insurance shall be maintained in force until the project is completed. |

| SHAWNEE MISSION PUBLIC SCHOOLS |  |  |  |
| --- | --- | --- | --- |
| ACCOUNTS PAYABLE SCHEDULE |  |  |  |
| School |  | Payments |  |
| Cut Off |  | Released |  |
| 4/12/2019 |  | 4/23/2019 |  |
| 5/19/2019 |  | 5/30/2019 |  |
| 6/14/2019 |  | 6/25/2019 |  |

Requirements and Scope of Work

| 1. | Bid Requirements |
| --- | --- |
|  | Provide a bid for all annual inspections, testing and/or maintenance to include all labor, supervision, transportation, insurance, licenses, permits, tools, equipment, materials, and services needed to complete all necessary work for all varieties and classes of fire extinguishers as prescribed by NFPA, and as exist in the Shawnee Mission Public Schools facilities. This service is intended for a one-year period covering annual requirements for the 2019-2020 school year with an option for the Shawnee Mission School District to extend the contract an additional 4 years. |

The typical annual Fire Extinguisher Inspection and Service may consist of the following tasks, as well as, any and all tasks required in order to conform with all applicable NFPA, Federal, State, OSHA and Local Authority having jurisdiction Standards, Regulations, Codes and Requirements:

| 1. | Check that unit is properly hung with the proper manufacturer’s hanger. |
| --- | --- |
| 2. | Remove the extinguisher from its hanger. |
| 3. | Check the gauge pressure. |
| 4. | Check the condition of the gauge and its compatibility with the extinguisher. |
| 5. | Check the weight of the extinguisher. |
| 6. | Check that the last hydro-test test date is within code requirements. |
| 7. | Check the last 6-year maintenance inspection for compliance, if applicable. |
| 8. | Check the last 12-year maintenance inspection for compliance, if applicable. |
| 9. | Check the valve and shell for damage or corrosion. |
| 10. | Remove the hose and inspect it for cracks or splits. |
| 11. | Check the hose threads for signs of wear. |
| 12. | Perform conductivity test on hose, per NFPA 10. |
| 13. | Check the condition of the discharge horn. |
| 14. | Check for obstructions that interfere with accessibility of the extinguisher. |
| 15. | Break the extinguisher seal and remove the locking pin. |
| 16. | Check the upper and lower handles. |
| 17. | Replace safety disk, if necessary. |
| 18. | Verification of service collar, replace if necessary. |
| 19. | Replace o-ring, if necessary. |
| 20. | Replace the locking pin and reseal the fire extinguisher. |
| 21. | Check the valve opening for powder or any foreign matter. |
| 22. | Refill extinguishers, if needed. |
| 23. | Empty and Recharge all stored pressure-loaded stream fire extinguishers. |
| 24. | For dry extinguishers, fluff the powder by turning the unit. |
| 25. | Clean the extinguisher shell with spray cleaner. |
| 26. | Return the hose to its proper position. |
| 27. | Check the condition of the hose/horn retention band at the side of the extinguisher. |
| 28. | Check that the unit’s classification is properly identified with the appropriate decal. |
| 29. | Check that the operating instructions are clean and legible. |
| 30. | Tag the extinguisher properly. |
| 31. | Survey the hazard area to verify that the unit classification corresponds with the hazard. |
| 32. | Check that the unit is properly located within the normal path of travel, at a conspicuous height. |
| 33. | Check that the unit is visible and unobstructed. |
| 34. | Insure label is in place and legible. |
| 35. | Replace the extinguisher on its hanger. |
| 36. | Ensure extinguisher inventory information is accurate, document the inspection, and provide a legible written summary to the district. |

| 2. | Scope of Work (Corresponding Bid Section) |
| --- | --- |

| A. | Annual Inspection Services (Bid Section A) |
| --- | --- |
|  | Work to be performed shall comply with all requirements of the most current NFPA regulations and minimum requirements of the Kansas State Fire Marshal. Work is to include, but not be limited to: |

| - | Inspection for physical damage. |
| --- | --- |
| - | Inspection of rivets for damage. |
| - | Inspection of handles for damage. |
| - | Inspection of hoses and/or nozzles for damage. |
| - | Inspection of pressure valve for proper pressure and proper function. |
| - | Replacement of all pull pin seals. |
| - | Replacement of all fire extinguisher tags. |

| B. | Requirements for Fire Extinguisher Maintenance: (to be performed during the annual inspection and maintenance process) (Bid Section B) |
| --- | --- |
|  | Used-up and/or non-functioning fire extinguishers shall be refilled and/or repaired, properly tagged and recertified for use upon discovering during the annual inspection and maintenance process. Fire extinguishers removed from service for maintenance or recharging shall be temporarily replaced by a fire extinguisher suitable for the type of hazard being protected and shall be of at least equal rating. Replacement fire extinguishers shall be obtained as available and applicable from Shawnee Mission School District surplus stock. For all extinguishers that undergo maintenance that includes internal examination, or have been recharged, the following shall be done |

| - | Installation of the verification of service collar. |
| --- | --- |
| - | Installation of new inspection ring or metallic label with tagging to include the month and year of the inspection, name or initials of person performing the maintenance, and name of agency performing the maintenance. |

| C. | Six Year Inspections for Dry Chemical and Halon Units (Bid Section C) |
| --- | --- |
|  | Work to be performed shall comply with all requirements of the most current NFPA regulations and minimum requirements of the Kansas State Fire Marshal. Work shall include, but not be limited to: -; Emptying of affected units.. -; Visual inspection of units for any damage and/or wear, to include the inside of the units.. -; Replacement of “O”rings.. Any extinguishers manufactured prior to October 1984 shall be removed from service at the next scheduled 6 year inspection, or next scheduled hydrotest, whichever comes first. |

| D. | Five-Year Hydro Test for CO2 and K-Class Units (Bid Section D) |
| --- | --- |
|  | Work to be performed shall comply with all requirements of the most current NFPA regulations and minimum requirements of the Kansas State Fire Marshal. Any extinguishers manufactured prior to October 1984 shall be removed from service at the next scheduled hydrotest, or scheduled 6 year inspection, whichever comes first. |

| E. | Twelve-Year Hydro Test for Dry Chemical and Halon Units (Bid Section E) |
| --- | --- |
|  | Work to be performed shall comply with all requirements of the most current NFPA regulations and minimum requirements of the Kansas State Fire Marshal. Any extinguishers manufactured prior to October 1984 shall be removed from service at the next scheduled hydrotest, or scheduled 6 year inspection, whichever comes first. |

| F. | a) | Class K Extinguishers (Bid Section F) |
| --- | --- | --- |
|  | b) | Replace any Class K fire extinguishers manufactured after January 1, 2002 that are equipped with extended wand-type discharge devices. Fire extinguishers installed prior to June 30th, 1998 for the protection of cooking appliances that use combustible cooking media shall not require replacement. Replacement shall be completed with prior consent/authorization of the School District. ## Review Suitability of Extinguisher for Possible Replacement (Bid Section F) ## Determine class of extinguisher and determine if it is suitable for the combustible loading present. Replace with appropriate class of extinguisher as required, with prior consent/authorization of the School District. Any obsolete fire extinguishers as defined by NFPA 10 shall be replaced with a fire extinguisher of the appropriate class for the combustible loading present, with prior consent/authorization of the School District. |

| G. | Trip Fee/Stop Charge (Bid Section G) |
| --- | --- |
|  | Include consideration for all trip fees/stop charges into the unit cost prices for the annual inspection services indicated on the bid form. A trip fee/stop charge will not be applicable for any service work conducted during the annual inspection services portion of the contract. Trip fee/stop charges will be applicable only for service work requested and performed during the non-inspection periods of the year. |

| 3. | Contractor Responsibilities |
| --- | --- |

| A. | Contractor shall perform a thorough examination of all fire extinguishers to ensure that all equipment will operate safely, effectively, and will be in compliance with all the guidelines set by the various government regulatory agencies. |
| --- | --- |
| B. | Contractor shall ensure that all portable fire extinguishers are fully inspected, tested, tagged, and recharged to function and be operational when needed at all times. |
| C. | Contractor shall provide certified technicians with skills, knowledge, equipment, servicing manuals, proper type of tools, recharge materials, lubricants, expellant, and manufacturer’s recommended replacement parts specifically listed for use in repair and maintenance of fire extinguishers. |
| D. | Fire Extinguishers Annual Inspection |

| i | Contractor shall verify that each portable fire extinguisher is in good operating condition and fully recharged. The Contractor shall provide hydrostatic testing as needed. Each inspection shall provide a thorough examination of the basic elements of a fire extinguisher, including but not limited to, the following: |
| --- | --- |

| a. | All necessary mechanical parts. |
| --- | --- |
| b. | Extinguishing agent of both cartridge and cylinder-operated dry chemical. |
| c. | Expelling means of all extinguishers. |
| d. | Weight of all carbon dioxide and halogenated fire extinguishers as required by the manufacturer. |
| e. | Gauge pressures shall be in operable range. |
| f. | Nozzles, discharge valves, and hoses shall be unobstructed and lock pins shall be in place. |

| ii | Contractor shall remove tamper seal on all rechargeable fire extinguishers by operating the pull pin or locking device. After the applicable maintenance procedures are completed, the Contractor shall install a new tamper seal. |
| --- | --- |
| iii | Contractor shall recharge dry chemical portable fire extinguishers if gross weight is less than manufacturer’s recommendations. |
| iv | Contractor shall fill Halon type portable fire extinguishers only with prior approval of the school district representative. |
| v | If the Contractor discovers a fire extinguisher has been discharged due to an emergency or accident during the annual inspection, the Contractor shall re-fill the extinguisher with the appropriate material. |

| vi | Contractor shall provide a copy of the annual inspection to the School District. The inspection shall include the following information: |
| --- | --- |

| a. | Maintenance dates and the initials of the person or vendor performing the inspection. |
| --- | --- |
| b. | The date when last recharged and the name of person or vendor performing the recharge. |
| c. | The hydrostatic retest date and the name of person or vendor performing the hydrostatic test. |
| d. | Description of dents remaining after passing a hydrostatic test. |
| e. | The date of the six-year maintenance for stored pressure dry chemical and halogenated agent types. |

| E. | Six Year Maintenance and Hydrostatic Testing |
| --- | --- |

| i | Contractor shall test all fire extinguishers as required by the six year maintenance date or hydrostatic testing date at time of service. |
| --- | --- |
| ii | Contractor shall be responsible for exchanging all fire extinguishers that require six year maintenance or hydrostatic testing. |
| iii | Recharging of Fire Extinguishers |

| a. | The extinguishing agent shall be completely discharged, valve assembly removed, o-ring replaced or lubricated, threads and sealing surfaces cleaned, container emptied and then filled with proper (free-flowing) agent, pressurized, sealed and locked. |
| --- | --- |
| b. | Contractor shall replace expellant cartridge as required on dry chemical units. |
| c. | Contractor shall follow the recommendations of the manufacturer when recharging any fire extinguisher. |
| d. | After recharging a fire extinguisher, Contractor shall perform a leak test on stored-pressure and self-expelling types of fire extinguishers. |
| e. | Fire extinguishers in need of recharging shall have a “Verification of Service” collar located around the neck of the container. The collar shall not interfere with the operation of the fire extinguisher. The “Verification of Service” collar shall include the month and year the service was performed. |
| f. | Recharge date shall be marked on tag. Testing shall be in accordance with ANSI/UL 77 and ANSI/UL 299, and NFPA 10-2007. |

| iv | Hydrostatic testing shall be performed by persons trained in pressure testing procedures and the Contractor shall employ proper safeguards, suitable testing equipment, facilities, and appropriate service manuals. |
| --- | --- |
| v | Each fire extinguisher shall be subject to the hydrostatic testing interval as outlined by the NFPA. |

| vi | Contractor shall maintain and record information on the inventory summary for each cylinder tested. High-pressure cylinders that pass the hydrostatic test shall be stamped with the re-tester’s identification number, month and year, or the retest per requirements. |
| --- | --- |
| vii | Fire extinguisher cylinders of the low-pressure type that pass a pressure hydrostatic test shall have the following information recorded on inventory summary: |

| a. | Month and year the test was performed. |
| --- | --- |
| b. | Test pressure used. |
| c. | Name and initials of the person performing the test. |

| viii | When the applicable maintenance procedures are performed, during periodic recharging or hydrostatic testing, the six year requirement shall begin reset from that date. |
| --- | --- |

| F. | Twelve Year Hydrostatic Test |
| --- | --- |

| i | Every six years, fire extinguishers that require a twelve year hydrostatic test shall be emptied and subject to the applicable maintenance procedures. The removal of agent from fire extinguishers shall only be done using a listed closed recovery system. |
| --- | --- |

| G. | Fire Extinguisher Service Maintenance and Repair |
| --- | --- |

| i | Contractor shall provide on-call repair services. Contractor shall provide School District a written estimate and receive approval prior to commencing repair or services. |
| --- | --- |
| ii | Contractor’s technicians shall perform maintenance and repair of portable fire extinguishers as needed in accordance with the manufacturer’s published service procedures and using only refill extinguishing agents listed on the container or as recommended by the manufacturer. |
| iii | Contractor shall immediately notify the School District representative if a fire extinguisher unit has been used or needs total replacement. |
| iv | Contractor shall furnish all repair and replacement parts including but not limited to lock pins, nozzles, valves, seals, o-rings, nitrogen cylinders, extinguishing agents, hoses, and adapters. These parts shall be in accordance to the manufacturer’s published requirements. Instruction labels are to be replaced as needed during inspection. |
| v | The Contractor shall perform repair services at the School location. In the event the unit needs to be repaired or serviced at the Contractor’s facility, the Contractor shall provide a temporary, like kind replacement for any fire extinguisher that must be removed from the School for repair purposes. Temporary replacement fire extinguishers shall be obtained as available and applicable from Shawnee Mission School District surplus stock. |

| H. | Fire Extinguisher Tags |
| --- | --- |

| i | Contractor shall remove all expired tags. When existing inspection tags are replaced, the Contractor shall attach Fire Marshall approved labels or tags imprinted with the company’s name, address, telephone number, and month and year maintenance was performed on each extinguisher. This tag shall identify the person performing the service, indicate if recharging was performed, and show the date the test was completed. The month and year the test was performed shall be indicated by hole punch. |
| --- | --- |
| ii | All inspection tags are to be all weather type tags and shall be provided at the cost of the Contractor. |

| I. | Parts and Material |
| --- | --- |

| i | A published list price for all parts and materials shall be submitted with any applicable Contractor’s invoice. Contractor shall provide written estimate of the required part(s) and material(s) to the School District for approval before replacement. All replacement parts shall be invoiced at the listed rates, less sales tax. |
| --- | --- |
| ii | The Contractor assures that all parts and materials provided are new, first rate quality, in good condition, or the latest improved models of parts or materials in current production, as offered to commercial trade capable of safety and effectively satisfying the requirements of this Contract. |
| iii | Contractor agrees not to use parts that are used, shop worn, demonstrator and prototype, reconditioned, or a discontinued model. |
| iv | Contractor agrees to maintain an adequate supply or be able to obtain within a reasonable amount of time any necessary replacement parts/materials in order to perform repairs and maintenance in a timely manner. |
| v | Contractor shall supply a warranty/guarantee covering all workmanship and labor (free of charge) on repairs for a period of one year, commencing on the acceptance date. |

| J. | Service Reports |
| --- | --- |

| i | Contractor shall supply the School District with a comprehensive report summary listing all fire extinguishers that were inspected, recharged, serviced or repaired. The report shall include the size, type, serial number of the fire extinguisher’s unit, brand, type of work performed, and date of next scheduled service. |
| --- | --- |
| ii | Upon completion of any inspection, the Contractor shall identify and submit to the School District, a written report of any deficiencies discovered in the fire extinguisher’s existing efficiency. The report shall include the fire extinguisher’s performance deficiency, type capacity, serial number, and location of the deficient units. |

| K. | Additional Requirements |
| --- | --- |

| i | All work shall be coordinated and approved by the School District. In the event additional work is required, Contractor shall provide the School District with a written estimate for review and approval prior to commencing the work. |
| --- | --- |
| ii | Contractor shall conduct all services provided under this bid in good quality and professional manner. |
| iii | Contractor shall cooperate with School District security procedures. |
| iv | Contractor shall make provisions to accomplish the service without undue interference with the school operations. |
| v | To safeguard both life and property, the Contractor shall provide to the School District a list of all chemicals to be used on-site, along with a copy of the Material Safety Data Sheet (MSDS) for all chemicals used. |

| L. | Liability for Loss and Damages |
| --- | --- |

| i | Any damages by Contractor, their personnel, subcontractors, and other service providers through this bid, including equipment, furniture, materials, or other property, shall be repaired or replaced by Contractor to the satisfaction of the School District at the Contractor’s expense. The School District, at its option, may repair any such damage and deduct the cost thereof from any sum due Contractor under this Agreement. |
| --- | --- |

| 4. | Requirement for Documentation |
| --- | --- |
|  | Contractor to provide and maintain an inspection form in an electronic, editable format acceptable to the owner for each school. This form shall be developed by the contractor and approved by the school district and shall be the property of the school district. The inspection form shall be kept current with the most recent edition of NFPA 10 and shall include the following minimum information: -; School/building name and address.. -; Date of inspection and/or service.. -; Description of each fire extinguisher including:. - brief description of location in building. - size. - class. - brand. - serial #. - manufacture date. - last date that maintenance was performed. - next 6 year maintenance due date. - next test due date. |

| 5. | Work Timeline and Renewal Terms: |
| --- | --- |
|  | The inspection process timeline will begin on or about June 2, 2019 and is to be completed no later than August 8, 2019. This will be considered a one-year contract for inspection and maintenance service, with the option to renew annually in subsequent years. This renewal will be based on the satisfaction of the Shawnee Mission School District and its evaluation of the service and performance provided for the preceding year. Annual adjustments to the contract (addition/subtraction) based on the district’s total extinguishers inventory will be made according to the unit price of each extinguisher type as outlined in the bid document. The School District will allow a maximum CPI increase each year. This contract will not be renewed for any subsequent year if the performance is considered unsatisfactory. The vendor will be notified in writing 90 days prior to each year’s renewal date (which will be considered as June 1 of each year) if the contract will not be renewed. |

| 6. | Materials and Workmanship: |
| --- | --- |
|  | All materials unless otherwise specified shall be new and free from any defects representing the highest quality of its kind. Manufactured articles, materials, and equipment shall be applied, installed, connected, erected, used, cleaned, and adjusted accordingly to manufactured specification of relevant use of equipment in a particular application. |

| 7. | Safety: |
| --- | --- |
|  | Contractor shall, at its own cost and expense, take all reasonable safety precautions with respect to its performance under this Contract. Minimum compliance will comply with the Safety Program of Shawnee Mission School District, applicable laws, regulations and ordinances, including federal, state and local occupational safety and health acts, right to know laws and hazardous communication standards. |

| 8. | Building Locations and Current Estimated Quantities |
| --- | --- |
|  | Attached is a list of school district facilities that shall receive inspection and maintenance services. The list includes addresses and an estimated number of fire extinguisher units at each building. Please note that the actual numbers in each building may vary slightly from the numbers identified. The most recent inventory of extinguishers for each applicable building is available for review by the prospective bidders. Please contact Alan Menn at 913-993-8505 to arrange for a time to review the inventory. This inventory is available for review at the Operations & Maintenance Building, 6445 Carter Ave, Merriam, Kansas 66203. |

| 9. | Service Hours |  |
| --- | --- | --- |
|  | A. | Services shall be provided Monday through Friday, 7:00 a.m. – 2:30 p.m. or as mutually scheduled upon by both parties and excluding observed holidays. Each site inspection shall be scheduled with the School District Representative, at least two (2) working days in advance. |

| 10. | School District Representatives |  |
| --- | --- | --- |
|  | A. | School District representatives during the initial term of this Agreement will be: C. Alan Menn Secretary, Operations & Maintenance Judd Remmers Custodial Supervisor |

| 11. | Other Requirements and Considerations |
| --- | --- |

| A. | Personnel Identification and Security Requirements |
| --- | --- |
|  | The awarded contractor is required to adhere to the following security requirements. -; Technicians must wear an easily identifiable shirt with company logo and report to the custodian at each school upon arrival.. -; Company vehicle shall be clearly marked with the company logo.. |
| B. | NFPA/State Fire Marshal Office Certification |
|  | All technicians performing inspections, testing, and/or maintenance shall meet minimum certification requirements as required by the NFPA and/or the Kansas State Fire Marshal. Copies of NFPA and/or Kansas State Fire Marshal certification is to be provided with each submitted bid. |

*Please note:

The following new locations are to be included/added to the updated inspection/inventory as an inclusion to this contract.  The new Operations and Maintenance Facility inventory numbers will vary and include fleet vehicles.

Career & Technical Campus

11475 W. 93rd St.

Overland Park, KS

Center for Academic Achievement

8200 W. 71st St.

Overland Park, KS

Lenexa Hills Elementary

8651 Haven St.

Lenexa, KS

Operations & Maintenance Facility

6445 Carter Ave.

Merriam, KS