| Send emailed bid response to: beckycollins@smsd.org Shawnee Mission Unified Schools Purchasing Department 8200 W. 71st Street Shawnee Mission, Kansas 66204 | DATE: May 19, 2020 BID NO. 20-008 BID TITLE: REPLACEMENT STAIR LIFT at EAST ANTIOCH ELEMENTARY Bids will be accepted until and then publicly opened on: Date: JUNE 2, 2020 Day: TUESDAY Time: 2:00 p.m. CST EMAIL BIDS TO: beckycollins@smsd.org Terms, conditions and specifications under which bids are requested are included. Please review thoroughly. |
| --- | --- |

You are invited to bid on Replacement Stair Lift at East Antioch Elementary for the Shawnee Mission Unified Schools per the enclosed terms, conditions and specifications, F.O.B. Destination, Freight Prepaid and Add.  FREIGHT COSTS MUST BE INCLUDED IN THE BID PRICE(S).

We are enclosing only one copy of the bid specifications.

AT THIS TIME ONLY EMAILED BIDS WILL BE ACCEPTED.

Unit bid price shall govern whenever a discrepancy occurs in the extended bid price on the Bid Summary page.  Bid will be awarded:  __X__ All-or-None, _____ Item-by-Item, _____ Groups of Items, or ____ Groups & by-Item.  Payment will be made ON COMPLETION of Purchase Order.  DO NOT INCLUDE SALES TAX.

Any questions regarding the specifications should be directed to Jeff Reed @ email; jeffreyreed@smsd.org.   Phone:  (913) 993-8525.   Any questions regarding the bid procedures should be directed to Alan Menn @ email: alanmenn@smsd.org, Phone: (913) 993-6474.

THIS BID IS NOT TRANSFERABLE

MANDATORY ON SITE WALK THROUGH WILL BE TUESDAY, MAY 26, 2020 AT 10:00 a.m. AT EAST ANTIOCH ELEMENTARY, 7342 LOWELL, OVERLAND PARK, KS  66204

Bidders shall hold all bid prices firm for acceptance for 90 calendar days after date of bid opening.

Bid results will be posted on the smsd.org website within approximately 5 working days after the bid opening.  Go to About; Departments; Purchasing/Bidding; Bids and Bid Summaries.  Additionally, you may review the bid results in the Purchasing Office during the hours of 8:00 AM to 4:30 PM.

NOTICE OF “NO RESPONSE FORM”

BID NO.  20-008

VENDORS WHO RESPOND TO THIS INVITATION

WITH A COMPLETED NOTICE OF “NO RESPONSE” FORM

SHALL REMAIN ON OUR MAILING LIST, IF REQUESTED.

VENDORS MAKING NO RESPONSE AT ALL

MAY BE REMOVED FROM OUR MAILING LIST.

Dear Vendor:

Please check () the appropriate box below, complete the remainder of this form and return it NO LATER THAN the scheduled Bid/Proposal/or Quote Date and Time.

Our company cannot provide the products, supplies and/or services listed in this bid, proposal or

quote.  Please MOVE our name and address to the following category(ies) so that we may bid at a later date. ______________________________________________________________________________

______________________________________________________________________________

We have chosen NOT to submit a response at this time, but would like to remain on your bid list

for this product category.  We did not submit a response because:

Reason(s): _____________________________________________________________________

______________________________________________________________________________

Please REMOVE our name from all SMSD bid lists until further notice.

Reason(s): _____________________________________________________________________

______________________________________________________________________________

COMPANY NAME:  __________________________________________________________

REPRESENTATIVE (please print):______________________________________________

ADDRESS:  _____________________________________   PHONE (_____) ______________

AUTHORIZED SIGNATURE: __________________________________________________

TITLE:  ______________________________________    DATE:  ______________________

PLEASE RETURN THIS FORM ONLY TO:

Shawnee Mission Unified School District #512

Purchasing Department

Notice of “NO RESPONSE”

8200 W. 71st Street

Shawnee Mission, KS  66204

OR

Fax to:  913/993-6225

BID No.   20-008

# SHAWNEE MISSION PUBLIC SCHOOLS

8200 W. 71st Street

SHAWNEE MISSION, KS  66204

5% BID SECURITY FORM

If the bid for this project is equal to or greater than $10,000, bid security is required.

Bid Security issued to:  Shawnee Mission Public Schools, in the amount of 5% of the total amount of your Bid shall accompany your Bid as a guarantee that, if awarded all or part of the Bid, your firm will enter into contract to complete the work per the Bid Specifications.  Cashier checks and certified checks should be made payable to Shawnee Mission USD #512.

If the firm awarded the Bid defaults in entering into a contract for the execution of the work specified, the Bid Security will become the property of the School District.  Bids not accepted within ninety (90) days after the time set for submission will have their Bid Securities returned.

PLEASE NOTE:  Should you submit a cashier check or certified check instead of a bid bond; the following steps will be used by SMSD in the handling of that check:

- SMSD will deposit your check into a SMSD bank account within 2-3 days after bid opening.

- Within four (4) weeks after board approval of the bid, a district check shall be mailed to the non-successful bidder(s) to reimburse them for the exact amount of their cashier/certified check.

- Within four (4) weeks after the completion of a formal written and properly signed contract, or the issuance of a SMSD purchase order, a district check shall be mailed to the successful bidder(s) for the exact amount of their cashier/certified check.

NOTE:	IF BID SECURITY IS NOT ENCLOSED WITH THE BID, IT WILL BE CAUSE FOR REJECTION OF THE BID.

|  |  | $ |
| --- | --- | --- |
| ## Company |  | ## Amount of Total Bid |
|  |  | ## $ |
| ## Address |  | ## Amount of Bid Bond |

Bid Security attached to this form.  (Please send the two together.)

| ## Signature of Authorized Representative |  | ## Phone |
| --- | --- | --- |
| ## Please Print Name |  | ## Position |

BID FORM

## BID No.  20-008

BID OF:

A CORPORATON ORGANIZED AND EXISTING UNDER THE LAWS

OF THE

A PARTNERSHIP CONSISTING OF

PARTNERS:

OR:	A SOLE PROPRIETOR; HERINAFTER CALLED THE BIDDER.

TO:	EMAIL – beckycollins@smsd.org

The undersigned acknowledges that he has received and familiarized himself with the following:

Request for Bid for Stair Lift at East Antioch Elementary

Location:  7342 Lowell, Overland Park, KS  66204

Shawnee Mission Public School District #512

Bid Number 20-008

ADDENDA NO(s):	 Received

The undersigned further acknowledges that he has familiarized himself with local conditions affecting the cost of the work at each place where the work is to be done.

In submitting this bid, the undersigned agrees:

| 1. | To furnish all material, labor, tools, expendable equipment, permits, supervision and all utility and transportation services necessary to perform and complete, in a workmanlike manner, all of the work required in accord with the bid documents. |
| --- | --- |
| 2. | To hold his bid open for ninety (90) days after receipt of bids and to accept the provisions of the instructions to bidders regarding disposition of bid security. |
| 3. | To commence the work upon receipt of Notice to Proceed, on or about June 1, 2020, after the approval of the Board of Education at it’s regularly scheduled meeting on May 26, 2020, and to substantially complete the work not later than July 10, 2020. If the Bidder cannot meet this schedule, please identify this in the Substantial Completion Date section of this Bid Form. |
| 4. | To accept the assessment of liquidated damages of $100 per calendar day starting the next calendar day after the indicated Substantial Completion Date and extending for seven days, and $500 per calendar day for each day starting on the eighth day after the Substantial Completion Date. See the Special Terms and Conditions included in these Bidding Documents about work times during the School Year. |
| 5. | All materials to be non-proprietary, as specified, or approval equal. |

Lump Sum Base Bid:			Dollars

($	).

(Indicate bid in both numbers and words. In the case of a discrepancy between the two, the amount shown in words shall govern.)

Alternate Bid Number One (1):____________________________________________________Dollars

($_________________________).

(Indicate bid in both numbers and words.  In the case of a discrepancy between the two, the amount shown in words shall govern.)

Substantial Completion Date:

Per the Project Schedule and the Special Terms and Conditions, the Bidder agrees to the Substantial Completion Date established in the schedule, which will also begin the assessment of liquidated damages.  Yes _____________, or No _____________.

If No is selected, please identify the Substantial Completion date that the Bidder will achieve working under the guidelines of the Special Terms and Conditions.  Bidder’s designated Substantial Completion Date is to be _________________, which will begin the assessment of liquidated damages.

In submitting this bid, it is understood that the right to reject any and all bids and to waive irregularities in the bidding has been reserved by the owner.

Date this	 day of	, 2020.

Name of Bidder

Address of Bidder

Authorize Officer

Area Code/Telephone Number

________________________________________________________________________

Email Address

Terms and Conditions

| A. | Bid Requirements and Considerations: 1. The Board of Education reserves the right to reject any or all bids, to accept any item or items in the bid, and to waive any informality in bids. 2. Each bid must be completed on SMSD bid forms. 3. Alternate bids will be considered only if the alternate properly meets specifications outlined in the bid. 4. Each bid shall be accompanied by bid security in the amount of five percent (5%) of the base bid, made payable unconditionally to the school district. This security will be submitted as evidence of good faith as a guarantee that, if awarded the contract, the bidder will execute required bonds and insurance within ten (10) days after receipt of Notice to Proceed. 5. Each bidder shall carefully examine the bidding documents and thoroughly inform himself with all requirements prior to submitting a bid. Should a bidder find discrepancies or ambiguities in, or omission from bidding documents, or should he be in doubt as to their meaning, he will at once and at least three days prior to bid date, notify the school district. Any subsequent addenda sent to bidders will become part of the contract documents. 6. Prior to submitting a bid, each bidder shall examine and thoroughly familiarize himself with all existing conditions; including applicable laws, codes, ordinances, rules, and regulations that will affect his work. Bidders shall visit the site, examine the existing conditions, and shall ascertain by reasonable means, all conditions that will in any manner affect the work. Contractors and/or bidders are required to check in with building authorities at the school immediately upon entering the school premises. 7. Prices quoted are to be free of all Federal, state, and local taxes, unless otherwise imposed by a governmental body and applicable to the work or material. The school district will obtain from the State of Kansas a sales tax exemption certificate number. The sales tax exemption certificate will permit the contractor to purchase materials for incorporation into this project without paying sales tax, provided that the contractor furnishes the certificate number to the supplier. 8. When submitting a substitute article as equal, the full name and illustrated description must be given. The Board of Education reserves the right, however, to decide upon its suitability for the intended use. Upon request, samples of substitute articles must be submitted. 9. Bids must be emailed to beckycollins@smsd.org Bids not received by appointed time by email will be rejected. 10. If bid is accepted, USD #512 must be supplied with seller’s employer identification number of social security number, per IRS regulations. 11. Each contractor is responsible for his/her own worker’s compensation and liability insurance coverage. Shawnee Mission Unified School District #512 assumes this COVERAGE IS INCLUDED IN THE PRICE OF EACH BID TOTAL. 12. Any catalog, brand name or manufacturer’s reference used herein is intended to be descriptive and not restrictive. Offers on any reputable manufacturer’s regularly produced product which is similar and substantially equivalent will be considered. SMSD reserves the right to make final decisions as to the acceptability of comparable items. 13. Vendors who do not bid, but wish to remain on our bid list, should notify the Shawnee Mission USD #512 Purchasing Department in writing using the enclosed “Notice of No Response” form. Failure to do so may result in removal from this list. 14. If required by the bid form, the contractor shall submit with his bid a list of subcontractors and other persons or organizations that will perform work on this project. |
| --- | --- |
| B. | Form and Requirements of the Contract: |
|  | 1. The form of contract will be a Purchase Order issued by Shawnee Mission School District. In submitting his bid for consideration, each bidder agrees to commence work as soon as practical upon receipt of the school district purchase order and subsequent execution of applicable bonds and certificates of insurance. 2. The district shall not be responsible for any goods delivered or services performed without its purchase order signed by an authorized representative of the Purchasing Department. 3. The contractor shall not commence work under this contract until he has obtained the owner’s approval of a certificate of insurance providing evidence that he has obtained all the insurance required under this section, at least equal to the limits set forth hereinafter, with an insurance company acceptable to the owner. All policies shall provide for ten (10) days written notice to the owner prior to effective date of any changes affecting the policy. Two copies of the certificate of insurance in a form acceptable to the owner shall be delivered to the owner. The contractor shall not allow any subcontractor to commence work until the subcontractor has obtained insurance coverage similar to that required of the contractor. 4. For projects with a value of $20,000 or more; subsequent to award, the contractor shall furnish Performance Bond, Labor and Materials Payment Bond, and Kansas Statutory Bond covering the faithful performance of the contract and the payment of all obligations arising thereunder. All such bonds shall be submitted to the school district prior to the commencement of any contract work. 5. Contracts entered into on the basis of submitted bids are revocable if contrary to law. 6. The laws of the State of Kansas shall govern any contracts resulting from this bid. Actions must be filed in the Johnson County Courthouse in Johnson County, Kansas. 7. The seller shall provide the standard patent infringement indemnity clause which shall hold and save the Board of Education and its officers, agents, servants, and employees, harmless from liability of any patented or unpatented invention, process, article, or appliance manufactured, or used, in the performance of the contract, including its use by the Board of Education. |
| C. | General Work Requirements. |
|  | 1. The contractor will be required to start the work per the schedule included herein. Liquidated damages as stated on the bid form will be assessed for each consecutive calendar day which the work is not substantially complete, beginning with the first day beyond the substantial completion time stated. Substantial completion is the owner’s ability to utilize the facility for its intended purpose. Shawnee Mission Public Schools will be the sole judge of substantial completion. 2. The owner reserves the right and may delay work if scheduling between school administration and contractor cannot be resolved. 3. It will be the contractor’s responsibility to have the approaching licenses and permits required by the state and/or municipality in which the work will be performed. It is also the contractor’s responsibility to make certain all work and material meets local and state codes. Bidders shall include permit fees in their bid. 4. The contractor shall observe and comply with all ordinances, laws, and regulations, and shall protect and indemnify the owner against any claim or liability arising from or based on any violation of the same. The contractor shall comply with all regulations of agencies having jurisdiction with respect to sanitation and safety during construction. 5. All items shall be new and unused, unless otherwise specified by the district, and in first class condition. 6. Contractor shall be responsible for protection of the adjacent spaces during all phases of the project, demolition material storage and new construction. 7. All items furnished must be of their respective kinds, and will be free from defects in material and workmanship. Items will be subject to our inspection and approval at any time. Items furnished must be manufactured in compliance with all existing legal or governmental directives. 8. All work shall be of the highest quality. The contractor and subcontractor shall check their work regularly for quality and conformance as the work is in progress. Unsatisfactory work shall be corrected immediately. 9. The contractor shall promptly correct work rejected by the owner or failing to conform to the requirements of the contract documents, whether observed before or after substantial completion and whether or not fabricated, installed or completed. The contractor shall bear all costs of correcting such rejected work, including additional testing and inspections and compensation for owner services and expenses made necessary thereby. 10. As work is completed by the contractor/subcontractor, it shall be his responsibility to remove all excess material, equipment and debris from the premises. 11. Upon substantial completion, a scheduled punchlist inspection shall be conducted by the school district to identify any item(s) requiring additional work. All items noted on the punchlist shall be accomplished by the contractor prior to final payment. |

| D. | Miscellaneous Requirements |
| --- | --- |
|  | The law requires that Section 1 through 5 of KSA 44-1030 (as follows) are to be included in all contracts to which our agency is a party: Except those with contractors, vendors or suppliers whose cumulative dollar total in any fiscal year is $5,000.00 or less, or who have fewer than four (4) employees: 1. The contractor shall observe the provisions of the Kansas act against discrimination and shall not discriminate against any person in the performance of work under the present contract because of race, religion, color, sex, physical handicap unrelated to such person’s ability to engage in the particular work, national origin or ancestry; 2. In all solicitations or advertisements for employees, the contractor shall include the phrase, “equal opportunity employer” or similar phrase to be approved by the commission; 3. If the contractor fails to comply with the manner in which the contractor reports to the commission in accordance with the provisions of KSA 1976 Supp .44-1030, as amended, the contractor shall be deemed to have breached the present contract and it may be canceled, terminated or suspended, in whole or in part, by the contracting agency; 4. If the contractor is found guilty of violation of the Kansas act against discrimination under a decision or order of the commission which has become final, the contractor shall be deemed to have breached the present contract and it may be canceled, terminated or suspended, in whole or in part, by the contract and it may be canceled, terminated or suspended, in whole or in part, by the contracting agency; and 5. The contractor shall include the provisions or paragraphs one (1) through (4) inclusively of this subsection (a) in every subcontract or purchase order so that such provisions will be binding upon such subcontractor or vendor. |
| E. | Payments to the Contractor: |
|  | In order for payment to occur on the “Payment Release Date”, the vendor’s INVOICE and the “BLUE” receiving copy of the Shawnee Mission purchase order must be received into the Business Office by the school cut-off date (preferably earlier) so that sufficient time is allowed for the payment to actually be processed through the Accounts Payable system. INVOICES MUST BE SUBMITTED TO THE APPROPRIATE PROJECT MANAGER FIVE DAYS PRIOR TO THE SCHOOL CUT-OFF DATE. SUBMIT INVOICES TO THE PROJECT MANGER AT THE OPERATIONS & MAINTENANCE OFFICE NAD NOT TO THE McEACHEN OFFICE. |

CONTRACTOR AND VENDOR CODE OF CONDUCT

Shawnee Mission School District requests that all contractor and vendor employees conduct themselves in an acceptable manner while performing work on school district property.  The following items are prohibited on school district properties:

- Physical or verbal contact with students or non-designated staff.

- All school district properties are tobacco free.  All tobacco, including smokeless tobacco, is prohibited.  There are no designated areas for tobacco use.  Contractors are required to post no tobacco signs.  Smoking will not be permitted inside private vehicles which are on school district property.  Workers may be required to sign a consent form acknowledging no tobacco use on the property.  Violators may be required to leave the work site.

- Drugs and/or alcohol consumed or present on district properties.

- Firearms and hunting items.

- Foul or abrasive language.

Additionally, all workers shall wear appropriate clothing on all parts of the body.  All workers shall utilize areas for vehicle access and parking, material storage, etc.  All workers shall wear nametags identifying their name and the name of the company they are representing.

INSURANCE REQUIREMENTS

| A. | Worker’s Compensation Insurance: Worker’s Compensation and Employer’s Liability Insurance as required by law to cover fully all employees. |
| --- | --- |
| B. | Bodily Injury and Property Damage Insurance: A comprehensive general bodily injury and property damage policy, including automobiles, covering the work to be performed. The policy shall be written to provide damage arising from one accident, with not less than $1,000,000 aggregate damages to, or destruction of property during the policy period; except, in case of automobile damage coverage, the minimum provided shall be not less than $1,000,000 bodily injury and $1,000,000 property damage per accident for any vehicle used on the project, whether owned, hired or nonowned. |
| C. | Special Insurance: Contractor for General Construction work shall take out and maintain insurance providing a minimum coverage of $1,000,000 for the following hazards: |
|  | Where the work to be performed involves excavation or other underground work or construction, the property damage insurance provided shall cover all injury to or destruction of property below the surface of the ground, such as wires, conduits, pipes, mains, sewers, etc., caused by the contractor’s operations, or injury to or destruction of property above or below ground resulting therefrom. Property damage insurance shall also cover the collapse of, or structural injury to, any building or structures on or adjacent to the owner’s premises, or the injury to or destruction of equipment and/or property resulting therefrom, caused by the removal of other buildings, structures, or supports, or by excavation below the ground, where the construction of a new structure or the demolition of any existing structure involves any of the foregoing designated hazards and in all cases where the contract provides for alterations in, additions to, or the underpinning of, and existing structure or structures. |
| D. | Subcontractor’s Insurance: If a part of this contract is sublet, the contractor shall either cover any or all subcontractors in his insurance policies; or require each subcontractor to secure insurance which will protect him against all applicable hazards not covered by the contractor’s insurance. |
|  | Certificate and Maintenance of Insurance: The contractor shall submit two (2) copies of Certificate of Insurance to the owner. The required insurance shall be maintained in force until the project is completed. |

|  | INVOICES MUST BE SUBMITTED TO THE APPROPRIATE PROJECT MANAGER AT LEAST FIVE DAYS PRIOR TO THE SCHOOL CUT-OFF DATE (preferably earlier) SHAWNEE MISSION PUBLIC SCHOOLS. ACCOUNTS PAYABLE SCHEDULE. School; Payments. Cut Off; Released. 2/14/2020; 2/25/2020. 3/6/2020; 3/24/2020. 4/17/2020; 4/28/2020. 5/14/2020; 5/27/2020. 6/12/2020; 6/23/2020. |
| --- | --- |

____________________________________________________________________________________

SCOPE OF WORK

Base bid will consist of removal from property one (1) located at East Antioch Elementary, 7342 Lowell, Overland Park, KS  66204, incline wheelchair lift, (see attached site drawing) and replace with one (1) new incline wheelchair lift as specified in this document.

SECTION 14 42 13

INCLINE WHEELCHAIR LIFT

** NOTE TO SPECIFIER **  Garaventa Lift; Incline Wheelchair Lifts.

This section is based on the products of Garaventa Lift, which is located at:

United States

P.O. Box 1769

Blaine, WA 98231-1769

Canada

7505 134 A St.

Surrey, BC V3A 3WB

Toll Free: 800-663-6556

Tel:  (604) 594-0422

Fax:  (604) 594-9915

Email: productinfo@garaventalift.com

Web: www.garaventalift.com

[click Here] for additional information.

Garaventa Lift is an international company specializing in the manufacturing of wheelchair lifts and elevators. A world leader in the accessibility industry with a reputation for reliability, safety and innovation, Garaventa Lift has over 50,000 installations worldwide.

Introduced in 1979, the Garaventa Stair-Lift was the first inclined platform wheelchair lift in North America capable of travel along straight or curving stairways, up several flights of stairs and across horizontal landings.  This flexibility, and the most experienced design team in the industry, allows Garaventa Lift to solve difficult accessibility issues.

The GSL Artira was introduced in 2001 and features a computer based control system, and Smart-Lite technology, making it the easiest lift on the market to use.

  - SUBMITTALS

    - Product Data:  Manufacturer's data sheets on each product to be used, including:

      - Submit manufacturer's installation instructions, including preparation, storage and handling requirements.

      - Include complete description of performance and operating characteristics.

    - Shop Drawings:

      - Show typical details of assembly, erection and anchorage.

      - Show complete layout and location of equipment, including required clearances.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications:	Firm with minimum 10 years documented experience in manufacturing of inclined wheelchair platform lifts of installations of type specified.

    - Installer Qualifications:  Firm licensed to install equipment of this scope, with evidence of experience with specified equipment.  Installer shall maintain an adequate stock of replacement parts and have qualified people available to ensure timely maintenance and callback service at the project site.

  - REGULATORY REQUIREMENTS

** NOTE TO SPECIFIER **  Edit and delete one of the two following paragraphs to suit local requirements.  First paragraph is for installations in the United States.  Second paragraph is for installations in Canada.

    - Provide platform lift in compliance with:

      - ASME A18.1 - Safety Standard for Platform Lift and Stairway Chairlift.

      - ASME A17.5 - Elevator and Escalator Electrical Equipment.

      - NFPA 70 - National Electric Code.

    - Provide platform lift in compliance with:

      - CSA B355 - Lifts for Persons with Physical Disabilities.

      - CSA B44.1/ASME A17.5 - Elevator and Escalator Electrical Equipment.

      - CSA - National Electric Code.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer's unopened packaging until ready for installation.

    - Store components off the ground in a dry covered area, protected from adverse weather conditions.

  - PROJECT CONDITIONS

    - Do not use wheelchair lift for hoisting materials or personnel during construction period.

  - WARRANTY

** NOTE TO SPECIFIER ** The manufacturer’s basic warranty is a limited 2 year warranty for the replacement at no cost of defective parts but does not include the labor costs required to replace the defective parts.  Warranty requires maintenance agreement during period of the warranty. Delete if not required.

    - Warranty: Provide a two-year limited warranty covering replacement of defective parts and excluding labor. Preventive maintenance agreement required.

** NOTE TO SPECIFIER **  Include the following paragraph if warranty is specified above and delete if not required. Adjust to match extended warranty period above.

  - MAINTENANCE SERVICE

    - Furnish service and maintenance for elevator system and components for the following period from Date of Substantial Completion.

      - Two years.

    - Include systematic examination, adjustment, and lubrication of elevator equipment. Repair or replace parts whenever required. Use parts produced by manufacturer of original equipment. Replace wire ropes when necessary to maintain required factor of safety.

    - Provide emergency call back service for this maintenance period.

    - Perform maintenance work using competent and qualified personnel approved by elevator manufacturer or original installer.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:  Garaventa Lift; United States - P.O.  Box 1769, Blaine, WA 98231-1769. Canada 7505 134A St., Surrey, BC V3W 7B3. ASD.

** NOTE TO SPECIFIER **  Select one of the following two primary paragraphs for Stair Lifts at Straight or Turning Stairways or Stair Lifts at Straight Stairways and delete the one not required.
 
 ** NOTE TO SPECIFIER **  The following paragraphs are for platform lifts at straight or turning stairways and where lifts serve two or more landings. Edit to suit project requirements. Indicate locations and stair and landing requirements on the Drawings.

  - STAIR LIFT FOR STRAIGHT OR TURNING STAIRWAYS

    - Lift must consist of a tubular guide rail system, a folding platform that is moved along the guide rails by a rope sprocket drive system, overspeed safety system and call stations at each landing. Conform to the following design requirements:

      - Application:

** NOTE TO SPECIFIER **  Select one of the following two paragraphs and delete the one not required.

        - Design and fabricate lifts to manufacturer’s standard for existing indoor stairways.

      - Platform Load Rating: 660 lbs. (330 kg).

      - Travel Speed:  20 fpm (101.6 mm/s), slowing to 50 percent of rated speed before entering and while rounding corners.

      - Platform Deck:  16-gauge (1.6 mm) sheet metal coated with electrostatically applied and baked anti-skid Sandex black paint.

** NOTE TO SPECIFIER **  Select the following paragraph for standard ADA compliant platform size. Delete if not required.

        - Platform Size A (ADA Compliant).

      - Platform Operation:

        - Automatic Fold:  Folded and unfolded electrically from the call station.

        - Emergency Manual Fold:  When unit is left in the open position, platform may be manually folded and retained in closed position.

      - Under Platform Obstruction Sensing:

        - Provide an under-platform sensing device to stop the platform from traveling in the downward direction when encountering 4 lbs. (1.8 kg) of pressure.

        - Platform is permitted to travel in the opposite direction of obstruction to allow clearing.

      - Passenger Restraining Arms:

        - Platform equipped with retractable passenger restraining arms in compliance with ASME A18.1a.

        - Arms stop moving when an obstruction causing 4 lbs. (1.8 kg) of pressure is encountered and will immediately retract when the signal is removed.

        - Provide with means to manually unlock and open the restraining arms for passenger emergency evacuation.

        - Arms are folded and unfolded electrically from the call stations or platform controls.

        - Top of arms mounted 37-3/8 inches (948 mm) above the platform deck. When in guarding position the arms are located above the perimeter of the platform.

        - The gaps between ends of arms shall not exceed 4 inches (100 mm).

      - Boarding Ramps:

        - Provide boarding sides of platform with retractable ramps positioned for travel at a height of 6 inches (152 mm) measured vertically above the platform deck.

        - Lock ramps in their guarding positions during travel. When the platform is at the landing, only the retractable ramp servicing the landing shall be operable.

        - Ramps shall be folded and unfolded electrically from call stations or platform.

        - Retractable ramps, in the guarded position, shall withstand a force of 125 lbs. (556 N) applied on any 4-inch (100 mm) by 4-inch (100 mm) area. This force shall not cause the height of the ramp, at any point in its length, to be less than 6 inches (152 mm) measured vertically above the platform deck.

        - Provide a means to manually unlock the ramps for emergency evacuation when platform is located at a landing.

        - Provide a bi-directional obstruction sensitive device on the travel direction end of the platform to stop lift when 1.8 kg (4 lbs.) of pressure is encountered, either from inside or outside of the platform. Platform is permitted to travel in the opposite direction of obstruction to allow clearing.

        - When platform folds, passenger restraining arms shall fold down and be covered by the folded platform.

      - Platform Kick Plate:

        - Provide non-boarding and non-guide-rail side of the platform with a kick plate barrier of not less than 6 inches (152 mm) in height, measured vertically from the platform deck.

        - When the platform is folded the kick plate shall cover the platform controls providing protection from vandalism.

      - Pedestrian Safety Lights:

        - Equip platform with amber pedestrian safety lights located at both ends of the platform to alert pedestrian traffic that the platform is on the stairway.

      - Hand Grips:

        - Equip platform with two 6-7/8-inch (174 mm) long by 1-1/4-inch (32 mm) diameter aluminum hand grips or grab bars on the front face of the platform with the top being 33-1/4 inch (845 mm) above the platform deck.

      - Clearance Dimensions:

        - When folded platform shall not protrude more than 12-5/8 inches (321 mm) to 13-5/8 inches (346 mm) from mounting surface.

        - When unfolded and in use platform shall not protrude more than 40 inches (1015 mm) to 41 inches (1040 mm) from wall.

      - Controls:

        - Platform Controls: 24 V Low Voltage type.

        - Platform equipped with emergency stop switch located within reach of the passenger 37-1/8 inches (942mm) above platform deck. When activated emergency stop button shall cause electric power to be removed from the drive system stopping lift immediately.

        - Operating controls shall be two separate 1-1/2 inches (36 mm) round constant pressure buttons with directional arrows mounted on the front surface of the platform control panel.

        - Directional buttons shall prompt the user with the available travel direction by illuminating the appropriate button.

        - When platform arrives at landing and the user releases the directional button, the passenger restraining arms and boarding ramp shall unfold automatically allowing passenger to disembark.

        - Platform shall equipped for:

** NOTE TO SPECIFIER ** Select key switch or keyless operation. Delete paragraph not required for the Project.

          - Keyed Operation

      - Platform Deck Light:  Integral lamp automatically activated when platform is in unfolded position.

      - Platform Security Lock: Provide to prevent unauthorized unfolding of the platform.

      - Attendant Handheld Pendant Control: Provide with plug-in socket on platform control panel.

** NOTE TO SPECIFIER **  Select the following paragraph when alarm is required to meet local code requirements or for remotely located lifts.

      - Platform On Board Emergency Alarm:  Provide platform with on board alarm that sounds when emergency stop button is pushed. Provide battery backup for platform on board alarm.

** NOTE TO SPECIFIER **  Select the following paragraph where required to minimize the impact of platform boarding at stairway egress width. Delete if not required.

      - Remote Platform Boarding:  Platform shall travel beyond standard boarding position to remote boarding location away from stairs. Provide with ramp extensions 3 inch (76 mm) extruded aluminum added to the boarding ramps.

** NOTE TO SPECIFIER ** Select the following paragraph where required. Delete if not required.

      - Under Hanger Sensing: Provide bottom of platform hanger with a sensing plate to stop the platform from traveling in the downward direction when encountered with 4 lbs. (1.8Kg) of pressure. It shall be possible to drive the platform away from the obstruction.

** NOTE TO SPECIFIER ** Select the following paragraph where required. Delete if not required.

      - Side of Hanger Obstruction Device: Provide a sensor that detects obstructions in the path of the side of the hanger. Lift shall stop immediately and not travel until the obstruction is removed. It shall be possible to drive the platform away from the obstruction.

    - Drive and Guide Rail System

      - Operation:

        - Motor: 2 H.P. electric motor with an integrated brake.

        - Required power: 208-240 VAC, single phase, 50/60 Hz. on a dedicated 20-amp circuit.  Rated current shall be 7 amps for operation with rated load.  Dedicated 120-240 VAC power circuit provided to the lift units by school district personnel.  Circuit rating, rough in location and final connection to be determined by the contractor chosen and coordinated with school district.

        - Locate roped sprocket drive system consisting of a motor, gearbox and PCC controller (Programmable Configuration Controller) at the upper end of the tubes. PCC controller shall be custom programmed to soft start and stop and the slow down platform travel speed for all corners and landings of the lift.  Normal operating speed shall be 20 feet per minute (6 m per minute), slowing to 50 percent of this speed before entering and while rounding corners.

        - Equip drive with an emergency manual lowering system.

** NOTE TO SPECIFIER ** Select one of the following two drive cabinet paragraphs. The first paragraph is standard and the second paragraph is a space saving option.  Delete paragraph not required for the Project.

      - Standard Drive Cabinet:

        - Cabinet: 20-1/2 inches (520 mm) wide by 41-1/2 inches (1053 mm) high by 10-5/8 inches (270 mm) deep.

        - Cabinet door is key locked and monitored with an electrical cutout safety switch.

        - Provide an integrated lockable main disconnect switch and breaker on the drive cabinet.

      - Guide Rail:

        - Construct of two 2-inch (51 mm) diameter steel tubes spaced 23-5/8 inches (600mm) apart vertically. Tubes will run parallel to the stairs and horizontal to landings throughout the length of travel.

        - When negotiating a horizontal landing a third 2-inch (51 mm) diameter steel tube shall be added to the tube system to guide and stabilize platform.

        - Tube system shall not protrude more than 4-7/8 inches (125 mm) to 5-7/8 inches (150 mm) from the wall.

        - Locate overspeed safety at the bottom of the tube assembly and shall consist of a mechanical overspeed sensor and brake with electrical drive cut-out protection.

        - Provide a final limit switch at the upper end of the tubes to stop the platform if it travels past the normal terminal stopping device.

** NOTE TO SPECIFIER ** The following paragraph is optional. Delete if  not required for the Project.

** NOTE TO SPECIFIER ** Select the following paragraph where required to keep stairway clear when lift is not in use. Delete if not required.

      - Platform Storage Beyond Upper Landings:

        - Platform shall travel in the folded position beyond the upper landing at the top stair nose to a remote parking position away from the stairs.

        - Platform shall travel in the folded position beyond the lower landing to a remote parking position. Provide with a ramp extension for this configuration.

** NOTE TO SPECIFIER ** The following paragraph is required for certain stair configurations. Delete if not required for the Project.

      - Final Limit Switch at Lower Landing:  Platform will land over a flight of stairs and will have a final lower limit switch.

** NOTE TO SPECIFIER ** Select one of the following rail mounting paragraphs and delete the ones not required. Direct mounting is recommended only for solid concrete walls. Mounting to a 2 by 8 inch board is intended for wood frame walls where the 2 by 8 inch board can be securely attached to the wooden studs. Use of steel support posts is for installations where there is no wall to attach to or where wall construction does not provide enough strength. See the Garaventa GSL Artira Design and Planning Guide for further rail mounting information and a loading diagram.

      - Rail Mounting:

        - Tower Mount Struts: Provide with 2-1/2 inches (65 mm) by 2-1/2 inches (65 mm) hollow structural steel tubular posts to support the guide rails.

** NOTE TO SPECIFIER **  Infill panels are optional. Select one of the following three paragraphs for in-fill safety panels.  Delete entirely if not required for the Project.

** NOTE TO SPECIFIER ** The following paragraphs may be required to meet local code requirements. This is an alternate to infill panels.  Delete if not required for the Project.

        - Steel Tube Filler: Provide additional 2-inch (51mm) diameter steel tubes added to the guide rail system for aesthetics or to create a further safety barrier with a maximum 6 inch (152 mm) opening between tubes.

** NOTE TO SPECIFIER ** With the installation of guide rails existing handrails are often obstructed or removed. The following paragraphs represent the minimum requirements for adding optional pedestrian handrails. Edit as required for the Project.

    - Pedestrian Handrail Integrated with Guide Rail:

      - A third rail acting as a handrail shall be added where existing handrails are either removed or blocked by the lifting equipment.

      - The top of the handrail gripping surface shall be between 34 inches (864 mm) and 38 inches (965 mm) above the stair nosing and have a smooth gripping surface 1-1/2 inch (38 mm) in diameter.

      - Handrail shall be in the same vertical plane as the guide rail system.

      - Handrails shall be mounted to the tube assembly and shall not be interrupted by newel posts, or other construction elements or obstructions.

    - Call Stations:

      - Provide a call station at each serviced landing that will automatically shut off if left unattended for over 2 minutes.

      - Call stations, 24 V low voltage with four illuminated 2 inches (51 mm) by 2 inches (51mm) square membrane touch sensitive buttons: one touch platform fold, one touch platform unfold and two directional call and send buttons.

      - Provide call stations with Smart-Lite Technology to prompt the user with the next sequential step of operation.  Call station buttons will emit an audible "beep" when pushed to confirm button activation to the user.

** NOTE TO SPECIFIER ** The following paragraphs include additional or optional call station features.  Select and edit paragraphs required and delete those not required for the Project.

      - Call stations shall equipped for:

** NOTE TO SPECIFIER ** Select key switch or keyless operation. Delete paragraph not required for the Project.

        - Keyed Operation.

** NOTE TO SPECIFIER ** The following paragraph is optional delete if not required for the Project.

      - Provide Attendant Call buttons on each call station.

** NOTE TO SPECIFIER ** Select the call station mounting requirements from the following paragraphs. Delete the paragraphs not required.

      - Call Station Mounting:

        - Lower and landing call station.

          - Provide surface mounted call station.

        - Upper landing call station.

          - Surface mount on wall.

        - Provide free-standing mounting pedestals for call stations located as follows:

          - Upper landing.

** NOTE TO SPECIFIER **  Select additional safety or code requirements from the following paragraphs and delete those not required.

    - Additional Safety or Code Requirements

      - Wall Mounted Audio-Visual Alerts:  Provide with adjustable volume control that sound while the lift is in operation and are visible by pedestrian traffic from all flights and landings.

** NOTE TO SPECIFIER **  The following paragraphs include provisions for indoor and outdoor locations. Select the paragraph required and delete those not required.

** NOTE TO SPECIFIER **  Select the following paragraph for platform lifts at straight stairways serving two adjacent landings. Edit to suit project requirements. Indicate locations and stair and landing requirements on the Drawings.

- EXECUTION

  - EXAMINATION

    - Do not begin installation until substrates have been properly prepared.

    - Verify required supports are correct.

    - Verify electrical rough-in is at correct locations.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

  - INSTALLATION

    - Install platform lifts in accordance with in compliance with regulatory requirements specified and the manufacturer's instructions.

    - Install system components and connect to building utilities.

    - Accommodate equipment in space indicated.

    - Startup equipment in accordance with manufacturer's instructions.

    - Adjust for smooth operation.

  - FIELD QUALITY CONTROL

    - Perform tests in compliance with regulatory requirements specified and as required by authorities having jurisdiction.

    - Schedule tests with agencies and Architect, Owner, and Contractor present.

  - PROTECTION

    - Protect installed products until completion of project.

    - Touch-up, repair or replace damaged products before Substantial Completion.

PART 3 – EXECUTION:

3.1	All work will be performed during the hours of 7:00 a.m.-3:30 p.m., Monday - Friday unless otherwise scheduled through the SMSD Representative/Project Manager.

3.2	Prior to commencing work elevator contractor must coordinate with owner on an agreed start date and estimated completion date.  Refer to information in the Bid Form and General Information about substantial completion and liquidated damages.

3.3	Contractor must perform cleanup and removal of all debris related to the scope of work.  In addition remove all equipment and unused or removed materials from job site.  Job site needs to be clean and neat in appearance prior to final inspection.

3.4	Provide a final inspection with owner and/or owner representative.

3.5	Final walk thru with owner after complete acceptance of elevator.  Owner will sign off on final completion form on this day once satisfied the scope of work was met and completed.  Then that day the warranty period will begin officially.

3.6         Damage done to the floor and walls by the contractor will be repaired at the contractor’s expense.

Company

Address

City                                    State                                          ZIP

Phone                                                    Fax

Email Address				Website Address			Tax ID #

AUTHORIZED SIGNATURE

PLEASE PRINT NAME					Date