## Sheet1
Lead in Water Testing Final Results
School |  | 3 | 4 | 5 | 7 | MS | HS | Total | District Average
Samples |  | 40 | 42 | 44 | 29 | 100 | 106 | 361
Failures |  | 3 | 0 | 0 | 1 | 7 | 9 | 20
Average |  | 0.075 | 0 | 0 | 0.034483 | 0.07 | 0.084906 | 0.055402 | 5.54%
High School Failures
Lab Sample ID | Client Sample ID | Location Description | Collection Date | Analysis Method | Dilution Factor | Analysis Date | CAS | Analyte | Result | Unit
680-131638-28 | HS-28 | Café Drinking Fountain | 10/26/2016 06:27 | 200.8 | 1 | 11/08/2016 00:42 | 7439-92-1 | Lead | 45.0 | ug/L
680-131638-42 | HS-42 | Lab Sink Rm 607/609 | 10/26/2016 07:09 | 200.8 | 1 | 11/08/2016 00:49 | 7439-92-1 | Lead | 54.2 | ug/L
680-131638-45 | HS-45 | Lab Sink Rm 609 | 10/26/2016 07:14 | 200.8 | 1 | 11/07/2016 23:12 | 7439-92-1 | Lead | 54.0 | ug/L
680-131638-51 | HS-51 | Lab Sink Rm 608 | 10/26/2016 07:23 | 200.8 | 1 | 11/08/2016 00:27 | 7439-92-1 | Lead | 960 | ug/L
680-131638-60 | HS-60 | Lab Sink Rm 602 | 10/26/2016 07:45 | 200.8 | 1 | 11/08/2016 09:26 | 7439-92-1 | Lead | 23.9 | ug/L
680-131638-61 | HS-61 | Lab Sink Rm 602 | 10/26/2016 07:47 | 200.8 | 1 | 11/07/2016 14:44 | 7439-92-1 | Lead | 16.6 | ug/L
680-131638-63 | HS-63 | Lab Sink Rm 602 | 10/26/2016 07:48 | 200.8 | 1 | 11/07/2016 17:09 | 7439-92-1 | Lead | 16.9 | ug/L
680-131638-64 | HS-64 | Lab Sink Rm 602 | 10/26/2016 07:50 | 200.8 | 1 | 11/07/2016 17:37 | 7439-92-1 | Lead | 22.6 | ug/L
680-131638-67 | HS-67 | Lab Sink Rm 602 | 10/26/2016 07:56 | 200.8 | 1 | 11/07/2016 20:46 | 7439-92-1 | Lead | 22.2 | ug/L
Middle School Failures
680-131639-36 | MS-36 | MS Kitchen Hand Sink | 10/29/2016 09:31 | 200.8 | 1 | 11/08/2016 09:13 | 7439-92-1 | Lead | 19.4 | ug/L
680-131639-37 | MS-37 | MS Kitchen Hand Sink | 10/29/2016 09:33 | 200.8 | 1 | 11/08/2016 13:20 | 7439-92-1 | Lead | 251 | ug/L
680-131639-39 | MS-39 | MS Kitchen Hose Area | 10/29/2016 09:42 | 200.8 | 1 | 11/08/2016 00:38 | 7439-92-1 | Lead | 23.5 | ug/L
680-131639-49 | MS-49 | Lab Sink Rm 201 | 10/29/2016 10:09 | 200.8 | 1 | 11/08/2016 16:12 | 7439-92-1 | Lead | 16.0 | ug/L
680-131639-56 | MS-56 | Lab Sink 202A Prep | 10/29/2016 10:22 | 200.8 | 1 | 11/08/2016 14:30 | 7439-92-1 | Lead | 181 | ug/L
680-131639-61 | MS-61 | Lab Sink Rm 202 | 10/29/2016 10:31 | 200.8 | 1 | 11/07/2016 21:01 | 7439-92-1 | Lead | 16.1 | ug/L
680-131639-64 | MS-64 | Lab Sink Rm 202 | 10/29/2016 10:36 | 200.8 | 1 | 11/08/2016 01:02 | 7439-92-1 | Lead | 16.5 | ug/L
School 3 Failures
680-130351-14 | 3-14 | Boys Bathroom Sink | 09/27/2016 05:30 | 200.8 | 1 | 10/04/2016 05:56 | 7439-92-1 | Lead | 15.3 | ug/L
680-130351-17 | 3-17 | Room 107 Old Fountain | 09/27/2016 05:35 | 200.8 | 1 | 10/13/2016 15:42 | 7439-92-1 | Lead | 16.9 | ug/L
680-130351-35 | 3-35 | Room 203 Sink | 09/27/2016 06:30 | 200.8 | 1 | 10/04/2016 03:36 | 7439-92-1 | Lead | 74.4 | ug/L
School 7 Failures
680-130357-29 | 7-29 | Room 148 Bathroom Sink | 09/28/2016 05:45 | 200.8 | 1 | 10/04/2016 15:32 | 7439-92-1 | Lead | 16.1 | ug/L