PART 1 - GENERAL

1.01	SUMMARY

A.	Provisions of Division 01 apply to this section.

B.	Section Includes:

- Excavating, backfilling, and compacting for buildings and structures.

- Fill materials.

C.	Related Sections:

- Section 02 41 00:  Site Clearing.

- Section 31 22 00:  Grading.

- Section 31 23 15:  Excavating, Backfilling and Compacting for Pavement.

1.02	SYSTEM DESCRIPTION

A.	Import and Export of Earth Materials:

- Fees:  Pay as required by authorities having jurisdiction over the area.

- Bonds:  Post as required by authorities having jurisdiction over the area.

- Haul Routes and Restrictions: Comply with requirements of authorities having jurisdiction over the area.

1.03	SUBMITTALS

- Imported Soils: A geotechnical engineer, retained by the Owner as an Owner Consultant, shall obtain initial product Sample for testing in accordance with the terms of sub-section 3.05 of this section.

- Shoring calculations as required in sub-section 3.03 of this section.

1.04	QUALITY ASSURANCE

A.	Comply with the following as a minimum requirement:  Standard Specifications for Public Works Construction, current edition, except as modified herein.

- Sampling, testing, and certification of imported and/or exported soils shall be performed in accordance with Section 01 45 33.

1.05	PROJECT CONDITIONS

A.	Information on Drawings or in soils report does not constitute a guarantee of accuracy or uniformity of soil conditions over the Project site.

B.	A copy of the foundation investigation and soils report is available for examination at the Architect's office during regular office hours of Architect.

PART 2 - PRODUCTS

2.01	FILL AND BACKFILL MATERIALS

  - Fill and backfill materials shall be a granular material previously removed from excavation, or imported fill material, free of large clods and stones larger than 3 inches, foreign materials, vegetable growths, sod, expansive soils, rubbish and debris. Material shall conform to these specified requirements and related sections.

  - Fill material exhibiting a wide variation in consistency and or moisture content shall be blended and/or aerated to stabilize and upgrade the material.

  - Imported Fill Material:

- Provide suitable materials obtained from Project site excavations for earthwork and fill materials. If excavated materials are not of suitable quality or sufficient quantity, import additional materials as necessary.

- Imported fill shall be a granular material with sufficient binder to form a firm and stable unyielding subgrade and shall not have more than 60 percent of fines passing 200 mesh sieve. Material shall have a coefficient of expansion of not more than 2 percent from air dry to optimum moisture content and not more than 6 percent from air dry to saturation.  Imported material shall be clean and free of rubbish, debris and toxic or hazardous contaminants.  Adobe or clay soils are not permitted.

  - Other Fill Materials: Brick rubble and broken concrete originating from the Project site may be legally disposed of off the Project site, or incorporated in fill, if reviewed by the geotechnical engineer, retained by the Owner as an Owner Consultant. Unless otherwise provided, no such materials may be imported from outside the Project site.

  - Permeable Backfill:

- Provide permeable backfill material behind retaining structures consisting of gravel, crushed gravel, crushed rock, natural sands, manufactured sand, or combinations of these materials conforming to the following gradations:

Sieve Size	Percentage Passing

3/4 inch	100

3/8 inch	80-100

No. 100	0-8

No. 200	0-3

- Those portions of fill material passing a No. 4 sieve shall provide a sand equivalent of at least 60.

- Provided backing for weep-holes shall consist of 2 cu. ft. of aggregate in burlap sacks, securely tied. Aggregate shall conform to requirements for No. 3 concrete aggregate as specified in subsection 200-1.4 of the Standard Specifications for Public Works Construction.

- Permeable Backfill Alternate Materials: Instead of the materials specified for retaining structures backfill, a drainage matting system such as Miradrain by Mirafi, Inc., or equal, may be provided if reviewed by the Architect.

PART 3 - EXECUTION

3.01	SITE PREPARATION

A.	Clear the Project site as required in Section 02230: Site Clearing.

3.02	PROTECTION

  - Protect and guard excavations against danger to life, limb, and property as required by, but not limited to, OSHA regulations.

  - Protect adjacent existing improvements including landscaping against damage.

  - Shore, crib, or lag excavations and earthen banks as necessary to prevent caving-in, erosion or gullying of sides.

  - Divert or de-water excavations until concrete is placed, forms are removed, and backfilling is complete.

3.03	SHORING

- Provide shoring as necessary to properly and safely support earth sides of excavations, curbs, sidewalks, gutter, drives and stairs, against movement and collapse.

- Design and Calculations: Provide in accordance with requirement of governing California Building Code and Safety Orders of State of California, Division of Industrial Safety, Title 8, Subchapter 4, Article 6, Sections 1530 and 1541.

- Remove shoring upon completion of Work, or when no longer needed, unless otherwise required by authorities having jurisdiction over the Work.

3.04	EXCAVATION

- Form sides of footings, pads, grade beams, and slab foundations, unless otherwise indicated. Provide excavations of sufficient size to permit installation and removal of forms and other Work as required.

- Machine-drill excavation for round footings to size and depth indicated.  Provide a collar or casing, or other adequate protection, to exclude dirt and debris. Protect excavations with plank covers until concrete is placed.

- Provide excavation bottoms level and free from loose material. Excavate to indicated or required elevations of undisturbed earth.

- Provide excavations free from standing water by pumping, draining, or providing protection against water intrusion. If soil becomes soft, soggy, or saturated, excavate to firm undisturbed soil and fill as required. Slope adjacent grades away from excavations to minimize entry of water.

- Calculate excavation quantities based on elevations or depths indicated on Drawings.

- Provide 2000 psi concrete for backfill of over-excavated areas to indicated or required elevations.

- Special preparation of B.E.P. areas: Excavate areas designated on Drawings as bottom of excavated planes (B.E.P.), by excavating and filling to indicated grades and elevations.

  - IMPORT/EXPORT OF MATERIALS

- Provide fill materials as specified in Part 2- Products. If excavated materials from the Project site are not of required quality or sufficient quantity, import additional materials as necessary.

- In addition to the requirements of this section, import and/or exported materials shall comply with the requirements of Section 01 45 33.

- Imported fill materials shall be sampled by the geotechnical engineer, retained by the Owner as an Owner Consultant, for compliance with the requirements of Part 2 of this section.

- The geotechnical engineer, retained by the Owner as an Owner Consultant, shall submit all samples to a DSA approved independent testing laboratory for testing.

- Initial sampling shall be performed by a geotechnical engineer, retained by the Owner as an Owner Consultant, before importing material to the Project site.  Identify the location of the source site in addition to the address, name of the person and/or entity responsible for the source site. The geotechnical engineer, retained by the Owner as an Owner Consultant, shall obtain both the initial sample and additional samples from the identified site and shall submit all samples to the approved independent testing laboratory for testing.

- The geotechnical engineer, retained by the Owner as an Owner Consultant, shall perform additional sampling during import operations. If the total quantity of import is determined to be greater than 1000 cubic yards of material, one sample shall be obtained and submitted for testing for each 250 cubic yards of imported material. If the total quantity of import is determined to be less than 1000 yards, one sample shall be obtained and submitted for testing for each 100 cubic yards of imported material.

- The independent approved testing laboratory shall perform the required tests and report results of all tests noting if the tested material passed or failed such tests and shall furnish copies to the PI, Architect, OAR, DSA, Contractor, and others as required. Report shall state tests were conducted under the responsible charge of a licensed State of California professional engineer and the material was tested in accordance with applicable provisions of the Contract Documents, Title 24, CCR and the DSA. Upon completion of the Work of this section, the independent testing laboratory and geotechnical engineer shall submit a verified report to the DSA as required by Title 24, CCR.

- Bills of lading or equivalent documentation will be submitted to the PI on a daily basis.

- Upon completion of import operations, provide the OAR a certification statement attesting that all imported material has been obtained from the identified source site.

3.06	BACKFILLING

- After concrete has been placed, forms removed and concrete Work inspected, backfill excavations to indicated or required grades. Backfill simultaneously on each side of walls or grade beams. Remove rubbish, debris, and other waste materials from excavations before placing backfill.

- Before installing any backfill, adequately cure concrete and provide bracing to stabilize structures. Protect waterproofing or dampproofing against damage during backfilling operations with required protection board. Remove bracing as backfill operation progresses.

- Do not furnish or install expansive soils for below grade building walls.

- Install each layer of material in a not to exceed thickness of 6 inches, unless otherwise required.

- Rigidly control the amount of water to be installed to provide optimum moisture content for type of fill material furnished. Do not over-saturate or compact by flooding or jetting.

- Install wall backfill before installing railings and fences on walls.

- Impervious backfill materials shall be installed in layers along with and by the same methods specified for structure backfill. Impervious backfill materials shall be at the approximate grade and elevation and where exposed to erosion, shall be covered with at least a 12 inch layer of fill material as reviewed by the geotechnical engineer, retained by the Owner as an Owner Consultant.

- Install weep hole drainage at the backside of walls so the backing completely covers the weep holes, is horizontally centered and extends at least 12 inches above the bottom of the weep opening. Provide an 8 inch square section of 1/4 inch galvanized or aluminum screen, with a minimum wire diameter of 0.03 inch, and install at the backside of each weep hole before installing the backfill material.

- Where a reviewed drainage matting system is provided instead of permeable backfill for retaining structures, install in accordance with the manufacturer recommendations.

3.07	COMPACTING

- Compact each layer of fill material by tamping, sheepsfoot rollers or pneumatic-tired rollers, to such extent as to provide specified relative compaction.  At inaccessible locations, compact to specified requirements with hand-held, operated and directed compaction equipment.

PROJECT ARCHITECT NOTE: EDIT THE FOLLOWING COMPACTION

PERCENTAGE, TO REFLECT WITH RECOMMENDATIONS CONTAINED IN THE

SOILS REPORT.

- Unless otherwise indicated, compact each layer of fill material to a relative compaction of at least (?) percent.

- Do not compact by flooding or jetting.

- When fill materials, or a combination of fill materials, are encountered or provided which develop densely packed surfaces as a result of installation or compacting operations, scarify each layer of compacted fill before installing the next succeeding layer.

3.08	INSPECTION AND TESTING

  - The geotechnical engineer, retained by the Owner as an Owner Consultant, will inspect and test excavations, sample material quality as required in Part 2, and observe installation and compaction of fill materials.

  - The geotechnical engineer, retained by the Owner as an Owner Consultant, will sample imported fill materials from their designated source before delivery to the Project site.

  - Installation of backfill shall be observed by the geotechnical engineer, retained by the Owner as an Owner Consultant.

  - The geotechnical engineer, retained by the Owner as an Owner Consultant, will inspect and test excavation Work before the installation of fill and/or other materials.

  - Compaction:  Test compaction in accordance with ASTM D 1557, Method C.

  - DSA will inspect foundation excavations when completed and ready for forms, after forms are in place and before first placement of concrete.

3.09	PROTECTION

A.	Protect the Work of this section until Substantial Completion.

3.10	CLEANUP

A.	Remove rubbish, debris, and waste materials and legally dispose of off the Project site.

# END OF SECTION