| Revision History |  |
| --- | --- |
| Revision Date | Section/Nature of Revision |
| 3/1/17 | Document issued |
| 10/2/25 | 1.2 B: removed industrial control devices, controllers and assemblies and added controllers, contactors and overload relays rated 600 volts 2.1 B-E: removed B-D and added and shall be approved by the Owner 2.2 A: removed AC general purpose magnetic contactor and added controllers, contactors and overload relays rated 600 volts 2.3 B-E: removed B-D and added and shall be approved by the Owner 2.5: added the entire section |

PART 1 - GENERAL

1.1	SECTION INCLUDES

- General Purpose Contactors

- Lighting Contactors

1.2	REFERENCES

- ANSI/NEMA ICS 6 Industrial Control and Systems: Enclosures

- NEMA ICS 2 Controllers, Contactors and Overload Relays Rated 600 Volts

- ANSI/NFPA 70 National Electrical Code

1.3	SUBMITTALS

A.	Submit under provisions of Division 1.

B.	Product data: include dimensions, size, voltage ratings and current ratings.

C.	Manufacturer's instructions: indicate application conditions and limitations of use stipulated by product testing agency specified under regulatory requirements.

1.4	PROJECT RECORD DOCUMENTS

A.	Submit under provisions of Division 1.

B.	Accurately record actual locations of each contactor and indicate circuits controlled.

1.5	OPERATION AND MAINTENANCE DATA

A.	Submit under provisions of Division 1.

B.	Maintenance data: include instructions for replacing and maintaining coil and contacts.

1.6	QUALIFICATIONS

Manufacturer: company specializing in manufacturing products specified in this section with minimum three years’ experience.

PART 2 – PRODUCTS

2.1	MANUFACTURERS – GENERAL PURPOSE CONTACTORS

- Square D

- Substitutions: under provisions of Division 1 and shall be approved by the Owner

2.2	GENERAL PURPOSE CONTACTORS

- Description: NEMA ICS 2, Controllers, Contactors and Overload Relays Rated 600 Volts.

- Coil voltage: 120 volts, 60 Hertz.

- Poles: as scheduled.

- Size: as scheduled.

- Enclosure: ANSI/NEMA ICS 6, Type as required to meet conditions of installation.

2.3	MANUFACTURERS – LIGHTING CONTACTORS

- Square D

- Substitutions: Under provisions of Division 1 and shall be approved by the Owner

2.4	LIGHTING CONTACTORS

- Description: NEMA ICS 2, magnetic lighting contactor.

- Configuration: mechanically or electrical held, verify with drawings.

- Coil voltage: 120 or 277 volts, 60 Hertz.

- Poles: as indicated.

- Contact rating: match branch circuit overcurrent protection, considering derating for continuous loads.

- Enclosure: ANSI/NEMA ICS 6, type as required to meet conditions of installation.

2.5	ACCESSORIES

- Devices shall be factory installed in controller enclosure, unless otherwise indicated.

- Push buttons, pilot lights and selector switches: NEMA ICS 2, 30 mm, heavy duty type.

- Stop push button.

PART 3 – EXECUTION

3.1	INSTALLATION

A.	Install in accordance with manufacturer's instructions in a readily accessible location per NEC 110-26.

B.	Where acceptable/possible, all contactors, excluding lighting contactors, are to be installed in the Electrical Room, where served from, adjacent to electrical panelboards.

***END OF SECTION***