| Revision History |  |
| --- | --- |
| Revision Date | Section/Nature of Revision |
| 3/1/17 | Document issued |
| 10/1/25 | 1.3 A-G: removed and added entire section 2.1 A-D: removed C and D. Added and shall be approved by the Owner 2.2 A: removed BU1 and added BS 31050 2.3 B: removed NEMA AB 1 and added UL 489 |

PART 1 – GENERAL

1.1  WORK INCLUDED

- Indoor Busway and Fittings

- Busway Plug In Units

1.2	RELATED WORK

Section 26 28 16 Disconnect Switches

1.3	REFERENCES

- ANSI/NEMA ICS 2 Controllers, Contractors and Overload Relays Rated 600 Volts

- FS W-C-375 Circuit Breakers, Molded Case, Branch Circuit and Service

- ANSI/UL 4248-1 Standard for Safety for Fuse Holders Part 1: General Requirements

- ANSI/UL 4248-12 Fuse Holders Part 12: Class R

- UL 489 Molded Case Circuit Breakers, Switches and Enclosures

- NEMA BS 31050 General Instructions for Handling, Installation and Maintenance of Busway Rated 600 Volts or Less

- ANSI/UL 98 Enclosed and Dead Front Switches

1.4	SUBMITTALS

A.	Submit shop drawings and product data under provisions of Division 1.

B.	Indicate busway ratings, dimensions and finishes.  Include dimensioned layout diagram, installation details and locations of supports and fittings, including firestops and weather seals.  Include details of wall and floor penetrations.

C.	Submit manufacturer’s installation instructions under provision of Division 1.

1.5	OPERATION AND MAINTENANCE DATA

A.	Submit data under provisions of Division 1.

B.	Include joint re-tightening schedule.

1.6	DELIVERY, STORAGE AND HANDLING

A.	Deliver products to site under provision of Division 1.

B.	Store and protect products under provisions of Division 1.

C.	Protect busway from moisture with appropriate coverings.  Store in dry, interior location.

D.	Prevent damage to internal components, housing and finish.

PART 2 – PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS – BUSWAY AND PLUG-IN UNITS

- Square D

- Substitutions: under provisions of Division 1 and shall be approved by the Owner.

2.2	INDOOR BUSWAY

A.	Plug in busway: NEMA BS 31050,  three phase, four wire plug in busway rated 120/208 and 277/480 volts, 60 Hz.  Provide non-ventilated housing with plug in openings on 24” (600 mm) centers one side, with hinged doors to protect opening where plug in unit is not installed.  Ampere ratings as scheduled and shown on the drawings.

B.	Conductors: copper bars fully insulated expect at joints.  Provide full neutral.  Provide insulated ground bus.

C.	Joints: provide single bolt type, with silver-plated contact surface for bus and splice plate.

D.	Provide fittings in accordance with manufacturer’s instructions.

E.	Finish: baked gray enamel.

2.3	PLUG IN UNITS

A.	Units: compatible with busway, enclosure with hinged door and operating handle for stick operation.  Provide insulated grounding stab.

B.	Molded case thermal-magnetic circuit breakers: UL 489 and FS W-C-375 circuit breakers with integral thermal and instantaneous magnetic trip in each pole.

PART 3 – EXECUTION

3.1	INSTALLATION

A.	Do not install busway until building is closed in and moisture tight.

B.	Install busways and accessories in accordance with manufacturers’ instructions.

C.	Tighten joints using a torque wrench, to manufacturer’s specified values.

D.	Mounting and support: mount horizontal busway runs in upright position, as indicated.  Support busway at intervals as recommended by manufacturers.

***END OF SECTION***