PART 1 - GENERAL

1.01	SECTION INCLUDES

- Packaged Diesel Engine Generator System

- Exhaust Silencer and Fittings

- Battery and Charger

- Weatherproof Enclosure

1.02	RELATED SECTIONS

Section 26 36 23	Automatic Transfer Switches

1.03	REFERENCES

- ANSI/NEMA 250—Enclosures for Electrical Equipment (1000 Volts Maximum)

- ANSI/NEMA MG 1—Motors and Generators

- ANSI/NFPA 70—National Electrical Code (NEC)

- ANSI/NFPA 110—Emergency and Standby Power Systems

- ANSI/NEMA AB 1—Molded Case Circuit Breakers

- ANSI/NFPA 30—Flammable and Combustible Liquids Code

- UL 2200—Standard for Stationary Engine Generator Assemblies

1.04	SYSTEM DESCRIPTION

A.	Engine generator system to provide source of emergency and standby power.

B.	Operation:  In accordance with ANSI/NFPA 70 and 110

1.05	SUBMITTALS

A.	Submit shop drawings and product data under provisions of Division 01.

B.	Submit shop drawings showing plan and elevation views with overall and interconnection point dimensions.

C.	Submit manufacturer's data, including sound reduction test data, on weatherproof sound attenuated enclosure.

D.	Provide three (3) bound copies and one (1) electronic copy of all service manuals and related software. The software shall be an open architecture that is not proprietary to one manufacturer

E.	Provide twelve hours of on-site training over the course of two days for up to two of the owner’s technicians.

1.06	PROJECT RECORD DOCUMENTS

A.	Submit record documents under provisions of Division 01.

B.	Accurately record location of engine generator, mechanical and electrical connections.

1.07	DELIVERY, STORAGE, AND HANDLING

A.	Deliver products to site under provisions of Division 01.

B.	Store and protect products under provisions of Division 01.

C.	Accept packaged engine generator set and accessories on site in crates and verify any damage.

D.	Protect equipment from dirt and moisture by securely wrapping in heavy plastic.

PART 2 - PRODUCTS

2.01	MANUFACTURERS

- Caterpillar

- Detroit Diesel

- Kohler

- Onan

- Generac Power

- Substitutions:  Under provisions of Division 01

2.02	ENGINE

A.	Type:  Water-cooled in-line or V-type, four stroke cycle, internal combustion engine.

B.	Fuel System:  Appropriate for use of diesel

C.	Engine Speed:  1,800 rpm

D.	Governor:  Isochronous type to maintain engine speed within 0.5 percent, steady state, and 5 percent, no load to full load, with recovery to steady state within 2 seconds following sudden load changes.  [Equip governor with means for manual operation and adjustment.]

E.	Safety Devices:  Engine shutdown on high water temperature, low oil pressure, overspeed, and engine overcrank.  Limits as selected by manufacturer.

F.	Engine Starting:  DC starting system with positive engagement, number and voltage of starter motors in accordance with manufacturer's instructions.  Include remote starting control circuit, with MANUAL-OFF-REMOTE selector switch on engine- generator control panel.

G.	Engine Jacket Heater:  Thermal circulation type water heater with integral thermostatic control, sized to maintain engine jacket water at 90°F (32°C), and suitable for operation on 120 volts AC.

H.	Radiator:  Radiator using glycol coolant, with blower type fan, sized to maintain safe engine temperature in ambient temperature of 110°F (43°C).  Radiator Air Flow Restriction: 0.5 inches of water (9.34 mm of mercury), maximum.

- Engine Accessories:  Fuel filter, lube oil filter, intake air filter, lube oil cooler, fuel transfer pump, fuel priming pump, and gear-driven water pump.  Include fuel pressure gauge, water temperature gage, and lube oil pressure gage on engine- generator control panel.

J.	Mounting:  Provide unit with suitable spring-type vibration isolators and mount on structural steel base.

K.	The engine shall be EPA certified for the appropriate tier at the time of installation.

2.03	GENERATOR

A.	Generator:  ANSI/NEMA MG 1; 3-phase, 4-pole, reconnectible brushless synchronous generator with brushless exciter.

B.	Rating:  As indicated on drawings.

C.	Insulation:  ANSI/NEMA MG 1, Class F.

D.	Temperature Rise:  130 degrees C standby.

E.	Enclosure:  ANSI/NEMA MG 1; open drip proof.

F.	Voltage Regulation:  Include generator-mounted volts per Hertz exciter-regulator to match engine and generator characteristics, with voltage regulation +/- 1 percent from no load to full load.  Include manual controls to adjust voltage drop +/- 5 percent voltage level, and voltage gain.

2.04	ACCESSORIES

A.	Exhaust Silencer:  Residential type silencer, with muffler companion flanges and flexible stainless steel exhaust fitting, suitable for horizontal orientation, sized in accordance with engine manufacturer's instructions.

B.	Batteries:  Heavy duty, diesel starting type lead-acid storage batteries, [170] [	] ampere-hours minimum capacity.  Match battery voltage to starting system.  Include necessary cables and clamps.

C.	Battery Tray:  Plastic coated metal or wooden tray treated for electrolyte resistance, constructed to contain spillage of electrolyte.

D.	Battery Charger:  Current limiting type designed to float at 2.17 volts per cell and equalize at 2.33 volts per cell.  Include overload protection, full wave rectifier, DC voltmeter and ammeter, and 120 volts AC fused input.  Provide wall-mounted enclosure to meet ANSI/NEMA 250, Type 1 requirements.

- E.	Generator Circuit Breaker: Molded-case, electronic-trip type; 100 percent rated; complying with UL 489.

1)	Tripping Characteristics: Adjustable long-time and short-time delay and instantaneous.

2)	Trip Settings: Selected to coordinate with generator thermal damage curve and all downstream over current devices per NEC Article 700.28.

3)	Shunt Trip: Connected to trip breaker when generator set is shut down by other protective devices.

4)	Mounting: Each circuit breaker installed in separate box in accordance with NEC Article 700 separation of circuits

F.	Engine-Generator Control Panel:  ANSI/NEMA 250, Type 1 generator mounted control panel enclosure with engine and generator controls and indicators.  The controller shall meet the requirements of NFPA 110 Level 1 rating.  Using a digital display, include provisions for the following equipment and features:

1)	Frequency Meter:  45-65 Hz range.

2)	AC Output Voltmeter.

3)	AC Output Ammeter.

4)	DC voltage

5)	Engine coolant temperature.

6)	Engine lubricating oil temperature.

7)	Running time meter.

8)	Manual operation of the engine and generator for testing purposes.

9)	User programmable (based on KW and frequency) outputs for shedding of loads to maintain critical systems.

10)	Provide a minimum of 2 dry contact inputs that can be user configured to shut down the generator via other systems.

11)	Provide all NFPA 110 Level 1 required outputs and a minimum of 10 additional outputs for interfacing with other systems for monitoring and alarm purposes. Additional outputs shall be user configurable to provide signals for (at a minimum); generator run, fault, overload alarm, KW load.

G.	Remote Serial Annunciator:  The annunciator shall meet the requirements of NFPA 110 Level 1 rating.  Include provisions for the following equipment and features:

- LED indicators for shutdowns and warnings (pre-alarms), or status.

- LED indicators, an audible horn, an alarm silence button, and a lamp test button required by NFPA 110, Level 1.

- Up to three (3) user-defined inputs shall each activate an LED and an audible horn for shutdowns, warnings, or status conditions.

- Provide an RS-485 connection at the annunciator from the generator controller.  Maximum distance shall be 1220 m (4000 ft.) from the generator controller to the furthest annunciator.

H.	The generator set shall be provided with overload protection for the armature that is separate from the line circuit breaker(s). Provide either a shunt trip circuit breaker with phase monitoring or a controller capable of shutting down the generator in the event of an overload.

2.05	MANUFACTURERS (WEATHERPROOF SOUND ATTENUATED ENCLOSURE)

- As provided by the manufacturer

- Pritchard Brown

- Phoenix Products

- Wedlake Fabricating

- Substitutions:  Under provisions of Division 01

2.06	WEATHERPROOF SOUND ATTENUATED ENCLOSURE

A.	The intent of this specification is to provide the Owner with a type generator set enclosure complete in every detail and requiring no additional in-field modifications or assembly, except where specifically allowed by these specifications.  The enclosure is to be accurately dimensioned so as to be in compliance with the National Electrical Code (NEC), the National Fire Protection Association (NFPA) for clearance of all specified items included therein, and all applicable fire codes for a structure and application of this type.

1)	Construction:  The enclosure shall consist of a roof, two (2) side walls and two (2) end walls of prepainted, aluminum, stressed-skin, and semi-monocoque construction.  The roof shall be a one (1) piece cambered sheet of .040" thick aluminum with 1/8" thick extruded aluminum recessed side and end rails with cast aluminum corners.  Extruded aluminum I-beam roof bows shall be spaced on 12" centers.  The side and end wall shall be .040" thick aluminum sheet mill-prepainted and riveted on 3" centers with 1/8" extruded aluminum hat sections, and with side posts on 24" centers.  The corner posts shall be a radius type extruded aluminum alloy.

2)	Doors:  All doors on the enclosure shall be strategically located in areas as to allow ease of maintenance on the generator set and allow good access to and visibility of instruments, controls, engine gauges, etc.  The door frames shall be welded aluminum consisting of extruded aluminum riveted to the side panels.  Forged aluminum hinges with stainless steel pins and nylon bushings shall also be provided.  The personnel doors shall be manufactured from aluminum and fully gasketed to form a weather-tight perimeter seal.  A three- point latching assembly with interior latch release and exterior padlocking provisions shall also be provided.

3)	Louvers:  Provide gravity louver at discharge.  Louvers shall be designed to prevent the entrance of driving rainwater, but shall have sufficient free area to allow for 120% of the total engine/generator cooling air requirements used in this application.  Louvers shall be of all aluminum construction.

4)	The Manufacturer of the enclosure shall provide mounting brackets for the exhaust silencer specified.  In addition, the exhaust silencer shall be installed outside the enclosure.

5)	Finish:  Upon final assembly of the enclosure, it shall be prime painted with a minimum of two (2) coats of aluminum primer.  The final finish painting shall be a minimum of two (2) coats of enamel.  Four (4) spray cans of exterior touch-up paint shall be included with the unit.  The interior of the enclosure shall be finish painted in white enamel and two (2) spray cans of interior touch-up paint shall also be included with the unit.  Exterior finish painted color selected by the Architect.

6)	Sound Attenuation:  The entire enclosure except for the louvered openings shall have sound attenuation material mechanically attached to the interior surfaces of the unit.  Sound absorbing material shall be held in place by expanded aluminum metal to form a removable section easily inspected by maintenance personnel.  The sound attenuation material and fastening system shall apply to the enclosure roof as well as the side panels and doors, and shall consist of a minimum of two inches (2") of fiberglass covered by one- half inch (1/2") thick sound attenuation foam.  The enclosure, including louvered sections, must be capable of reducing generator sound by 10 DBA at 10 feet.

7)	Bird Screens:  Provide bird screens at all inlet and outlet openings.

8)	Door Hardware:  Add panic hardware on emergency exit door hardware on generator enclosure exit door.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Verify that surfaces are ready to receive work and field dimensions are as shown on drawings.

B.	Verify that required utilities are available in proper location and ready for use.

C.	Beginning of installation means installer accepts existing conditions.

D.	Provide separate overcurrent protection device for each ATS.  See Appendix 2.

3.02	INSTALLATION

A.	Install in accordance with manufacturer's instructions.

B.	Packaged engine generator systems, not solidly grounded at the ATS, shall have a separate grounding electrode from the grounding termination at the generator to the main grounding electrode at the main service to the building sized per NEC Article 250.66.  Solidly grounded ATS and generator systems shall be bonded at the ATS.  Minimum loads to be connected are:  Emergency lights, exit lights, fire alarm system, intercom system, and telephone system.  (See Appendix 2)

C.	Provide full load test utilizing portable test bank for four (4) hours minimum.  Field inspection and testing will be performed under provisions of Division 01.  Simulate power failure including operation of transfer switch, automatic starting cycle, and automatic shutdown, and return to normal.  Generator Manufacturer to provide load bank test.

D.	During test, record the following at 20 minute intervals:

- Kilowatts

- Amperes

- Voltage

- Coolant temperature

- Room temperature

- Frequency

- Oil pressure

E.	Test alarm and shutdown circuits by simulating conditions.

3.03	MANUFACTURER’S FIELD SERVICES

Prepare, start, test, and adjust systems under provisions of Division 01.

3.04	ADJUSTING

A.	Adjust work under provisions of Division 01.

B.	Adjust generator output voltage and engine speed.

3.05	CLEANING

A.	Clean work under provisions of Division 01.

B.	Clean engine and generator surfaces.  Replace oil and fuel filters.

3.06	DEMONSTRATION

A.	Provide systems demonstration under provisions of Division 01.

B.	Describe loads connected to emergency and standby system and restrictions for future load additions.

C.	Simulate power outage by interrupting normal source, and demonstrate that system operates to provide emergency and standby power.

3.07	REMOTE FUEL TANK SPECIFICATION

          - Subbase-Mounted, Double-Wall, Fuel-Oil Tank: Factory installed and piped, complying with UL 142 fuel-oil tank. Features include the following:

Tank Bottom:  Sloped bottom to remove particulates and other fuel-borne contaminants from the fuel intake to the engine.

Tank Top:  Sloped top to prevent standing water.

Electric tank level indicator with digital readout on control panel.

Low Fuel Sensing Switch: shall be provided, in accordance with NFPA110, to indicate when less than the minimum fuel necessary for full load running, as required by the specified EPSS class.

          - Fuel-Tank Capacity: Minimum 133 percent of total fuel required for low-fuel sensor quantity or for the hours of continuous operation for indicated EPSS class.

          - Leak detection in interstitial space.

          - Vandal-resistant fill cap.

          - Prior to operating generator, ensure tank is full of fuel.  After load bank test is completed and immediately prior to turning generator over to owner, fuel tank shall be topped off.

3.08	WARRANTY

A.	Equipment, parts, and labor shall be warranted to be free from defects in material and workmanship for a period of five (5) years from date of final substantial completion and acceptance of system by Owner.

B.	Contractor shall arrive on site within two (2) normal business days to repair system under warranty.  All repairs shall be completed within one (1) week.

C.	Failure to respond in time specified shall result in School Board Maintenance Department making repairs and charging warrantor all labor and material necessary for repairs. It is agreed by this Contractor that this remedy will not void any warranties.

Appendix References:	Electrical Distribution Grounding System Detail (2 pages) Emergency Standby Generator Detail

END OF SECTION