| Revision History |  |
| --- | --- |
| Revision Date | Section/Nature of Revision |
| 3/1/17 | Document issued |
| 9/30/25 | 1.2 A-J: removed entire section and added new section 2.1 A-E: removed C-E and added shall be approved by the Owner 2.2 A and C: removed KS 1 and added BS 31047. Removed ES W-S-865 and added ANSI/UL 98 2.2 B: removed F-S W-F-870 and added ANSI/UL 4248-1 2.2 D: removed KS 1 and added BS 31047 2.4 A: removed 198E and added 248-8. Added ANSI/UL 248-12 |

PART 1 - GENERAL

1.1	WORK INCLUDED

- Disconnect Switches

- Fuses

- Enclosures

1.2	REFERENCES

- ANSI/UL 248-1 Low Voltage Fuses Part 1: General Requirements

- ANSI/UL 248-12 Low Voltage Fuses Part 12: Class R Fuses

- ANSI/UL 248-8 Low Voltage Fuses Part 8: Class J Fuses

- ANSI/UL 248-10 Low Voltage Fuses Part 10: Class L Fuses

- ANSI/UL 248-12 Low Voltage Fuses Part 12: Class R Fuses

- ANSI/UL 248-15 Low Voltage Fuses Part 15: Class T Fuses

- ANSI/UL 4248-1 Standard for Safety for Fuse Holders Part 1: General Requirements

- ANSI/UL 4248-12 Fuse Holders Part 12: Class R Fuses

- ANSI/UL 98 Enclosed and Dead Front Switches

- NEMA BS 31047 Heavy Duty Enclosed and Dead Front Switches (600-Volts Maximum)

1.3	SUBMITTALS

A.	Submit product data under provisions of Division 1.

B.	Include outline drawings with dimensions and equipment ratings for voltage, capacity, horsepower and short circuit.

PART 2 – PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS – DISCONNECT SWITCHES

- Square D

- Substitutions: under provisions of Division 1 and shall be approved by the Owner.

2.2	DISCONNECT SWITCHES

A.	Fusible switch assemblies: NEMA BS 31047, type HD, ANSI/UL 98, quick-make, quick-break, load interrupter enclosed knife switch with externally operable handle interlocked to prevent opening front cover with switch in ON position. Handle lockable in OFF position.

- Fuse clips: ANSI/UL 4248-1.

- Non-fusible switch assemblies: NEMA BS 31047, type HD, ANSI/UL 98, quick-make, quick-break, load interrupter enclosed knife switch with externally operable handle interlocked to prevent opening front cover with switch in ON position.  Handle lockable in OFF position.

- Enclosures: NEMA BS 31047, as indicated on drawings.

- All service disconnects shall be “heavy-duty type.”  General duty equipment is not acceptable.

2.3	ACCEPTABLE MANUFACTURERS—FUSES

- Bussmann

- Gould-Shawmut

- Littelfuse

- Substitutions: under provisions of Division 1

2.4	FUSES

A.	Fuses 600 Amperes and less: ANSI/UL 248-8, Class J for feeders and transformer loads and ANSI/UL 248-12 Class RK 5 for motor loads.  Dual element, current limiting, time delay, one time fuse, 250 or 600 volts.

B.	Interrupting rating: 200,000 rms amperes.

C.	Spare fuses shall be provided in the amount of 10% of each size and type of fuse installed but, in no case, shall be less than three (3) spares for each different size and class of fuse being provided.  Store in fuse cabinet of sufficient size to house all fuses (provided by electrical Contractor), located by Project Architect/Engineer.

PART 3 – EXECUTION

3.1	INSTALLATION

A.	Install disconnect switches where indicated on drawings.  Where equipment is manufactured/provided with integral disconnecting means, disconnect switches shall not be required.

B.	Install fuses in fusible disconnect switches.

C.	Fuses and fuse holders shall be equipped with UL Class “R” rejection clips.

D.	All fusible switches which contain current limiting fusing shall have UL Class “R” rejection clips

E.	Fuses shall be dual element and current limiting.

- When using fuses of ratings above 600 amperes, specify 600-volts UL Class “L”, current limiting/ time delay/dual element with 200,000 ampere interrupting capacity (AIC).

- When using fuses of ratings 600 ampere and below, specify UL Class RK1 current limiting/time delay/dual element with 200,000 ampere interrupting capacity (AIC).

- All fuses shall be by the same manufacturer.

- All multi-pole breakers shall have factory installed common trip handle ties.

- Install in accordance with manufacturer's instructions and per NEC 110.26.

***END OF SECTION***