| Revision History |  |
| --- | --- |
| Revision Date | Section/Nature of Revision |
| 3/1/17 | Document issued |
| 9/30/25 | 1.3 A-E: changed entire section 1.7 B: removed two (2) and added three (3) 2.1 B-E: removed manufacturers and added shall be approved by the Owner 2.2 A-C: added ANSI 2.3 A, F-H and J-M: added ANSI 2.4 A: removed NEMA KS 1 and FS W-S-865 and added ANSI/UL 98 and ANSI/UL 4248-12 2.4 B: removed FS W-F-870 and added ANSI/UL 4248-1 |

PART 1 – GENERAL

1.1	WORK INCLUDED

A.	Manual Motor Starters

B.	Magnetic Motor Starters

C.	Combination Magnetic Motor Starters

1.2	RELATED WORK

- Section 26 05 29 Supporting Devices

1.3	REFERENCES

- ANSI/NEMA ICS 6 Industrial Control and Systems: Enclosures

- ANSI/UL 248-12 Low Voltage Fuses Part 12: Class R Fuses

- ANSI/UL 4248-1 Standard for Safety for Fuse Holders Part 1: General Requirements

- ANSI/UL 4248-12 Fuse Holders Part 12: Class R

- ANSI/NEMA ICS 2 Controllers, Contractors and Overload Relays Rated 600-Volts

1.4	SUBMITTALS

A.	Submit shop drawings and product data under provisions of Division 1.

B.	Indicate on shop drawings, front and side views of motor control enclosures with overall dimensions. Include conduit entrance locations and requirements; nameplate legends; size and number of bus bars per phase, neutral and ground; electrical characteristics including voltage, frame size and trip ratings, withstand ratings and time-current curves of all equipment and components.

C.	Provide product data on motor starters and combination motor starters, relays, pilot devices and switching and overcurrent protective devices.

D.	Submit manufacturers' instructions under provisions of Division 1.

1.5	OPERATION AND MAINTENANCE DATA

A.	Submit operation and maintenance data under provisions of Division 1.

B.	Include spare parts data listing, source and current prices of replacement parts and supplies and recommended maintenance procedures and intervals.

1.6	DELIVERY, STORAGE AND HANDLING

A.	Deliver products to site under provisions of Division 1.

B.	Store and protect products under provisions of Division 1.

C.	Store in a clean, dry space.  Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect units from dirt, water, construction debris and traffic.

D.	Handle in accordance with manufacturer's written instructions.

1.7	SPARE PARTS

A.	Keys: furnish five each to Owner (one goes to the Electrical Manager in the Maintenance Department).

B.	Fuses: furnish three spare fuses of each type and rating installed to Owner.  Leave spare fuses in equipment that the fuses are protecting.

PART 2 – PRODUCTS

2.1	ACCEPTABLE MANUFACTURER – MOTOR STARTERS

- Square D.

- Substitutions: under provisions of Division 1 and shall be approved by the Owner.

2.2	MANUAL MOTOR STARTERS

A.	Manual motor starter: ANSI/NEMA ICS 2, (size as noted on drawings) AC general purpose, Class A, manually operated, non-reversing full-voltage controller for induction motors rated in horsepower, with overload relay, red pilot light and key toggle operator.

B.	Fractional horsepower manual starter: ANSI/NEMA ICS 2, AC general purpose, Class A, manually operated, 1 pole full-voltage controller for fractional horsepower induction motors, with thermal overload unit, red pilot light and key toggle operator.

C.	Motor starting switch: ANSI/NEMA ICS 2, AC general purpose, Class A, manually operated, 1 pole full-voltage controller for fractional horsepower induction motors, without thermal overload unit, red pilot light, key toggle operator.

D.	Phase failure, overvoltage and undervoltage relays: provide contacts and locking potentiometers with overvoltage or undervoltage adjustments and LED indicators.

E.	Enclosure: ANSI/NEMA ICS 6 as noted on drawings.

2.3	MAGNETIC MOTOR STARTERS

A.	Magnetic motor starters: ANSI/NEMA ICS 2, AC general purpose, Class A, magnetic controller for induction motors rated in horsepower.  Provide all accessories listed.

B.	Full voltage starting: non-reversing type.

C.	Reduced voltage starting: closed-circuit transition wye-delta type.

D.	Two speed starting: two speed, two winding, variable torque type.  Include integral adjustable time delay transition between fast and slow speeds. Coordinate actual time setting required for motor that starter is connected to with manufacturer.

E.	Coil operating voltage: 120 volts, 60 Hertz.  Coordinate other voltages with controls Contractor prior to ordering.  All control voltage shall be 120 volts or less.

F.	Size: ANSI/NEMA ICS 2, size as shown on drawings.

G.	Overload relay: ANSI/NEMA ICS 2, electronic motor logic protection.

H.	Enclosure: ANSI/NEMA ICS 6, type as shown on drawings.

I.	Combination motor starters: combine motor starters with fusible switch disconnect in common enclosure.

J.	Auxiliary contacts: ANSI/NEMA ICS 2, two field convertible contacts in addition to seal-in contact shall be provided.

K.	Indicating lights: ANSI/NEMA ICS 2, run, green in front cover shall be provided.

L.	Selector switches: ANSI/NEMA ICS 2, HAND/OFF/AUTO, locking type, in front cover shall be provided.

M.	Relays: ANSI/NEMA ICS 2.  Provide as necessary for control functions.

N.	Control power transformers: 120 volts secondary in each motor starter shall be provided.

O.	Phase failure, overvoltage and undervoltage relays: provide contacts and locking potentiometers with overvoltage or undervoltage adjustments and LED indicators.

2.4	CONTROLLER OVERCURRENT PROTECTION AND DISCONNECTING MEANS

- Fusible switch assemblies: ANSI/UL 98, ANSI/UL 4248-12, quick-make, quick-break, load interrupter enclosed knife switch with externally operable handle.  Provide interlock to prevent opening front cover with switch in ON position.  Handle lockable in OFF position.

- Fuse Clips: ANSI/UL 4248-1.  Designed to accommodate Class R fuses.

2.5	ACCEPTABLE MANUFACTURERS – FUSES

- Bussmann

- Gould-Shawmut

- Littelfuse

- Substitutions:  Under provisions of Division 1

2.6	FUSES

A.	Fuses: ANSI/UL 198E, Class RK5, dual element, current limiting, time delay, one time fuse, 250 or 600 volts.

B.	Interrupting rating: 200,000 rms amperes

C.	Fusible units shall be equipped with UL Class “R” rejection clips.

PART 3 – EXECUTION

3.1	INSTALLATION

- Install motor control equipment in accordance with manufacturer's instructions.

- Motor starters supplied by the electrical Contractor unless otherwise indicated.

- Install fuses in fusible switches.

- Select and install electronic motor logic overload relay protection in all motor starters to match installed motor characteristics.

- Motor data: provide engraved nameplate, securely mounted on the door exterior, for each motor starter enclosure door identifying motor served, nameplate horsepower, full load amperes, code letter, service factor and voltage/phase rating.

- Install in accordance with manufacturer's instructions and per NEC 110.26.

***END OF SECTION***