PART 1 GENERAL

1.01	SECTION INCLUDES

Automatic Transfer Switches

1.02	RELATED WORK

Section 26 32 13	Packaged Engine Generator Systems

1.03	REFERENCES

- NEMA ICS 1—General Standards for Industrial Control and Systems.

- NEMA ICS 2—Standards for Industrial Control Devices, Controllers, and Assemblies.

- NEMA ICS 6—Enclosures for Industrial Controls and Systems.

- NFPA 70—National Electrical Code (NEC)

- NFPA-110—Standard for Emergency and Standby Power Systems.

- NEC 700—Emergency Systems.

- NEC 701—Legally Required Stand-By Systems.

- NEC 702—Optional Stand-By Systems.

1.04	QUALITY ASSURANCE

Manufacturer:  Company specializing in automatic transfer equipment with three (3) years’ experience.

1.05	SUBMITTALS

A.	Submit product data under provisions of Division 01.

B.	Submit product data for transfer switches showing overall dimensions, electrical connections, electrical ratings, and environmental requirements.

C.	Submit manufacturer's installation instructions under provisions of Division 01.

1.06	OPERATION AND MAINTENANCE DATA

A.	Submit operation and maintenance data under provisions of Division 01.

B.	Include instructions for operating equipment.

C.	Include instructions for operating equipment under emergency conditions.

D.	Identify operating limits which may result in hazardous or unsafe conditions.

E.	Document ratings of equipment and each major component.

F.	Include routine preventive maintenance and lubrication schedule.

G.	List special tools, maintenance materials, and replacement parts.

H.	Provide three (3) copies of all service manuals and related software.  The software shall be an open architecture that is not proprietary to one manufacturer.

I.	Provide twelve (12) hours of on-site training over the course of two days for up to two of the owner’s technicians.

1.07	REGULATORY REQUIREMENTS

Conform to NFPA 110 code for emergency electrical systems.

PART 2 - PRODUCTS

2.01	MANUFACTURERS

- ASCO (Automatic Switch Company)

- Onan

- Zenith Controls

- Kohler

- Substitutions: Under provisions of Division 01

2.02	AUTOMATIC TRANSFER SWITCH

A.	Description:  NEMA ICS 2; automatic transfer switch.

B.	Configuration:  Electrically-operated, mechanically-held, 4-wire, 4 pole transfer switch with programmed transition.

2.03	RATINGS

A.	Ratings:  NEMA ICS 2; as scheduled on drawings

B.	Ratings:  Level 1 per NFPA 110

2.04	AUTOMATIC SEQUENCE OF OPERATION

A.	Initiate Time Delay to Start Alternate Source Engine Generator:  Upon initiation by normal source monitor.

B.	Time Delay to Start Alternate Source Engine Generator:  0 to 60 seconds, adjustable, set at 2 seconds.

C.	Initiate Transfer Load to Alternate Source:  Upon initiation by normal source monitor and permission by alternate source monitor.

D.	Time Delay before Transfer to Alternate Power Source:  0 to 60 seconds, adjustable, set at 3 seconds.

E.	Initiate Retransfer Load to Normal Source:  Upon permission by normal source monitor.

F.	Time Delay before Transfer to Normal Power: 0 to 60 seconds, adjustable, set at 3 seconds; bypass time delay in event of alternate source failure.

G.	Time Delay before Engine Shut Down:  0 to 30 minutes, adjustable, set at 5 minutes, of unloaded operation.

H.	Engine Exerciser:  Start engine weekly; run for 30 minutes before shutting down.  Bypass exerciser control if normal source fails during exercising period.

I.	Alternate System Exerciser:  Transfer load to alternate source during engine exercise period.

2.05	ENCLOSURE

Enclosure:  ICS 6; Type 1

2.06	ACCESSORIES

A.	Indicating Lights:  Mount in cover of enclosure to indicate NORMAL SOURCE AVAILABLE, ALTERNATE SOURCE AVAILABLE, and SWITCH POSITION.

B.	Test Switch:  Mount in cover of enclosure to simulate failure of normal source.

C.	Return to Normal Switch:  Mount in cover of enclosure to initiate manual transfer from alternate to normal source.

D.	Transfer Switch Auxiliary Contacts:  Two (2) normally open; two (2) normally closed.

E.	Normal Source Monitor:   Monitor each line of normal source voltage and frequency; initiate transfer when voltage drops below 85 percent or frequency varies more than 3 Hertz from rated nominal value.

F.	In-Phase Monitor:  Inhibit transfer until source and load are within 5 electrical degrees.

G.	Remote Transfer Switch:  Alarm and indication panel in building per NFPA 110 and Local Code.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Verify that surfaces are ready to receive work.

B.	Verify field measurements are as shown on drawings.

C.	Verify that required utilities are available, in proper location, and ready for use.

D.	Beginning of installation means acceptance of existing conditions.

3.02	INSTALLATION

A.	Install in accordance with manufacturer's instructions (interior only).

B.	Four pole ATS and generator systems shall be bonded at the Automatic Transfer Switch.  At a minimum, the following loads are to be connected to the generator; Emergency Lights, Exit Lights, Fire Alarm System, Intercom System, Telephone System, and the cooler freezer system in the cafeteria.  However if the project is being designed as a shelter area, refer to the “Design Guideline for Emergency Loads in Primary Shelters” document found in the appendix. NEC Section 700 loads shall have a dedicated ATS.  All other non-emergency loads (i.e., NEC Sections 701 and 702) shall have a dedicated ATS.

C.	See Sheet E-EDG in the appendix for details.

3.03	WARRANTY

A.	Equipment, parts, and labor shall be warranted to be free from defects in material and workmanship for a period of five (5) years from date of final substantial completion and acceptance of system by Owner.

B.	Contractor shall arrive on site within two (2) normal business days to repair system under warranty.  All repairs shall be completed within one (1) week.

C.	Failure to respond in time specified shall result in School Board Maintenance Department making repairs and charging warrantor all labor and material necessary for repairs. It is agreed by this Contractor that this remedy will not void any warranties.

Appendix References: Electrical Distribution Grounding System Detail

Emergency Standby Generator Detail

END OF SECTION

THIS PAGE INTENTIONALLY LEFT BLANK