PART 1 GENERAL

1.01	WORK INCLUDED

A.	The work required under this Division shall include all materials, labor and auxiliaries required to furnish and install complete surge suppression for the protection of building electrical and electronics systems from the effects of line induced transient voltage surge and lightning discharge as indicated on drawings and specified in this Section.

B.	Related work specified elsewhere:

- Section 26 05 10	Basic Electrical Requirements

- Section 26 05 33	Conduit, Raceways, and Boxes

- Section 26 05 19	Building Wire and Cable

1.02	QUALITY ASSURANCE

A.	All Surge Protective Devices (SPD) shall be manufactured by a company normally engaged in the design, development, and manufacture of such devices for electrical and electronics systems equipment.

B.	The surge protective device manufacturer shall offer technical assistance through support by a factory representative and local stocking distributor.

C.	Submittals:  Surge Protective Devices submittal shall include:

1)	Schematic data on each suppressor type indicating component types.

2)	Dimensioned drawing of each suppressor type.

3)	Manufacturer's performance data for each suppressor type.

4)	Manufacturer shall furnish complete maintenance and installation manuals and a list of replacement parts.

5)	The manufacturer shall certify that their SPD device has been designed and tested to fail in a safe, non-violent mode with no smoke, fire, flame, case, or module physical damage.

6)	Manufacturer shall submit the cover page of the manufacturer’s UL Test Report to show compliance with UL 1449, Third Edition.

7)	Manufacturer shall submit UL documents listing UL clamping voltages for each unit being submitted.

D.	Equipment Certification:  Items shall be listed by Underwriters' Laboratories as an assembly, shall bear the UL seal and be marked in accordance with referenced standard U.L. 1449, Third Edition.  Protection modes shall be as follows:  seven (7) modes Wye = L-N, L-G, N-G; six (6) modes Delta = L-G, L-L.

E.	Surge suppression devices shall be installed and located in accordance with requirements of all applicable National Fire Protection Association (NFPA) Codes.

F.	Manufacturer shall have a minimum of ten (10) years experience in the design, development, and manufacture of SPD equipment and a minimum of one (1) year experience with the technology being submitted and installed in the field.

1.03	WARRANTY

A.	All surge protective devices shall be warranted for a minimum period of ten (10) years with free replacement of the device by the Manufacturer if the device fails to perform for any reason within those ten (10) years.  Replacement shall be interpreted to include parts and shipping costs only.

B.	It is the intent that failed devices shall be replaced at no cost to Owner throughout the 10-Year Warranty period.

1.04	CODES AND STANDARDS

The following standards and publications are referenced in various parts of this specification and shall apply.

- UL 1283, Sixth Edition—Standard for Electromagnetic Interference Filters.

- UL 1449, Third Edition—Standard for Surge Protective Devices

- ANSI/IEEE C62.41.1—IEEE Recommended Practice for Surge Voltages in Low- Voltage AC Power Circuits.

- ANSI/IEEE 62.11—IEEE Standard for Metal Oxide Surge Arrestors for AC Power Circuits (>1 kV).

- ANSI/IEEE C62.45—IEEE Recommended Practice for Surge Testing for Equipment Connected to Low-Voltage (1000V and Less) AC Power Circuits.

1.05	REQUIRED SUPPRESSORS

Provide U.L. surge protective device for the equipment described herein and as indicated on the drawings:

- On electrical service entrance panels

- On distribution and branch circuit panels

PART 2 - PRODUCTS

2.01	SUPPRESSORS FOR ELECTRICAL SERVICE ENTRANCE PANELS, SECONDARY PANELS, OR BRANCH PANELS

- Surge Protective Devices shall be installed at the service entrance on the load side of the first main disconnect.

- SPD shall be installed as close as feasible to the device being protected in a position which will minimize lead length between suppressor and the buses or control breaker to which the suppressor connects.  SPD leads shall not extend beyond the suppressor manufacturer's recommended maximum lead length without specific approval of the Engineer.

- SPD shall be designed for the specific type and voltage of electrical service and shall provide clamping action for line to neutral, line to ground, and neutral to ground.

- SPD shall be designed to withstand a maximum continuous operating voltage of not less than 115% of nominal RMS line voltage for 120V and 115% of nominal RMS line voltage for 277V.

- The SPD shall be life cycle tested as per ANSI/IEEE 62.45 to withstand 1,000 test surges at 10 KA for service entrance devices and 1,000 test surges at 3 KA for all other applications without failure or degradation of UL 1449 clamp voltages by more than 10%.

- SPD shall be UL 1449, Third Edition, listed for all specified suppression modes and shall be approved for the location in which they are installed.

- SPD shall have an operating temperature range of -10 degrees C to +50 degrees C.

- Provide visible/audible or redundant visible alarm systems to indicate when the unit is operable and when it has failed.  The alarm system shall be provided for each coupling mode.

- Devices shall be marked with their short circuit current rating as per Article 285 of the 2014 NEC and shall be rated as such to comply with the minimum A.I.C. rating of the service gear and or panelboard in which the SPD is to be installed.

- SPD’s shall be compliant with UL 96A for Master Labeling of the Lightning Protection System.

- SPD’s shall be UL 1449 Third Edition listed with a 20kA In rating.

2.02	SUPPRESSOR CRITERIA:  SUPPRESSORS SHALL MEET OR EXCEED THE FOLLOWING

CRITERIA

A.	Service Entrance (2 device types)

277/480 Volt, 3 Phase, 4 Wire plus ground, Wye and 120/208 Volt, 3 Phase, 4 Wire plus ground, Wye.

a)	Minimum Single Impulse Current Rating:  100,000 amperes per coupling mode (8/20 μs waveform).  Per phase rating shall be 200 kA for L-N and L-G.

b)	SPD shall be failsafe, shall not holdover current, shall have repeated surge capability, shall be self-restoring, and shall be fully automatic.

c)	The ANSI/IEEE C62.41.2, Category B/'C Low' clamping voltage shall not exceed the following (including any integral disconnects):

| VOLTAGE | L-N | N-G | L-G |
| --- | --- | --- | --- |
| 120/208 | 750 | 750 | 750 |
| 277/480 | 1200 | 1200 | 1200 |

d)	Where direct connections are not provided, terminals shall be provided for all of the necessary power, neutral, and ground connections.  Each terminal shall accommodate a minimum wire size of #8 AWG.

B.	Distribution and Branch Circuit Panels: (1 device type)

1)	277/480 Volt, 3 Phase, 4 Wire plus ground, Wye.

a)	Minimum Single Impulse Current Rating:  50,000 amperes per coupling mode (8/20 μs waveform).  Per phase rating shall be 100 kA for L-N and L-G.

b)	SPD shall be failsafe, shall not holdover current, shall have repeated surge capability, shall be self-restoring, and shall be fully automatic.

c)	The ANSI/IEEE C62.41.2 Category B/'C Low' clamping voltage shall not exceed the following (not including any integral disconnects):

| VOLTAGE | L-N | N-G | L-G |
| --- | --- | --- | --- |
| 277/480 | 1200 | 1200 | 1200 |

d)	Where direct connections are not provided, terminals shall be provided for all of the necessary power and ground connections.  Each terminal shall accommodate a minimum wire size of #8 AWG.

2)	120/208 Volt, 3 Phase, 4 Wire plus ground, Wye (1 device type)

a)	Minimum Single Impulse Current Rating:  50,000 amperes per coupling mode (8/20 μs waveform).  Per phase rating shall be 100 kA for L-N and L-G.

b)	Suppressors shall be failsafe, shall not holdover current, shall have repeated surge capability, shall be self-restoring, and shall be fully automatic.

c)	The ANSI/IEEE C62.41.2 Category B/'C Low' clamping voltage shall not exceed the following (not including any integral disconnects):

| VOLTAGE | L-N | N-G | L-G |
| --- | --- | --- | --- |
| 120/208 | 750 | 750 | 750 |

d)	Where direct connections are not provided, terminals shall be provided for all of the necessary power and ground connections.  Each terminal shall accommodate a minimum wire size of #8 AWG.

e)	All computer power panelboards shall have integral SPD protection.

2.03	ACCEPTABLE MANUFACTURERS

- Liebert

- Ditek Corporation

- Erico, Inc.

- PQ Protection

- Advanced Protection Technologies (A.P.T.)

PART 3 - EXECUTION

3.01	INSTALLATION OF SUPPRESSORS

A.	Suppressors shall be installed as close as practical to the electric panel to be protected.

B.	Suppressors shall be installed in a neat, workmanlike manner.  Lead dress shall be as short and as straight as possible and be consistent with recommended industry practices for the system on which these devices are installed.

C.	Equipment shall be installed following manufacturer's recommendations and guidelines in compliance with NEC Articles 250/285 for grounding and bonding; NEC Article 110.9 and 110.10 for overcurrent protection.

D.	All surge suppression devices specified in this specification section shall be designed and installed such that normal operation of the system shall not be impaired by the installation of these devices.

E.	All SPD devices shall be installed and connected to overcurrent devices. Tap or Buss connections are not acceptable.

F.	On site verification of proper installation by the SPD Manufacturer shall be included at no additional cost to the owner.

END OF SECTION