PART 1 - GENERAL

1.01	SECTION INCLUDES

- Exterior Luminaires and Accessories

- Poles

1.02	REFERENCES

- UL 1598—Luminaires

- UL 8750—Standard for Light Emitting Diode (LED) Equipment for Use in Lighting Products

- ANSI C136.36A—American National Standard for Roadway and Area Lighting Equipment – Aluminum Lighting Poles

- ANSI/NFPA 70—National Electrical Code

- ANSI/IES RP-20—Lighting for Parking Facilities

1.03	SYSTEM DESCRIPTION

Parking area/exterior lighting as indicated on documents and described herein.

1.04	DESIGN REQUIREMENTS

A.	Design and layout lighting system in conformance with IES recommended procedures.

B.	Parking Lot:  ANSI/IES RP-20, high activity level.

1.05	PERFORMANCE REQUIREMENTS

- Parking Area:  Provide illumination levels and uniformity indicated on drawings.

- Coordinate with landscape architect.

1.06	SUBMITTALS

A.	Submit under provisions of Division 01.

B.	Shop Drawings:  Indicate dimensions and components for each luminaire which is not a standard product of the manufacturer.

C.	Product Data:  Provide dimensions, ratings, and performance data.

D.	Manufacturer's Instructions:  Indicate application conditions and limitations of use stipulated by product testing agency specified under Regulatory Requirements.

E.	Manufacturer's Instructions:  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of product.

1.07	PROJECT RECORD DOCUMENTS

A.	Submit under provisions of Division 01.

B.	Accurately record actual locations of each luminaire.

1.08	OPERATION AND MAINTENANCE DATA

A.	Submit under provisions of Division 01.

B.	Maintenance Data:  Include instructions for maintaining luminaires.

1.09	QUALIFICATIONS

Manufacturer:  Company specializing in manufacturing products specified in this Section with minimum three (3) years’ experience.

1.10	REGULATORY REQUIREMENTS

A.	Conform to requirements of ANSI/NFPA 70.

B.	Furnish products listed and classified by Underwriters Laboratories, Inc. as suitable for purpose specified and shown.

1.11	DELIVERY, STORAGE, AND HANDLING

A.	Deliver, store, protect, and handle products to site under provisions of Division 01.

B.	Accept products on site.  Inspect for damage.

C.	Protect poles from finish damage by handling carefully.

1.12	COORDINATION

Furnish bolt templates and pole mounting accessories to installer of pole foundations.

PART 2 - PRODUCTS

2.01	PRODUCTS

A.	Light Poles

1)	Manufacturers shall be Lithonia, Valmont, or Hapco.  Equals may be considered but must be approved prior to bidding.  (Lithonia #RTA258G and #RTA358J, Basis for Design.)

2)	Light poles shall be cast aluminum, round tapered (minimum 8” diameter) with a 4-bolt anchor base designed for side-mount light fixtures.

a) 	Elementary School:  Provide twenty-five foot (25’) poles.

b)	Middle School:  Provide twenty-five foot (25’) poles or thirty-five foot (35’) poles depending on site conditions.  Coordinate with Owner prior to ordering.

c)	High School:  Provide thirty-five foot (35’) poles.

3)	Poles and light/pole combinations shall be rated for Florida Building Code wind load requirements.

4)		Concrete poles shall not be acceptable.

B.	Pole Light Fixtures

1)	Fixtures shall be LED fixtures by Lithonia or pre-approved equal.

2)	All poles shall be provided with individual in-line-fusing installed at the base of each pole.  Provide a Tron HEB-JK fuse holder and a KTK 5 amp fuse. See Paragraph 3.02.B.3.

3)	Light fixtures shall be die-cast aluminum designed for pole side mounting.

C.	Poles and light fixtures typically to be dark bronze.  Engineer may select other color finishes to suit architecture and exterior building décor/colors.

D.	Pre-Cast Base shall be required.

See site pole detail

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Examine excavation and concrete foundation for lighting poles.

B.	Examine each luminaire to determine suitability for lamps specified.

3.02	INSTALLATION

A.	Existing Facilities:

1)	Contractor shall be responsible for cutting loose and removing all overhead electrical services to existing poles, as indicated.  Abandoned/removed lighting systems, poles, conductors, hardware, etc., shall be removed in it entirety.  Conductors and services shall be removed back to its origination point.

2)	All existing site, parking, and security lighting being removed shall remain operational until new system is installed and working.

3)	Contractor shall verify all underground utilities and walk jobsite prior to any underground work with necessary hand digging as required to insure safety.

4)	All work shall be coordinated with Owner.  Contractor shall maintain necessary safeguards, barricades, signage, etc., warning against hazards with minimum interference and no obstructions causing endangerment to the facility occupants’ ability to enter and exit facility.

5)	Installation method shall be directional boring.  However, if minimal trenching is necessary, all trenching shall be covered daily with no unattended exposed sections.  Any trenches shall be compacted as they are backfilled with grass areas neatly raked adjacent to trench.  Grass area shall be restored to original condition with sod only, no seed allowed.

6)	Any trimming of existing trees shall be by a qualified, licensed company as noted or at the discretion of the Owner.

7)	During demolition, Contractor shall remove all abandoned conductors back to their over-current device.  All exposed, abandoned conduits shall be removed.

8)	Contractor shall provide equipment as required to install pole lights and/or poles in areas not accessible by vehicles.

9)	All existing paving, curbing, parking striping, and walks shall be restored to original condition.

10)	All existing underground systems (i.e., irrigation, etc.) shall remain functional and operational during the course of construction.  Any damage to systems due to construction shall be the sole responsibility of the Contractor to replace or repair to previous or better condition.

11)	All existing poles, lighting, electrical equipment, and overhead aerial cables are to remain as is unless otherwise noted

B.	New and Existing Facilities:

1)	All wiring/conductors up poles to light fixtures shall be #10 stranded copper with in line fusing at base/handhole of each pole.

2)	Exothermically weld a #6 solid bare copper conductor to ground rod in the wiring access section (18” pigtail).  Run this pigtail through the lug which is attached to the pole and splice to the equipment grounding conductor.

3)	Individual over-current protection/fusing shall be installed at the base of each pole to protect the fixtures.  The fuse holders shall be:  Tron HEB-JK weatherproof fuse holders with weatherproof boots and Bussman Limitron KTK-5 Amp fuses.  Any deviations from these specifications must be approved by the electrical inspector.

4)	All circuit conductors that are spliced or pulled through the hand hole shall be a minimum length of 18” long.

5)	Splice all wires with wing nuts and tape with plastic, electrical tape.  All splices shall have the wirenut up.

6)	All raceways to contain a minimum #10 THHN green equipment-grounding conductor.

7)	No above grade or below grade junction boxes or pull boxes.

8)	All fixtures, brackets (arms) shall be installed according to the manufacturer’s written instruction.

9)	Provide and install surge protectors on the load side of the contactor.  The surge protector shall be a Square D Cat. #SDSA3650.

10)	It shall be the Electrical Contractor’s responsibility to contact “Sunshine” prior to digging on School Board property.  In addition to incoming utilities, other underground obstructing and shall be, but not limited to:

Possible underground utilities:

- Primary electrical conductors

- Secondary electrical conductors

- Gas piping

- Telephone cables

- TV cables

- Sprinkler conductors (low voltage)

- Sprinkler piping

- Potable water piping

- Reclaimed water piping

- Sanitary sewer piping

- Storm drainage piping

- Branch circuit conductors

- Fiber Optics

- Chiller/HVAC piping

11)	The parking lot/perimeter lighting systems shall be controlled from one location (typically in an electrical/mechanical room, as shown on drawings). The control itself shall be an auto/off/hand control (Square D Cat. #9999 SC2 auto/off/hand control).  Provide primary control through energy management control system (coordinate with Division 015 Contractor).  For redundant control, also provide, install, and wire into the control circuit a Paragon EC7000 series time clock and Precision T-30 photocell for the automatic operation of the lights.  The lighting contactor shall be Square D Class 8903 SMG81V02A12 30A/600v electrically held circuit breaker combination disconnect/lighting contactor.  The Contractor shall verify coil voltage prior to ordering equipment.  Install a separate branch circuit out of the nearest 120/208 Volt panelboard in the electrical room.

12)	The Contractor shall supply and install a Square D split reducer (Cat. #LBA362104) in each of the lighting contactors to distribute power from the load side of the contactor to the pole light conductors.

13)	The Contractor shall supply and install a pole light numbering system.  The poles shall be numbered according to the drawings or by approval of the owner.  Each school will start from #1 and continue until all poles are numbered.  The number shall be Panduit 2-1/2” reflective numbers Cat. #PRL250YB-O through PRL250YB-9.  They shall be installed six feet (6’) A.F.G. so as to not interfere with the access cover plate.  The numbers shall be installed so as to make them easily readable from the closest street or be read from the front of the various buildings.  Please see the Electrical Inspector or project Coordinator for the exact intent of numbering locations.

14)	Contractor shall stake mark center of all pole bases and receive approval of layout from Owner prior to installation.  If Contractor installs poles without approval, the Contractor shall relocate at Owner's request.

C.	Use details provided by the Pinellas County School Board for all site and lighting poles installed for School Board projects.

D.	Operate each luminaire after installation and connection.  Inspect for improper connections and operation.

3.03	ADJUSTING

A.	Adjust work under provisions of Division 01.

B.	Aim and adjust luminaires to provide illumination levels and distribution as directed.

C.	Relamp luminaires which have failed lamps at date of Substantial Completion.

3.04	CLEANING

- Clean work under provisions of Division 01

- Clean electrical parts to remove conductive and deleterious materials

- Remove dirt and debris from enclosure

- Clean photometric control surfaces as recommended by manufacturer

- Clean finishes and touch up damage

3.05	WARRANTY

A.	Equipment, parts, and labor shall be warranted to be free from defects in material and workmanship for a period of one (1) year from date of final substantial completion and acceptance of system by Owner.

B.	Contractor shall arrive on site within two (2) normal business days to repair system under warranty.  All repairs shall be completed within one (1) week.

C.	Failure to respond in time specified shall result in School Board Maintenance Department making repairs and charging warrantor for all labor and materials associated with the repairs. It is agreed by this contractor that this remedy shall not void any warranty.

Appendix Reference:	Site Pole Details

END OF SECTION