PART 1 - GENERAL

1.01	SECTION INCLUDES

PART 2 - PRODUCTS

2.01

PART 3 - EXECUTION

3.01	BASKETBALL/TENNIS COURT/PLAYCOURT POLE RECEPTACLE INSTALLATION

A.	Install a 20 amp, Spec Grade, receptacle on the backside of the nearest basketball post at minimum of 18" above finished grade.  Provide a separate branch-circuit homerun to the panelboard in a 1" minimum conduit.  Install a single-pole toggle switch adjacent to the panelboard to control the receptacle on the basketball court. Use type FD box.  Use gasketed type weather-proof in-use cover.

B.	Exterior conduits installed in areas above finished grade shall be 1" rigid hot dipped galvanized steel.  Rigid conduit shall extend down to and include a 90 degree factory elbow.  Then, it is permissible to change over the Schedule 40 PVC conduit.

C.	The branch-circuit conductors shall be #10 THHN/THWN the entire length from the over current device to the receptacle.

D.	Provide and install a 20 amp GFCI breaker of the same manufacturer of the panelboard in which the branch-circuit originates.

E.	Install ground rod at one corner of the court in accordance with Grounding and Bonding specification section.

F.	Provide a #4 AWG solid copper grounding electrode conductor from the ground rod to structural steel.  All connections shall be exothermically welded.

3.02	KILNS

3.03	PEDANT CORD OUTLET

3.04	HAND DRYERS

3.05	COOLER/FREEZER LIGHTS

3.06	RELOCATABLE POWER/SYSTEM SUPPORT SYSTEMS

3.07	ELECTRONIC MARQUEES (Refer back to 10 73 33)

END OF SECTION