PART 1 - GENERAL

1.01	SECTION INCLUDES

- Exterior Luminaires and Accessories

- Poles

1.02	REFERENCES

- ANSI C78.379—Electric Lamps—Incandescent and High-Intensity Discharge Reflector Lamps—Classification of Beam Patterns

- ANSI C82.4—Ballasts for High-Intensity-Discharge and Low-Pressure Sodium Lamps (Multiple-Supply Type)

- ANSI/NFPA 70—National Electrical Code (NEC)

- NEMA Publication FA-1

1.03	SYSTEM DESCRIPTION

The performance criteria requires lighting equipment which shall provide initial average light levels of 62.5 foot candles.  A maintenance factor of 0.8 is to be used in determining the initial value after adjustment for a tilt factor.  These initial light levels shall provide a maintained lighting level of 50 foot candles.  The light levels are to be stated in the numeric values to be obtained during the initial hours of operation of the lighting system.  There shall be a maximum of 0.1 foot candles horizontally and vertically at the property line.

1.04	DESIGN REQUIREMENTS

A.	Design and layout lighting system in conformance with IES recommended procedures.

B.	Poles and light/pole combination shall be rated per Florida Building Code wind load requirements.

1.05	PERFORMANCE REQUIREMENTS

A.	Provide illumination levels and uniformity indicated above.

B.	Uniformity ratio:  The foot candle level shall have a uniformity ratio of maximum to minimum of not greater than 2.5:1 or better.  There shall be a maximum of 0.1 foot candles horizontally and vertically at the property line.

1.06	SUBMITTALS

A.	Submit under provisions of Division 01.

B.	Shop Drawings:  Indicate dimensions and components for each luminaire which is not a standard product of the manufacturer.

C.	Product Data:  Provide dimensions, ratings, and performance data.

D.	Manufacturer's Instructions:  Indicate application conditions and limitations of use stipulated by product testing agency specified under Regulatory Requirements.

E.	Manufacturer's Instructions:  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of product.

1.07	PROJECT RECORD DOCUMENTS

A.	Submit under provisions of Division 01.

B.	Accurately record actual locations of each luminaire.

1.08	OPERATION AND MAINTENANCE DATA

A.	Submit under provisions of Division 01.

B.	Maintenance Data:  Include instructions for maintaining luminaires.

1.09	QUALIFICATIONS

Manufacturer:  Company specializing in manufacturing products specified in this Section with minimum three (3) years’ experience.

1.10	REGULATORY REQUIREMENTS

A.	Conform to requirements of ANSI/NFPA 70.

B.	Furnish products listed and classified by Underwriters Laboratories, Inc., as suitable for purpose specified and shown.

C.	Design shall be in accordance with IES recommendations.

1.11	DELIVERY, STORAGE, AND HANDLING

A.	Deliver, store, protect, and handle products to site under provisions of Division 01.

B.	Accept products on site.  Inspect for damage.

C.	Protect poles from finish damage by handling carefully.

1.12	COORDINATION

Furnish bolt templates and pole mounting accessories to installer of pole foundations.

1.13	EXTRA MATERIALS

A.	Furnish under provisions of Division 01.

B.	Provide two of each lamp type and wattage installed.

C.	Provide two of each ballast type.

PART 2 - PRODUCTS

2.01	LIGHT STRUCTURE SYSTEM

A.	General Description:  The Basis of Design and specification for the Light Structure System is Musco Sports Lighting, Inc., Light Structure GREEN.  Other manufacturer’s equipment must be equivalent in all respects.  Equipment provided shall meet the following:

1)	Pre-stressed centrifically spun concrete base.

2)	Hot-dipped galvanized steel shafts.

3)	Hot-dipped galvanized steel cross arms.

4)	Fixture consisting of:  lamp, lamp socket, reflector, lens, lamp cone, reinforcing retaining ring.

5)	UL listed double fusing for the lamp circuits.

6)	Ballast and termination enclosure to consist of:  NEMA 4X enclosure with ballasts, termination blocks, and capacitors.

7)	Thermal magnetic breaker.

8)	All wiring from the load side of the breaker to the lamp socket.

9)	Plug-in or landing lug connection devices for all electrical circuits on the pole.

10)	Aiming method for alignment of the luminaries.

11)	Method for realignment of the luminaire after movement for relamping.

B.	Manufacturers:  Subject to compliance with requirements provide light structure system by the following:

- Musco Sports Lighting, Inc.

- Qualite Sports Lighting, Inc.

- Hubbell Lighting, Inc.

2.02	LUMINAIRE STRUCTURE

A.	The lamp and reflector mounting device shall be factory assembled to the cross arms and the cross arms shall be attached to a section of the pole by the Manufacturer.

B.	Each reflector shall be attached to the cross arm with its aiming position predetermined relative to all other fixtures on the pole such that all luminaries on the assembly are oriented to form a single photometric unit in the factory before shipment.

C.	Lamps shall be 1500 watt metal halide and shall meet ANSI designated MM48PC-

1500 BU and be Philips #MH1500BU, GE, Sylvania or Venture.

D.	A removable lens of impact and thermal resistant glass with silicone gasket shall be centered in a stainless steel lens rim and attached to the reflector with a hinged.

E.	The Manufacturer shall provide a memory positioning device for each luminaire on the assembly.  The device shall provide for automatic repositioning of the aiming after relamping.

F.	All steel components shall be hot-dipped galvanized ASTM A-123.  High purity reflector grade aluminum shall be alzak finished.  All other aluminum components shall be heavy anodized to military MIL-A-8625S Type III (commercial AAC12A41) specification and shall further be coated with an epocy primer and heavy top coat of polyurethane enamel.  All non-current carrying fasteners, hinges, and latches shall be stainless steel and shall be coated with a thermoset epoxy type organic coating such as Empigard to prevent galvanic interaction.

G.	Cross arms for the luminaire assembly shall be welded to the pole section before galvanized by certified welders.  Any additional fasteners used for the attachment of accessories to the cross arm shall be stainless steel and coated with Empigard or equivalent.

H.	The cross arm, reflector and its attachment to the pole shall be provided by the

Manufacturer such that it shall withstand winds of 145 mph.

2.03	WIRE HARNESS

A.	The wiring harness shall be supported at the top of the pole by a stainless steel wire mesh grip matched to the size of the harness.  There shall be not more than 13 conductors supported by a single wire mesh grip.  If harness is longer than 65’ an interim wire mesh grip support shall be located approximately half way down the pole.

B.	The wiring mesh grip shall be mechanically attached to the pole to an enclosed mounting loop so that it cannot accidentally be removed in any direction.

C.	All wiring harness conductors shall be color-coded and clearly labeled.

D.	Each end of the wire harness shall be terminated into a plug-in with conductors sequenced consistent with the pattern of the wiring schematic provided by the Manufacturer.

E.	All conductors and plug-ins shall be tested for resistance underload, for continuity, schematic sequence, and for insulation integrity.  Manufacturer shall ship with the wire harness a copy of the test results.

F.	There shall be included within the wiring harness one conductor for use as a grounding conductor.  The grounding conductor shall be equal in size to the load carrying conductors.  Provide lighting protection/grounding at each pole that meets requirements of NFPA 780.

2.04	ELECTRICAL COMPONENT ENCLOSURE (ECE)

A.	All ballast, fuses, capacitors, and disconnects (thermal magnetic breakers) shall be located in a central enclosure, approximately 10' above grade.  Wiring harnesses shall be properly secured from remote enclosure to top of pole, with wiring support grip, and rubber abrasion bumpers every 10’ to prevent abrasion from contact with inside of pole.

B.	The ECE shall be a NEMA 3R rated gasketed enclosure to house the ballasts, capacitors, fuses, thermal magnetic circuit breaker, and distribution lugs.

C.	The ECE shall be divided into two (2) compartments.  The upper compartment shall house the ballasts, capacitors, and fuses.  The lower compartment shall provide for the thermal magnetic circuit breaker, distribution lugs, and connection of all circuits coming into and out of the ECE.

D.	The ECE shall be heavy hot dip galvanized to ASTM A-123 standards after fabrication to a thickness of not less than 3 mils.

E.	All latches, hinges, and non-current carrying fasteners, outside and inside the enclosure, shall be stainless steel and shall further be coated with a clear thermoset polymer coating such as Empigard to prevent galvanic interaction.

F.	The access door to the ECE shall be attached by a full-length stainless steel hinge and shall be secured when closed by lockable stainless steel latches.

G.	There shall be provided within the ECE a UL listed thermal magnetic circuit breaker such that electrical power to all equipment on the pole served by the feeder circuit shall be disengaged by the operation of one switch.  The breaker shall be located in a compartment separated from any capacitors or ballasts.

H.	The breaker shall provide landing lugs for the conductors which provide power to the pole.

I.	There shall be provided an individual fuse for each ballast conductor except neutral conductors which shall not be fused or switched.

J.	Ballasts shall be lead peak auto regulating ballasts as manufactured by SOLA, Advance, or an approved equal, suitable for operation with 208 volt supply or 480 volt supply as indicated on drawings.

K.	Ballast enclosure/cabinet to be located opposite the cross arm/fixture side of pole for ease of maintenance access.

2.05	POLE STRUCTURES

A.	AASHTO structural design criteria shall be used to determine the pole stress allowance.

B.	The poles and foundations shall be designed to withstand sustained 150 mph.

C.	Pole Height:

1)	The height listed for the poles are the height above finished grade.  The total pole height including burial depth is to be determined by the supplier of the poles and shall include the height above finished grade and burial depth.

2)	The pole shall be designed to provide a mounting height as shown on the drawings above the surface at its foundation and to be of sufficient strength to support the effective projected area (EPA) of the pole and all of the attached devices including, as applicable, light fixtures, cross arms, mounting brackets, ballast boxes, and any other devices which are to be attached to the pole.

2.06	POLE MATERIAL

A.	Steel Poles:  The pole shaft shall be high strength low alloy tapered tubular steel with galvanized coating inside and out.  All connections of pole sections shall be by slip fitting of top section over the lower concrete section by a length of at least 1½” times the pole diameter.

B.	Concrete Poles:

1)	Centrifugally cast pre-stressed and reinforced round concrete.

2)	Materials:

a)	Coarse Aggregate:  Shall be clean washed limestone or granite with a maximum size of 3/8”, so graded as to achieve optimum quality in the finished product.

b)	Fine Aggregate:  Shall be clean washed concrete grade pit sand free of clay and other deleterious matter.

c)	Cement:  Shall be high early strength, equal to ASTM C-150, Type 3, and CSA Type 30.

d.	Water:  Shall be free of acids, alkalis, and organic materials.

e)	Steel:  Pre-stressing tendons shall conform to ASTM A416 and CSA G279.

f)	Steel:  Helical Reinforcing wire shall conform to ASTM A641 and shall have a hot dipped galvanized coating as per ASTM A641, Class 3.

C.	Provide three (3) feet lightning rod at pole top, bolted through pole with copper bolts, connected to earth ground with #3 copper conductor.

D.	Provide bird deterrents on each lighting pole that is not designated to have a bird nest platform.  Provide bird nest pole platforms at Owner’s specified locations. Provide four (4) bird nest pole platforms per site.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Examine excavation and concrete foundation for lighting poles.

B.	Examine each luminaire to determine suitability for lamps specified.

3.02	INSTALLATION

A.	Install in accordance with manufacturers' instructions.

B.	Install lighting poles at locations indicated.

C.	Install poles plumb.  Provide means to adjust plumb.  Grout around each base.

D.	Install lamps in each luminaire.

E.	Bond luminaires, metal accessories, and metal poles to branch circuit equipment grounding conductor.  Provide supplementary grounding electrode at each pole.

F.	Extend/bring all conduits into pole; no pull boxes/in ground boxes permitted.

3.03	FIELD QUALITY CONTROL

Operate each luminaire after installation and connection.  Inspect for improper connections and operation.

3.04	ADJUSTING

A.	Adjust work under provisions of Division 01.

B.	Aim and adjust luminaires to provide illumination levels and distribution as directed.

C.	Relamp luminaires which have failed lamps at date of Substantial Completion.

3.05	CLEANING

- Clean work under provisions of Division 01

- Clean electrical parts to remove conductive and deleterious materials

- Remove dirt and debris from enclosure

- Clean photometric control surfaces as recommended by manufacturer

- Clean finishes and touch up damage

END OF SECTION