ELECTRICAL DESIGN CRITERIA

Table of Contents

I.	GENERAL	1

II.	CRITERIA	2

A.	Submittals:	2

B.	Electrical load calculations:	3

C.	Fault Current Calculations:	3

D.	Riser diagrams:	3

E.	Florida Building Code – Energy Conservation:	3

F.	Floor Plan (Lighting):	4

G.	Floor Plan (Power):	4

H.	Panel Schedules:	5

I.	Elevators (NEC Article 620):	5

J.	Fire Pumps (NEC Article 695):	5

K.	Emergency, legally required standby or optional standby systems (NEC Articles 700, 701 and 702)	5

L.	Peak demand records:	6

M.	Signage:	6

# GENERAL

  - The design professional shall use this document in conjunction with the educational specifications and Pinellas County Schools (PCS) district master specifications to develop the design and contract documents.

  - Goals: the purpose of this Division 26 Electrical guideline is to provide consistent, uniform, quality, constructible construction documents for all PCS construction projects.  This will improve the building plan review process, maintainability of equipment and provide installation standardization.

  - This division contains requirements for the following elements:

    - Submittals

    - Electrical load calculations

    - Fault current calculations

    - Riser diagrams

    - Florida Building Code

    - Floor plan (lighting)

    - Floor plan (power)

    - Panel schedules

    - Elevators

    - Fire pumps

    - Emergency systems

    - Peak demand records

    - Signage

  - In this document, the term Engineer represents the professionally qualified design Engineer of Record or Engineering Consultant, duly licensed in the State of Florida, that signs and seals project construction documents.

  - The Engineer is the person responsible for the design and development of all project documents.

  - The design shall incorporate the latest design or code requirements.

    - National Electrical Code (NEC)

    - Illuminating Engineering Society of North America (IESNA)

    - Florida Building Code (FBC)

    - Florida Fire Prevention Code (FFPC)

    - Educational Specifications

    - National Fire Prevention Code (NFPA)

  - The criteria shall not limit or restrain the performance and liability of the professional or professionals responsible for the integrity and performance of the structure.

  - The criteria are applicable to new construction and to the remodeling and renovation of existing facilities.

  - The use of the criteria in this document does not exempt the design professionals from any federal or state code or standards controlling the design and construction of any facility.

  - Do not put electrical systems on the same drawings as the electrical power system.  Provide separate electrical systems drawings.

  - Drawing elements for electrical only projects:

    - On the cover page place the title block on the right edge of the page with the following information:

      - Sheet number.

      - Project name and description.

      - Issue date with revision column.

      - PCS project number/work order number.

      - Drawn by and date.

      - Checked by and date.

      - Project Architect/Engineer (PAE) name, address, phone numbers and email address.

      - Current Board Members and Superintendent.

      - Project issue date vicinity map drawing index.

      - 100% construction documents.

    - Number and label the drawings for electrical only projects with the following information:

Drawing Number     Drawing Title

      - E0.00	         ELECTRICAL SYMBOL LEGEND AND SCHEDULES

      - E0.01	         ELECTRICAL LEAD-IN SHEET

      - E0.02	         ELECTRICAL SHEET SPECIFICATIONS

      - E1.01	         ELECTRICAL DEMOLITION PLAN – SITE

      - E1.02	         ELECTRICAL DEMOLITION PLAN - BUILDING 1

      - E1.03	         ELECTRICAL DEMOLITION PLAN - BUILDING 2

      - E1.04	         ELECTRICAL DEMOLITION PLAN - BUILDING 3

      - E1.05	         ELECTRICAL DEMOLITION PLAN – ROOF

      - E2.01	         ELECTRICAL SITE PLAN

      - E2.02	          GROUNDING, DATA and POWER DISTRIBUTION PLAN

      - E3.03	          LIGHTING PLAN - BUILDING 1

      - E3.04	          LIGHTING PLAN - BUILDING 2

      - E3.05	          LIGHTING PLAN - BUILDING 3

      - E4.01	          POWER PLAN - BUILDING 1

      - E4.02	          POWER PLAN - BUILDING 2

      - E4.03	          POWER PLAN - BUILDING 3

      - E4.04	          POWER PLAN – ROOF

      - E5.01	          POWER ONE-LINE RISER DIAGRAM

      - E5.02	          COMMUNICATIONS BACKBONE RISER

      - E6.01	          ELECTRICAL SCHEDULES

      - E6.02	          ELECTRICAL SCHEDULES

      - E6.03	          ELECTRICAL SCHEDULES

      - E8.01	          ELECTRICAL DETAILS

      - E8.02	          ELECTRICAL DETAILS

      - E8.03	          ELECTRICAL DETAILS

      - E8.04	          ELECTRICAL DETAILS

      - EF8.01	          FIRE ALARM PLAN - BUILDING 1

      - EF8.02	          FIRE ALARM PLAN - BUILDING 2

      - EF8.03	          FIRE ALARM PLAN - BUILDING 3

      - EF8.04	          FIRE ALARM RISER AND DETAILS

# II.	CRITERIA

## Submittals:

- Electrical plans signed and sealed by a registered professional Engineer in the State of Florida.

- Electrical plans showing power and lighting for each floor and the location of all panel boards using the most current Florida Inventory of School Houses (F.I.S.H.) numbers.

- Electrical plans showing systems plans for each floor and the location of all MDF's and IDF's using the most current F.I.S.H. numbers.

- Electrical panel schedules showing the loads in VA or KVA and the A.I.C. rating.

- Riser diagram showing the point-to-point available fault current and the raceway and conductor size, type and grounding methods.

- A complete grounding electrode system detail that includes all items specified in NEC Article 250 for any transformers or other separately derived systems. Show how all items required to be bonded are tied together to comply with NEC 250.

- Fault current calculations through the panelboard level or to the point where the fault current is below 10K A.I.C.  Designate point-to-point in system calculated.

- Lighting power densities per the FBC, Energy Conservation and Section 26 51 00 of the PCS master specifications.

## Electrical load calculations:

- The design Engineer shall provide electrical load calculations, including a load summary showing all demand factors.

- The design Engineer shall provide the breakdown of connected loads into proper NEC categories (lighting, receptacles, motors, HVAC, kitchen equipment, appliances, etc.).

- Provide demand factors applied to each category of load.

- Provide total connected load in VA or KVA.

- Provide total calculated amps.

- PCS submittal requirement: panel board load calculation worksheet completed for all panel boards or shown in panel schedule.

## Fault Current Calculations:

- Submit enough information provided to clarify calculation.

- Utility transformer size in KVA and impedance (%Z) or known available fault current at the utility transformer.

- Conduit and wire size, type and length.

- Service equipment, panel boards, etc. A.I.C. rating.

- Complete fault current information through the panel board level.

- Arc flash protection compliance with 110.16.

## Riser diagrams:

- PCS submittal requirement: clearly identified service point.

- Provide service equipment ampacity, A.I.C. rating and overcurrent protection.

- Provide feeder conduit size and type, conductor size and type and number of conductors.

- Provide ground fault protection of equipment where required.

- Provide a grounded service conductor sized for the maximum unbalanced load.

- Show all service conduit's size and type, number of parallel runs, conductor's size and type and number of conductors.

- Show all overcurrent protection of conductors.

- Show tap conductor length(s) to overcurrent protective devices for all items shown in NEC 240.21 (a) through (g).

- Provide grounding electrode system, including concrete encased electrode, grounding electrode conductor and main bonding jumper are sized properly.

- Type of equipment grounding conductor for feeders shall be shown.

- Grounding electrode system, grounding electrode conductor and equipment bonding conductor shall be sized properly for separately derived systems.

- Grounding electrode system and grounding electrode conductor shall be sized properly when more than one building is supplied from a common service or feeder.

- Overcurrent protection of transformers shall be properly sized.

- Service and feeder raceway conductor fill shall comply with the NEC.

## Florida Building Code – Energy Conservation:

- Provide voltage drop calculations showing no greater than 2% voltage drop on all service entrance and feeder conductors.

- Electrical plans shall correspond to the energy calculation provided, including number and type of lighting fixtures, the occupancy type and the watts per square foot allowed.

- Electrical plans denote the type and location of all lighting fixtures.

- Provide automatic shutoff control of interior lighting to school classrooms and office buildings greater than 5,000 square feet.

- Electrical plans denote all required switch, occupancy/vacancy sensor and daylight sensor locations.

- Automatic shutoff control of exterior lighting through the Building Management System (BMS system).

- Provide branch circuit voltage drop calculations for large loads (i.e. motors ≥ 10 Hp, electric boilers, heat loads, etc.).

## Floor Plan (Lighting):

- High intensity discharge lighting shall not be used.

- Show homerun conduits and include size, type and number of conductors.

- Emergency lighting shall be clearly denoted on plans and include:

- Shall be designed to the requirements in FBC and NFPA.

- Shall have a minimum of two (2) per classroom.

- Emergency lighting on generator emergency circuits shall have override relays to turn lights on upon loss of normal power.

- Provide emergency lighting in all electrical and mechanical rooms.

- All luminaires shall be LED type.

- Photometrics shall be provided for all site lighting, typical classrooms and all assembly areas.

- Site lighting:

- Shall follow all FBC and IESNA guidelines.

- Shall have 0.0 FC at all property lines.

- Shall be controlled by BMS.

- All poles/luminaires shall be matching in color.

## Floor Plan (Power):

- Denote locations on electrical plans for all motors, compressors, heaters, stationary appliances, etc.

- Electrical plans shall denote the location of all electrical distribution equipment.

- All electrical equipment shall have working clearance shown, as required.

- Provide GFCI protection as required.

- Provide receptacle outlet locations as required.

- Branch circuits shall be properly sized for the load.

- Homerun conduits showing size, type and number of conductors.

- PCS submittal requirement: electrical equipment schedule shall be provided.

- Personnel doors: where equipment rated 800 amps or more contains overcurrent devices and there are personnel doors intended for entrance to and egress from the working space less than 25' from the nearest edge of the working space, the doors shall open in the direction of the egress and be equipped with listed panic hardware.

- The Owner shall approve all floor box locations.

- All distribution systems shall be fully rated.  Series rating not allowed.

- Half-sized or tandem breakers shall not be used.

- Provide a surge protection device in all panels.

- Panelboards/switchboards shall be provided with a minimum of 20% spare spacing for future additions.

- Stub three (3) empty 3/4" conduits and two (2) empty 1" conduits to accessible location above ceiling out of each recessed panelboard.

## Panel Schedules:

- Circuit modifications shall be legibly identified as to its clear, evident and specific purpose of use.

- Provide panelboard buss rating in voltage and amps.

- Provide panelboard ampacity, A.I.C. rating and overcurrent protection.

- Provide main breaker size or main lug only is shown.

- Panel schedule shall denote double lugs or feed-through lugs.

- Provide an accurate description or coding for each branch circuit.

- Provide the connected load of each branch circuit shown in VA or KVA.

- Provide the total connected and calculated load shown in VA or KVA.

## Elevators (NEC Article 620):

- Overcurrent protective devices for each elevator car light and shall be located in the elevator machine room.

- Provide a separate branch circuit for the elevator machine room receptacles and light.

- Provide a separate branch circuit for the elevator pit receptacles and light.

- Selective coordination of the elevator driving machine overcurrent protective device.

- Wiring methods shall comply with NEC 620.21.

- All 125-volt receptacles shall be GFCI protected.

- Pit lighting shall be a minimum of 10 FC measured at the pit floor.

- Pit receptacles shall be mounted a minimum of 12” above the pit floor.

## Fire Pumps (NEC Article 695):

- Normal power shall be supplied by a separate service or by a tap located ahead of and not within the same enclosure as the service disconnecting means.

- The normal power source shall be capable of carrying the locked rotor current of the fire pump motor indefinitely.

- Fire pump has generator backup power.

- Supervision for the fire pump circuit shall be provided.

- All transformers associated with the fire pump installation shall comply with NEC 695.5.

- All power wiring associated with the fire pump installation shall comply with NEC 695.6.

- The fire pump controller or fire pump transfer switch shall not supply any load other than the fire pump.

- Voltage drop calculations shall be provided.

## Emergency, legally required standby or optional standby systems (NEC Articles 700, 701 and 702)

- Generators shall comply with NEC 445.

- UPS shall comply with NEC 480.

- Separate service (when allowed).

- Systems shall be properly sized for the load.

- Generator load calculation for healthcare facilities shall comply.

- Multiple transfer switches required.

- Emergency systems shall be totally separate from all other systems.

- Service rated disconnect shown for generators located outside the building.

- The following systems shall be connected to the generator:

- Emergency lighting.

- Fire alarm system.

- Walk-in cooler/freezer.

- Data racks and all receptacles in the MDF and IDF’s.

- Intrusion detection system.

- Access control system.

- Video surveillance system.

- Elevator.

- PCS owned and operated lift stations.

- Emergency Responder Communication Enhancement System (ERCES).

- PCS radio repeater system.

## Peak demand records:

- Starting and ending dates of the metering.

- Highest reading of the metering period clearly shown.

- Power factor adjustment shown, when necessary.

- Explain the details of seasonal and occupancy adjustment factors.

- Utility demand records or recordings of demand metering for the peak period must accompany the submittal.

## Signage:

- Arc flash warning labels shall be provided.

- Identification of ungrounded conductors. The branch circuit color code shall be posted at each panel board location. This shall be a permanent plaque.

- Identification of all feeders, services or branch circuits that supply or pass through the building.  This identification will be a permanent plaque at each disconnect location denoting the location of all other disconnects and the area served by each.

- A permanent plaque shall identify fire pump disconnecting means.

- A permanent plaque shall be placed at the fire pump controller stating the location of the disconnecting means and the location of the key if locked.

- A permanent plaque shall be placed at the service equipment denoting the type and location of onsite emergency power.

- A permanent plaque shall identify the connection of the grounding electrode conductor for the emergency source when the connection is at a location remote from the emergency source.

- A permanent plaque shall be placed at the service equipment denoting the type and location of onsite legally required standby power.

- A permanent plaque shall identify the connection of the grounding electrode conductor of the legally required standby power source when the connection is at a location remote from the legally required standby power source.

- A permanent plaque shall identify the connection of the grounding electrode conductor for the optional standby power source when the connection is at a location remote from the optional standby power source.

***END OF SECTION***