MECHANICAL DESIGN CRITERIA

Table of Contents

I.	GENERAL	1

II.	CRITERIA	1

A.	HVAC DESIGN - GENERAL	1

1.	Drawings Numbering	1

2.	Requirements for Phases I through III	1

3.	Design guidelines	2

B.	HVAC DESIGN – ROOM SPECIFICIFICATION	2

1.	Media	2

2.	Dining/Multipurpose	2

3.	Gym	2

4.	Auditorium	2

5.	Classroom	2

6.	Mechanical AHU Equipment Rooms	3

7.	Chiller/Pump/Boiler Building	3

8.	Interior Corridors	3

C.	HVAC DESIGN – EQUIPMENT	3

1.	Chillers	3

2.	Cooling Towers	4

3.	Piping	4

4.	AHUs	4

5.	Ductwork	4

6.	Air Devices	4

7.	EFs	4

8.	Boilers	5

9.	DX Split Systems	5

III.	SPECIFICATIONS	5

A.	SPECIFICATIONS GENERAL:	5

B.	SPECIFICATIONS CRITERIA:	5

1.	Division 1 Boilerplate	5

2.	23 05 10 General Requirements	6

3.	23 05 29 Supports and Anchors	6

4.	23 05 53 Mechanical Identification	6

5.	23 05 48 Vibration Isolation	6

6.	23 07 19  Piping Insulation	6

7.	27 07 16  Equipment Insulation	7

8.	23 07 13 Ductwork Insulation	7

9.	23 21 13  Hydronic Piping	7

10.	23 21 16 Hydronic Specialties	8

11.	23 21 23 HVAC pumps	8

12.	23 57 00  Plate and Frame Heat Exchanger	8

13.	23 52 00 Boilers	9

14.	23 63 00  Condensing Units	9

15.	23 64 23.13 Air Cooled Scroll Chiller	9

16.	23 64 26.13 Air cooled Screw Chiller	9

17.	23 64 16.16 Water Cooled Centrifugal Chiller	9

18.	23 64 26.16 Water Cooled Screw Chiller	10

19.	23 65 00 Cooling Tower	10

20.	26 82 16.14 Electric Duct Heater	10

21.	23 82 19 Fan Coil Unit	10

22.	23 81 26 Split System Air Handling Unit	10

23.	23 74 16 Packaged DX Rooftop Unit	10

24.	23 73 13 Chilled Water Air Handling Unit	11

25.	23 35 00 Exhaust Fans	11

26.	23 30 00 Ductwork (Including Accessories)	11

27.	23 36 16 Variable Air Volume Units	12

28.	23 37 13 Air Devices	12

29.	23 09 23  DDC Controls	12

30.     40 97 00 Variable Frequency Drives	12

31.	23 05 10  Supplementary Requirements	12

32.	23 05 93  TAB Work	12

33.	23 25 00 Water Treatment	12

34.	23 41 00 HVAC filters	12

| Revision History |  |
| --- | --- |
| Revision Date | Section / Nature of Revision |
| 03/1/17 | Document Issued |
| 10/20/21 | Updated to reflect the current CSI format II C 8 F: added gas regulators vent outside per CSD-1 CF 190 (d) III B 13 h: added gas regulators vent outside per CSD-1 CF 190 (d) |
| 2/20/26 | II A 3: changed 74 to 73 II B 6 h: added provide concrete… II B 7 b: removed chilled water fan coil and added DX mini-split II C 1 b: added aluminum II C 1 c: added vibration isolation… II C 1 e: removed are not and added for end of unit coil… II C 4 e: removed 7 and added 9/9A II C f: removed 11 and added 13 mini pleat II C 4 i-k: added entire section II C 6: added specify 3 or 4 cone II C 6 e: added entire section III B 5 b: added or as required by manufacturer III B 6 f: added Alumaguard… III B 7 a added ¾” is acceptable III B 8 e: removed section III 9 a 3): added section III 9 c 1) and 2): removed sections and added all condenser pipe… III 9 d 1): added no jacket is required III 10 c: added section III 11 r: added section III 13 a 4)-6): added sections III 13 i: added section III 17 d: removed McQuay and York and added Daikin and JCI III 17 e: removed neoprene, when on ground level slab and use spring isolators if not and added factory provided III 19 a: removed section III 21 f: added section III 22 a: added section III 23 i: removed under 6 tons. Over 6 tons shall have belt drive. Added all sizes unless not available III 24 f 2): added bibb III 24 f 3): added section III 24 g-h: added sections III 26 c: added manual III 26 j: removed cleaned and added inspected for cleaning III 28 a: added 3 |
| 8/17/26 | II B 7 a: removed chilled water fan coil and added DX mini-split II B 8 a: removed provide one half cfm that is recommended by load model peak value II C 1 b: added or aluminum, removed vibration isolation and added neoprene pads between each II C 4 e: removed 7 and added 9/9A II C 5 d: added entire section II C 5 e: added entire section II C 8 a: removed flex tube boilers are preferred, provide and in design II C 10 d 6): added entire section II C 10 e: added entire section III B 5 d: added inertia pads are not required for smaller pumps III B 7 c 2): added do not need to be insulated III B 9 a 3): added ProPress connections are acceptable for copper tubing III B 11 r: added section III B 13 a: removed RBI, Bryan and Raypak. Added Riello III B 13 b: removed entire section and added boilers with internal pumps are preferred III B 13 d: removed entire section and added condensing boilers preferred III B 13 e: removed entire section III B 14 c: removed PVC coated steel wire III B 17 c: removed entire section III B 17 e: removed entire section and added use manufacturer’s recommended vibration isolator |

# GENERAL

A.	The design professional shall use this document in conjunction with the educational specifications and Pinellas County Schools’ (PCS) master specifications to develop the design and contract documents.

    - The Engineer of Record shall be responsible for incorporating owner requirements and preferences in drawings and specifications.  The Engineer shall utilize standard industry specifications and practices.

    - Exercise caution to maintain competitive bidding and avoid single-source supply of such equipment and systems.

  - In this document, the term Engineer represents the professionally qualified design Engineer of Record and/or Engineering Consultant, duly licensed in the State of Florida, that signs and seals Project design documents.

  - The Engineer is the person responsible and in charge for the design and development of all Project documents.

  - Engineer shall be responsible for using the latest code references, testing agencies, etc. including but not limited to:

    - Florida Building Code (FBC) - Mechanical

    - Florida Energy Code

    - National Fire Protection Association (NFPA)

    - American Association of Heating Refrigerating and Air Conditioning Engineers (ASHRAE) standards

    - ASHRAE Advanced Energy Design Guidelines for K12 School Buildings

    - The American Society of Mechanical Engineers (ASME)

    - ARI

    - The National Electrical Manufacturers Association (NEMA)

    - Underwriters Laboratories (UL)

    - The American National Standards Institute (ANSI)

    - Sheet Metal and Air Conditioning Contractors National Association (SMACNA)

    - Air Movement and Control Association (AMCA)

# CRITERIA

## HEATING VENTILATION AND AIR CONDITIONING (HVAC) DESIGN – GENERAL

### Drawings numbering: at a minimum include the following drawings with corresponding information on each drawing. Drawing numbering is preferred, but not mandatory.

      - M0.0 Legend

      - M0.1 Flow diagram

        - Any controllable equipment

        - Sensor locations

        - Table of loads.  (see attached)

      - M0.2 Site plan – pipe routing, associated site obstructions (trees, sidewalks, etc.)

      - M1.0 Demolition plans – clearly label equipment to be removed.

      - M2.0 New work plans – 1/8” per foot floor plans and ¼” per foot mechanical room layout

      - M3.0 Details

      - M4.0 Schedules

      - M5.0 Controls diagrams – control logic and sequence of operations for each piece of equipment to be controlled and location of LAN controllers and location of computer.

### Requirements for Phases I through III

      - Phase I Schematic Design:

        - Floor plan with location of major mechanical equipment.

        - Room sizes.

        - Flow diagram with system type.

        - Table of Contents specifications.

      - Phase II Design Development (mechanical design team shall schedule review meeting with PCS’ Mechanical Engineer to discuss design plan):

        - Floor plan with air handler unit’s (AHU) sized and positioned in room.  If there are no load models, assume 1.2 cfm/SF.

        - Show ¼” scale mechanical rooms.  Show locations of a Variable Frequency Drive (VFD), control panel, duct detector, spin in fitting in supply air, pipe penetrations into room (assume footer width), service clearances in shaded box.

        - Flow diagram with load summary table setup (or complete).

        - Site plan with pipe routing.

        - Chiller plant layout of equipment and single line piping.

          - Pumps shall have motors facing serviceable aisles.

          - Condenser pumps close to wall of tower yard.

          - Manufacturers operating and service clearances in shaded box.

          - Show locations for chemical treatment, VFD’s, disconnects, control panel, Fan Coil Unit (FCU), air separator and expansion tank.

        - All sheets including detail sheet with anticipated details, schedule sheet (not filled in) and anticipated general controls diagrams.

        - Full book specifications with owner requirements in bold.

      - Phase III Construction Documents:

        - Completed design.

        - Energy calculations.

        - Life Cycle calculations.

        - Completed load summary.

        - Elevation view of AHU mechanical room including height of outdoor air inlet and location of serviceable equipment such as control valves, control dampers, duct heaters and duct access doors.

        - Chiller equipment room: piping larger than 2” shall be double lined.  Show elevation view for clarification of specific pipe routing.

### Design guidelines:

      - Indoor summer: 73° F, 50% RH

      - Outdoor summer: 92° F, 80° F wet bulb

      - Indoor winter: 70° F

      - Outdoor winter: 32°F

      - Indoor kitchen: 78° F

      - Building pressurization: .10 to .15 cfm/SF

## HVAC DESIGN – ROOM SPECIFICATION

    - Media: ability to control humidity after hours without entire plant running.

    - Dining/multipurpose: single zone Variable Air Volume (VAV). CO2 demand control ventilation.

    - Gym: single zone VAV.  CO2 demand control ventilation.

    - Auditorium: CO2 demand control ventilation.

    - Classroom: do not use demand control ventilation.

      - Provide room temperature sensors in the return air for each room.

      - Use ANSI standard S12.60-2002 American National Standard Acoustical Performance Criteria, Design Requirements and Guidelines for Schools.

    - Mechanical AHU equipment rooms:

- Coordinate size and location with architect.

- Room shall be located on exterior wall with double doors to exterior.

- Provide 18” minimum clearance on back wall of AHU.

- Show all service clearances.

- All serviceable equipment shall be located such that a maximum 6’ ladder can be used.  All dampers, control valves and air monitors are preferred to be serviced from ground level.

- Provide access doors for dampers.

- Provide concrete pad on exterior grade of entrance to mechanical room with exterior lighting.

- Provide concrete housekeeping pad poured to closest two walls of mechanical room for AHU reposition if necessary.

- Provide positive pressurization with 4” spin in fitting with damper in supply air duct.

- Provide each room with hub drain to storm for condensate and floor drain to sanitary for other.

- Provide with hose bibb.

- If room is not of proper size, please notify PCS Mechanical Engineer.

    - Chiller/pump/boiler building:

      - Roll up door in front of each chiller that is sized large enough for installation and removal of entire machine.

      - DX mini-split unit for tempering of air.

      - Condenser water return pipe shall not be higher than cooling tower sump.

    - Interior corridors:

- Shall be conditioned.  Do not use VAV’s.

    - Food service cooking equipment:

- All cooking equipment used in processes producing smoke or grease laden vapors shall be equipped with an exhaust hood ventilation system that complies with all the equipment and performance requirements of NFPA 96: Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.  The system design shall be submitted for review to the PCS Fire Marshal.

## HVAC DESIGN – EQUIPMENT

    - Chillers:

    - Air cooled chillers shall be provided with low sound fans and compressor sound attenuation.

    - Air conditioning chillers shall be mounted and secured on 6” high hot dip galvanized, or Aluminum I beams with neoprene pads between each.

    - Provide chiller piping with an additional supply and return flange connection for emergency chiller installation.

    - Air conditioning chillers shall be provided with wire coil guards and hail guards for end of unit coil protection only.

    - Chillers shall be sized to connected load plus 10%.  Show in table on flow diagram.

    - Utilize primary/secondary pumping arrangement.  Consult with the PCS Mechanical Engineer if another pumping scheme is desired.

    - Provide chiller yard with concrete housekeeping pad, gravel or shell yard and exterior lighting.

    - Chiller yard walls shall be designed to attenuate noise to meet current noise guidelines and allow proper airflow to chillers.  Wall shall be no higher than 2’ above height of chillers.

    - Cooling towers:

      - Select only direct drive motor/fan assemblies.  No belt drive fans.

      - All stainless-steel construction including accessories and mounting hardware.

      - Provide with aluminum ladder.

    - Piping:

- Do not route piping below buildings (unless entering in building) or under walkways unless with approval from PCS Mechanical Engineer.

- High-density polyethylene pipe (HDPE) hydronic piping for underground installation may be specified as a bid base item with the insulated steel piping as an alternate deduct option.

    - AHUs:

      - No stacked dual path AHUs shall be accepted unless approval from the PCS Mechanical Engineer.

      - Mount on pad vibration isolators.

      - Provide base rails in addition to 6” high housekeeping pad.

      - Provide flexible duct connection for supply duct.

      - Provide mixing box with angled 2” MERV 9/9A pre-filters if space permits. 2” flat filters section is acceptable.

      - Provide separate filter section with 4” MERV 13 mini-pleat after filters.

      - Size AHU cooling coils using entering water temperature 1° F higher than leaving chilled water temperatures.

      - Outdoor air and return air dampers preferred to be located in mixing box.

      - Provide Ebtron outside air measuring station.

      - Provide access doors for any duct mounted equipment that requires servicing.

      - Provide shutoff valves in both supply and return pipe. Provide Y-strainer with hose bibb connection, balancing valve and control valve.

    - Ductwork:

      - Fiberglass duct is not acceptable.

      - Flex duct is preferred for transfer air duct.  Minimum two 90° turns not including drop down to devices.

      - Exposed duct shall be spiral or flat oval double walled internally insulated duct.  Paint to match structure.

      - DuctSox are an option in some situations.

      - External insulation shall have all seams taped and mastic.  Staples and tape are not acceptable.

    - Air devices: specify 3 or 4 cone diffusers.

- Insulate the tops of all air devices.

- Provide flex duct between 4’ and 10’ to supply air devices.

- Import VAV locations into architect’s reflected ceiling plan in addition to air devices.  Coordinate location of VAV’s to ensure proper service clearance.  Avoid lights, cable trays, plumbing pipe, etc.

- Use plastic air devices for kitchens.  Insulate tops of devices.

- No aggregate exhaust or return devices. Specify perforated.

    - Exhaust fans (EF):

- Rooftop exhaust fans are preferred.

- Provide with minimum 18” roof curb.

- Specify direct drive fans unless belt is only option.

- All EFs shall be controlled by the Emergency Management System (EMS) unless otherwise noted.  All EFs shall be at least monitored by EMS.

    - Boilers:

- Gas fired condensing boilers.

- Provide boiler rooms with manual emergency shutdown switches in accordance with ASME boiler code CSD-1.

- Provide minimum 18” clearance around entire boiler.

- Provide room with floor drain.

- Provide with rigid relief pipe.

- For gas regulators per CSD-1 CF 190 (d) gas vent, bleed, or relief lines shall have provisions to be piped by the installer outdoors at a safe point of discharge, a means shall be provided at the terminal point to prevent stoppage of the lines by foreign material, moisture or insects.

    - DX split systems:

- The following rooms shall be equipped with standalone DX cooling, which is preferably a mini split.

- Principal’s office.

- Dedicated computer lab.

- Main CER.

- Elevator machine room.

- Dry storage.

    - Pumps:

        - Orient pumps such that motors are facing out for easy access.

        - Do not use suction diffusers unless space constraints dictate.  Put Y-strainer in rise of suction pipe.  Use long radius elbow to inlet.

        - Y-strainer shall be equipped with hose bibb connection at drain.

        - All pumps shall be equipped with the following:

- Shutoff valves on supply and return.

- Check valve.

- Balancing valve.

- Y-strainer.

- Flexible connectors.

- No triple duty valves.

- Pumps do not need to be insulated.  Provide a drip pan underneath and piped to nearest floor drain.

# SPECIFICATIONS

## SPECIFICATIONS GENERAL:

    - All owner requirements shall be in bold in specifications during all submittals with the exception of 100% bid and permit set.  All owner furnished specifications shall be included in its entirety with footer showing the revision date.

## SPECIFICATIONS CRITERIA:

### Division 1 boilerplate

  - For all hard bid projects, provide most recent district supplied Division 1 boilerplate.  Consult with project coordinator for all fillable items.

  - For special conditions provide the following verbiage for contingency: In addition to your bid, there shall be a (fill in amount for 3% construction cost) contingency.  The contingency shall be a separate line item with no markup added to it.  The purpose of the contingency is for defraying expenses due to unforeseen circumstances related to construction.  The contractor shall be required to furnish documentation evidencing expenditures charged to the contingency with a 15% markup prior to written approval and release of funds by the Owner.  This contingency shall be part of the contract and if not used, or partially used, there shall be a deductive change order to reconcile the contract balance upon completion of the project.

### 23 05 10 General Requirements:

- Refer to 23 05 10.

### 23 05 29 Supports and Anchors

  - Provide pipe saddles for insulated pipe 12” long and 18-gauge sheet metal.

  - Provide pipe hanger within 12” of all elbows.

  - Support vertical piping midway at each floor or minimum 12’ spacing.

### 23 05 53 Mechanical Equipment Identification:

- Label all visible piping in mechanical rooms and exposed areas with supply and return and arrows denoting flow.  Mark with either hot, chilled, or condenser water.

- Label all equipment with 2” x 4” plastic tags.  Black with white lettering.

- Label AHU numbers by building number first following by number of AHUs in building.

- Label VAVs with AHU number first then VAV number:

  - Example AHU 2-3 (Building 2 AHU-3).

  - Example VAV 2-3-11 (VAV from AHU 2-3 #11).

- Label pumps as follows:

  - Chilled water: CHP

  - Primary chilled water: PCHP

  - Secondary chilled water: SCHP

  - Condenser Water: CP

  - Hot water: HWP

  - Boiler pump: BP

### 23 05 48 Vibration Isolation:

- Provide flex connectors at outlet of each pump and AHU.

- Pad mounted AHUs.  Neoprene or as required by manufacturer.

- Air cooled and water-cooled chillers.  Pad type neoprene pads or per manufacturers recommendations.

- Pumps on second floor or over 50 HP shall be installed on inertia pads.  Inertia pads are not required for smaller pumps.

### 23 07 19 Piping Insulation

- Provide clear insulation schedule for piping on each project.

- Exposed insulation in mechanical rooms (up to 8’), interior exposed rooms and all exterior insulated pipe shall have .016” aluminum smooth finish jacket.  Jacket shall be continuous and include pre-formed aluminum covers for all elbows and fittings.  Exterior jacketing must be installed with seams facing down.  Insulation shall be vapor sealed prior to installation of jacketing.  Jacketing shall be continuous and include pre-formed aluminum covers for all elbows and fittings.

- Interior above grade: white fire-retardant finish all service jacket (ASJ)

- Underground insulation shall be sealed in a waterproof manner.

- Insulate interior condensate pipe.  Exterior condensate pipe does not need insulation.

- All exposed Armaflex insulation on DX piping shall get aluminum jacket. Alumaguard flexible weatherproofing jacket is also acceptable.

  - Type A: closed cellular glass (foamless) .29 k value conductivity.

    - Chilled water.

    - heating hot water.

    - Refrigerant suction pipe in plenums or through firewall penetrations.

- Type B: closed cell foam plastic (Armaflex) 27 k value.

    - Condensate pipe.

    - Refrigerant suction lines except in plenums or firewall.

- Type C: glass fiber .23 k value.

- Domestic hot water

- Provide pipe saddles minimum 12”.

### 7.	27 07 16 Equipment Insulation:

- Chillers shall be insulated according to the manufacturer’s specifications. ¾” Armaflex is acceptable.

- Pumps shall be insulated with Foamglas® box.

- Type A: Closed cell glass Foamglas® .29 k value.

  - Air separators, strainers and valve bodies.

  - Pumps do not need to be insulated.

- Type B: closed cell foam plastic (Armaflex).

- Chiller cold surfaces.

### 23 07 13 Ductwork Insulation:

- All supply and return air duct shall be externally wrapped Type A fiberglass R-6 insulation with seams that are sealed with tape and mastic.

- Ducts greater than 18” width shall be pinned with fasteners to minimize sagging every 18”.  Pins shall be sealed with mastic.

- Exhaust and relief air duct shall be internally lined with Type B smooth surface cleanable duct liner.

- Double walled internally insulated duct for first 20’ of supply and return unless otherwise noted.

### 23 21 13 Hydronic Piping:

- Above grade chilled/hot water pipe:

  - 2.5” and larger Schedule 40 carbon steel.

  - 2” and smaller Type L, copper tubing or Schedule 40 black steel with screwed fittings.

  - ProPress fittings are acceptable for copper pipe.

- Below grade chilled/hot water pipe:

  - Factory fabricated pre-insulated piping system.

  - Consider factory pre-insulated HDPE pipe.  No insulation on joints, elbows.

  - PVC casing pipe.

  - Polyurethane foam insulation.

  - If no insulation or casing on joints, insulation at ends of each pipe section must be sealed weather tight.

  - Schedule 40 black steel sleeves required for penetrations through masonry or concrete walls floors and roofs.  Shall extend minimum 1” above finished floor (AFF).

- Condenser water pipe:

  - All condenser water pipe shall be HDPE.

- Condensate drain piping:

  - Inside mechanical room and inside building: copper insulated with Armaflex. No jacket is required.

  - Rooftop condensate may be uninsulated PVC painted with UV coating.

  - All condensate drain lines shall be supported properly.

### 23 21 16 Hydronic Specialties:

- Provide thermometers and pressure gauges for all AHUs in wells deep enough to provide accurate readings.

- Provide strainers before coils and pump inlets.  Strainers shall have valve and hose connection.

- Provide additional strainer before inlet of chillers.

### 23 21 23 HVAC Pumps:

- Approved manufacturers: B&G, Armstrong, Weinman and Taco.

- TEFC motor 1750 or less RPM. VFD compatible.

- Floor mounted end suction unless otherwise directed.

- Flexible coupling with coupling guard.

- Cast iron casing with gage ports and flanged suction and discharge.

- Bronze impeller keyed to motor shaft.

- Bearings: L10 rated life of 30,000 hours

- Carbon steel shaft with bronze key.

- Seal: stainless steel.

- Vertical inline are accepted for some applications.

- Contractor shall include impeller shaving on all pumps 7.5 HP and larger.

- Laser alignment for all pumps 20 HP or larger.

- Alignment by factory trained and authorized representative.

- 1 year warranty.

- Orient pumps with motors facing service area.

- Provide built in hoist for pumps larger than 40 HP.

- Long radius elbow in lieu of suction diffuser.  Strainer in rise of pump inlet.

- If space does not permit a long radius, elbow suction diffuser is acceptable.  Still need Y-strainer in rise.  Remove strainer from suction diffuser.

- Removable/reusable pump insulator is no longer preferred. Provide a drain pan below pump and copper pipe to nearest floor drain. Ensure pipe does not interfere with normal walkways.

### 23 57 00  Plate and Frame Heat Exchanger:

- HX shall be tested and flushed at the factory and shipped completely assembled.

- All nozzle connections shall be sealed.

- Shall designed, fabricated and tested in accordance with ASME code and shall bear the appropriate stamp and National Board Registration number.

- Shall be designed to include minimum of 10% additional surface for fouling.

- Shall be designed with a redundant heat exchanger.

- Plates shall be stainless steel.

- Gasket shall be one piece Nitrile rubber.

- Frame shall be carbon steel.

- Bolts shall be treated with rust-protective coating and covered with plastic sleeves.

- Frame and bolt shall be provided with capacity to add 25% more plates for future expansion.

- Provide backup heat exchanger unless otherwise noted.

- Design with proper service clearance.

- Provide with 2-year unconditional parts and labor warranty.

- Provide with 1” valve and hose bib connection to supply and return of shell side for flushing without removing plates.

### 23 52 00 Boilers:

- Manufacturer:

  - Riello

- Boilers with internal pumps are preferred.

- 160 Psig and 210° F ratings.

- Condensing boilers are preferred.

- Airtight observation port.

- Provide Boiler Inspectors Certifications and factory test reports and O&M manuals.

- For gas regulators per CSD-1 CF 190 (d) gas vent, bleed, or relief lines shall have provisions to be piped by the installer to the outdoors at a safe point of discharge a means shall be provided at the terminal point to prevent stoppage of the lines by foreign material, moisture or insects.

- Specify boilers to be condensing boilers.

### 23 63 00 Condensing Units:

- Casing: welded steel frame with zinc coated galvanized steel panel coated with epoxy primer and enamel finish.

- Condenser coils: aluminum fin bonded to copper tubing.

- Coil guard.

- Fans and motors: weatherproof motor.

- Compressors: scroll.

- Crankcase heater: thermostatically energized.

- Warranty: 1-year machine and 5-year compressor.

- Provide with defrost controls and low ambient operation to 35° F and anti-short cycle timer 5 minutes.

### 23 64 23.13 Air Cooled Scroll Chiller:

- Refer to attached specification.

### 23 64 26.13 Air cooled Screw Chiller:

- Refer to attached specification.

### 23 64 16.16 Water Cooled Centrifugal Chiller:

- Owner pre-purchased chillers: a life cycle cost analysis bid method shall be used for owner purchased equipment unless otherwise indicated.  See attachment for methodology. Engineers shall meet with the PCS Mechanical Engineer and project coordinator to discuss process.

- Warranty: in accordance with OEM service agreement and bid results.

- Acceptable manufacturers: Carrier, Daikin, Trane and JCI.

- Use manufacturer’s recommended vibration isolator.

- Compressors: hermetically sealed motor transmission and compressor.  Hermetic motor driven oil pump, oil cooler, pressure regulator, oil filter, oil pump starter, automatic water control valve, thermostatically controlled oil heater and reservoir oil temperature gage.

- Cooler: carbon steel with carbon steel tube sheet.  Tubes shall be 0.028” wall thickness.  Rated to 150 psig and tested to 225 psig.  Cooler shall be flooded shell and tube type.

- Provide factory 1.5” thick Armaflex vapor seal insulation on all cold surfaces including but not limited to evaporator shell, heads and compressors.

### 23 64 26.16 Water Cooled Screw Chiller:

- Refer to attached specification.

### 23 65 00 Cooling Tower:

- Gear driven fan.

- All stainless-steel construction of cold and hot water basin, structural elements, hardware for fabrication, hardware for miscellaneous connections i.e. conduit, pipe, etc.

### 26 82 16.14 Electric Duct Heater:

- Acceptable manufacturers: Warren and Indeeco.

- Heaters shall meet all NEC and UL requirements and listings.

- Elements shall be open coil, 80% nickel, 20% chromium Type A resistance wire.

- Heater frames shall be aluminized steel.

- Provide thermal cutout and over temperature protection, airflow switch, fuses, control circuit transformer and door interlocking disconnect switch.

- Provide SCR controls when possible.

- Provide with insulated dust tight terminal box.

- Install per ARI and SMACNA ducted electric heat guide.

### 23 82 19 Fan Coil Unit:

- Chassis shall be 18-gauge galvanized steel insulated with foil faced closed cell insulation.

- Provide with noncorrosive drain pan.  Provide with auxiliary drain pan or auxiliary drain connection installed with float switch.

- Access doors shall be hinged and fully accessible.

- Copper tubes and aluminum fins.

- 2” filter rack.

- Filter section must be accessible without the need for a screwdriver or other tool if practical.

- Centrifugal forward curbed fan.

- Electric heat shall be UL approved.

### 23 81 26 Split System Air Handling Unit:

- Warranty: provide 1 year manufacturer’s warranty and compressor warranty for 5 years.

### 23 74 16 Packaged DX Rooftop Unit.

- Warranty: provide 1 year manufacturer’s warranty and compressor warranty for 5 years.

- Casing:  zinc coated heavy gauge, galvanized steel with external surfaces finished with baked enamel.

- Service panels.

- ½” foil faced fiberglass insulation for ten tons and below.  ½” foil faced closed cell insulation for over ten tons.

- Compressor: direct drive scroll type.  Internal motor overloads, crankcase heater and vibration isolation.

- Fixed orifice refrigeration circuit.

- Internally finned copper tubes with aluminum plate fin.  Leak tested to 200 psig and pressure tested to 450 psig.

- Direct drive outdoor fans.

- Direct drive indoor fan for all sizes unless they are not available.

- Unit shall be secured to minimum 18” high roof curb in accordance with proper wind loading methods.  Contractor shall provide manufacturers detail for screw number and placement during inspection.

- Outdoor air damper shall have the capability to fully close and be manually set to up to 50% open.

### 23 73 13 Chilled Water Air Handling Unit:

- No large AHUs on second floor of buildings (contact district engineer if architect does not provide).

- Provide details of all AHU sections with access doors.

- Provide room large enough for proper normal clearance and 18” on backside of unit.

- Leave one panel on fan section free from conduit or other items that would need to be removed to remove section panel.

- Outdoor air louvers shall be no less than 60” above grade to lowest point of louver.

- All chilled water coils shall be equipped with the following:

  - Shut valves supply and return.

  - Strainer on inlet with valve and hose bibb.

  - Balancing valve and control valve on outlet.

- Fan walls are acceptable.

- Outdoor air and return air dampers are preferred in mixing box. If not practical, duct mounted valves shall be accessible and duct equipped with access door for service and inspection.

### 23 35 00 Exhaust Fans:

- Specify direct drive fans unless belt drive is only option.

- Provide rooftop exhaust fans as much as possible.

- Single restrooms may be single ceiling mounted exhaust fans.  Fans shall be controlled by light switch with 10-minute time delay for shutoff.

- Exhaust fans shall be connected to campus wide DDC controls.

- All rooftop fans shall be installed on a minimum 18” high roof curb.

- Acceptable manufacturers:

  - Greenheck

  - Cook

### 23 30 00 Ductwork (including accessories):

- Sheet metal ductwork for all supply, return, exhaust and relief air duct.  No duct board shall be permitted.

- Installed in accordance with SMACNA.

- Manual dampers shall be galvanized steel with locking quadrant and a 2” standoff.

- All interior surfaces shall be smooth.  Seams and joints shall be external.

- Provide turning vanes in all 45° and 90° bends.

- Mastic seal on all joints.

- Pressure tested by contractor in accordance with FBC and SMACNA and witnessed by PCS Test and Balance contractor.

- Double walled internally insulated duct for first 20’ of supply and return unless otherwise noted.

- Provide access doors in accordance with SMACNA for cleaning and inspection of all controllable components in system.

- All ductwork scheduled to be existing to remain shall be inspected for cleaning.  Replace air devices unless otherwise noted.

### 23 36 16 Variable Air Volume Units:

- Manufactured with 22-gauge zinc coated steel, 1” glass fiber insulation with foil liner to prevent fiberglass from entering airstream.

- UL listed.

- Support units directly to structure.  Do not support with ductwork.

- Coordinate location with Reflected Ceiling Plan and other trades to avoid clearance conflicts.

- Actuators shall be pre-installed on VAV boxes by controls contractor prior to being hung.

### 23 37 13 Air Devices:

- Supply air devices shall be Titus TMS AA or equivalent.  3 or 4 cone.

- Return air devices shall be Titus PAR AA or equivalent.  Perforated hinged for cleaning.

- Contact PCS Mechanical Engineer for specialty air devices for gyms, auditoriums, media centers, etc.

- Supply and return air devices shall be insulated on top of device.

- Supply air devices in kitchens shall be plastic with insulated tops.

- Acceptable manufacturers:

  - Metalaire

  - Titus

### 23 09 23 DDC Controls:

- See attached specifications.  Provide in its entirety.

- 40 97 00 Variable Frequency Drives:

- See attached specifications.  Provide in its entirety.

### 23 05 10 Supplementary Requirements:

### 32.	23 05 93 TAB Work:

### 33.	23 25 00 Water Treatment:

### 34.	23 41 00 HVAC Filters:

***END OF SECTION***